## Slide 1: Stress Test Evaluations of Taiwan's Nuclear Power Plants
Lih-Yih Liao
September 23, 2013
Notes: <number>

## Slide 2: Outlines
<number>
  General data of site/plant
  AEC Actions Timelines
  Taiwan Action Plan
  Cliff edge results
  Conclusions of the regulatory body

## Slide 3
<number>
General data of site/plant
Notes: RCCV :
<number>

## Slide 4
AEC
09
10
11
12
2012
01
02
08
2011
07
Preliminary Safety
Assessment Report
First phase Safety
Assessment Report
(final)
National Report
(Draft)
Final Phase Safety
Assessment Report
(draft)
First phase Safety
Assessment Report
(draft)
ENSREG
Stress test
specification
03
04
WENRA stress test
specification
1108 1st progress meeting
1207 2nd progress meeting
1229 3rd progress meeting
0119 4th progress meeting
0217 5th progress meeting
INER-Five review
meeting with DNR
Two batches RAIs
LM stress test
Utility Report
Taipower
Final Phase Safety
Assessment Report
(final)
05
06
07
08
09
10
11
12
2013
01
National Report
(Final)
※Special inspection report
CS,KS, MS stress test
Utility report
※Progress Report

## Slide 5: EU Stress Test: Taiwan Action Plan
Checklist on the basis of “Compilation of Recommendations and suggestions – Peer review of stress tests performed on European nuclear power plants” to cover all the implementation status of Post-Fukushima improvements in Taiwan’s nuclear power plants
The checklist is compiled of the following items
  E for ENSREG "Compilation of recommendations and suggestions"
  C for CNS Final Summary Report of 2nd Extraordinary Meeting 2012 para. 21 “significant activities and action..."

## Slide 6: EU Stress Test: Taiwan Action Plan
ENSREG Main Areas of Improvement (European Level Recommendations)

## Slide 7: EU Stress Test: Taiwan Action Plan
ENSREG and CNS Considerations (Items to be considered)

## Slide 8: EU Stress Test: Taiwan Action Plan
ENSREG and CNS Considerations (Items to be considered)

## Slide 9: EU Stress Test: Taiwan Action Plan

## Slide 10: EU Stress Test: Taiwan Action Plan

## Slide 11: EU Stress Test: Taiwan Action Plan

## Slide 12: EU Stress Test: Taiwan Action Plan

## Slide 13: EU Stress Test: Taiwan Action Plan

## Slide 14: EU Stress Test: Taiwan Action Plan

## Slide 15: EU Stress Test: Taiwan Action Plan

## Slide 16: EU Stress Test: Taiwan Action Plan

## Slide 17: EU Stress Test: Taiwan Action Plan

## Slide 18: EU Stress Test: Taiwan Action Plan

## Slide 19
<number>
Plant | Design Basis | Cliff-edge as original design
CS | 0.3g | 1.05g (core support structure)
KS | 0.4g | 0.77g (RCIC DC Switchgear)
MS | 0.4g | 1.48g (DC Bus Switchgear)
LM | 0.4g | 2.0g (RBSW injection pump)
Initiation Event: : Earthquake
Cliff edge results
*All values are peak ground acceleration values
Notes: All values are peak ground acceleration values (median values 中值)
<number>

## Slide 20
<number>
Plant | Design Basis | Cliff-edge as original design | Cliff-edge with countermeasure
CS | 10.7 run up(m) | 11.2 m (RCIC) | 16.7 m (TPC is now planning to build tsunami wall with height of 10.7+ 6 m)
KS | 10.3 run up(m) | 12.3 m (RCIC) | 16.3 m (TPC is now planning to build tsunami wall with height of 10.3+6 m)
MS | 12.0 run up(m) | 15 m (DC Bus) | 18.0 m (TPC is now planning to build tsunami wall with height of 12+6 m)
LM | 8.0 run up(m) | 12m (RCIC..etc) | 14.0m (TPC is now planning to build tsunami wall with height of 8+6 m)
Initiation Event: : Tsunami
Cliff edge results (cont.)
Notes: <number>

## Slide 21
<number>
Plant | Design Basis | Cliff-edge as original design | Countermeasure for Cliff-edge
CS KS MS LM | 8 hours | DC power: 24 hours (isolate non-vital DC load) | upgrade the capacity of DC power to 24 hour without load shedding for the first 8 hour Evaluation: extending coping time to 24 hours Autonomy of 72 hours with portable D/G
 |  | Coping time: 8 hours | 
Initiation Event: : Station black out
Cliff edge results (cont.)

## Slide 22
<number>
Plant | Cliff-edge as original design | Countermeasure for Cliff-edge
CS | 40 hours (CST storage capacity) | With fresh water from reservoir(There is no limitation for water supplying from creek or sea )
KS | 24 hours (CST storage capacity) | With fresh water from reservoir(There is no limitation for water supplying from creek or sea )
MS | 40 hours (CST storage capacity) | With fresh water from reservoir(There is no limitation for water supplying from creek or sea )
LM | 21 hours (CST storage capacity) | With fresh water from reservoir(There is no limitation for water supplying from creek or sea )
Initiation Event: : Loss of ultimate heat sink
Cliff edge results (cont.)

## Slide 23
<number>
scope and content
The regulatory body identified some areas to improve the scope and content of the assessments:
The analysis postulates that only one unit is affected. The consequences of both units in one site being affected shall be addressed.
The accident scenario, the availability of the mitigation systems and the cliff edge effects of the unit during shutdown conditions may be quite different from those of normal operation. However, the accident scenarios during shutdown conditions are not addressed in TPC stress test report. The missing assessment is considered necessary for a complete assessment.
Extreme external hazards (including earthquake, flooding, Tsunami, etc.) may result in SBO and complete loss of heat sink, the consequential impact to spent fuel pool (including the integrity of pool structure) should be evaluated.
TPC should finish the integrated PRA analytical model based on ASME PRA standard.
  Conclusions of the regulatory body
Notes: During shutdown conditions, the accident scenario, the available mitigation systems and the cliff edge effects may be quite different from those of normal operation. This is particularly important for the PWR because it was already well-known that the shutdown state and in particular mid-loop operation is the most un-favorable state in the event of SBO. If the reactor is open a few days after shutdown (for refuelling), without countermeasures, core heat up is typically within the one to three hours range. However, the situations in which the reactor coolant system is open or operating with reduced inventory are not addressed in TPC stress test report. The missing assessment is considered necessary for a complete assessment.

## Slide 24
<number>
Earthquake
General Comments:
Based on the review of TPC’s reports and the supporting documents, the subsequent technical meetings, the AEC considers that the resulting action plan of this seismic reassessment is adequate.
The AEC identified additional recommendations for TPC to further improve the seismic robustness of the plant facilities:
Although the preliminary results showed the DBEs of the three plants remain some margin, the maximum potential earthquake caused by the Shanchiao fault and Henchun fault are still to be evaluated, as they are so close to the Chinshan/Kuosheng and Maanshan NPPs respectively.
Spent fuel pools are almost filled up with spent fuels in Chinshan and Kousheng plants. The TPC should take steps to speed up the process of moving these spent fuels to ISFSI(Independent Spent Fuel Storage Installation).
  Conclusions of the regulatory body
Notes: the spacing between fuel bundles is small
to avoid fuel bundle collision during strong earthquake
ISFSI :Independent Spent Fuel Storage Installation

## Slide 25
<number>
Earthquake (cont.)
AEC requested TPC to submit the seismic action items based on the requirements set forth in section 2.1 and 2.3 of USNRC NTTF report tier 1 recommendation.
4. Referring to the international nuclear safety actions in response of the Fukushima Daiichi nuclear accident, AEC requested TPC to accomplish the following items
(1)Seismic/Tsunami hazard and event scenario simulation
(2)Seismic enhancement for the non-seismic TSC structures
(3)SSCs enhancement evaluation followed by the SSE upgrade from 0.3g to 0.4g for CSNPP
(4)Functionaility upgrade for emergency response facilities including adopting seismic base isolation or damping devices.
(5)Seismic upgrade of plant fire brigade building structures.
(6)Upgrade the raw water reservoir capacity as well as its reliability.
(7)Enhance the power durability of seismic monitoring sensors.
  Conclusions of the regulatory body

## Slide 26
<number>
  Flooding
General Comments:
AEC basically confirms the information and assessments provided by the licensee, especially the information regarding the licensing basis. In general, the assessments of safety margins are acceptable and the resulting action plan for improvements is adequate.
The regulatory body identified additional requests and recommendations to further improve the robustness of the units and the sites:
Referring to the tsunami analysis result by National Science Council and the guidelines or assessment results for tsunami evaluation from major nuclear industrial countries (such as NUREG/CR-6966), the licensee should further review the appropriateness of the design basis tsunamis and take the associated improvements to its nuclear power stations.
Notes: <number>

## Slide 27
<number>
  Flooding (cont.)
The licensee should review the appropriateness of the DBF in FSAR considering the rapid climate changes in the recent years. Associated improvements should be taken to increase the robustness of the plants against flooding. These should be reviewed and approved by the regulatory body through the process of periodic safety review every ten years.
Regarding the ground level of the buildings of Chinshan Power Station, the re-measured elevation (11m)is already 1m lower than the original design value (12m), which might not have enough margin even though it is still larger than the design basis tsunami run-up height (10.7m). Licensee’s action plan of improvements concerning this issue should be envisaged as soon as possible.

## Slide 28
<number>
  Flooding (cont.)
4.TPC should follow the first stage recommendations of USNRC NTTF report, especially the Recommendations 2.1 and 2.3 concerning the flooding and/or tsunami.
5.Referring to the experiences of other nuclear countries, it is recommended that TPC should conduct the following improvements to its nuclear power plant:
(1)a detailed scenario simulation of seismic and tsunami hazard;
(2)building sea walls or reinforced concrete flood barrier walls or watertight facilities to provide better protections against tsunami;
(3)upgrading the watertight capability of doors of buildings containing important equipments, fire-fighting doors as well as pipeline penetrations seals.

## Slide 29
<number>
General Comments:
AEC basically confirms the information and assessments provided by the licensee, especially the information regarding the licensing basis. Generally speaking, the potential consequences of extreme weather conditions (typhoon, storm, heavy rain, etc.) are covered by the major event – flooding. Most of the considered hazards were taken into account in the design basis of the facilities, and are hence not likely to affect the safety functions of the units.
The regulatory body identified additional requests and recommendations in order to further improve the robustness of the facilities when faced with extreme weather conditions:
Given the fact that typhoons of high intensities were observed in the past years in Taiwan, the protection of the buildings containing safety related equipment against projectile should be confirmed in case of a beyond ­design typhoon with wind speed exceeding 70.2 m/s (Beaufort Force 17).
Extreme natural events
Notes: (According to the typhoon intensity classification system of Central Weather Bureau in Taiwan, several typhoons have winds that reach Beaufort Force 16.)

## Slide 30
<number>
Climate changes have caused severe rainfall via the form of typhoons and/or tropical storms in recent years. The licensee should review the appropriateness of the design basis PMP (probable maximum precipitation). Associated improvements of the drainage systems should be envisaged to increase the robustness of the plants against heavy rain. These should be reviewed and approved by the regulatory body through the process of periodic safety review every ten years.
The watertight capability of fire-fighting doors and pipeline penetrations seals should be further investigated and clarified.
A systematic evaluation of combinations of extreme nature events should be performed.
Extreme natural events (cont.)

## Slide 31: Extreme natural events (cont.)
TPC should follow the tier 1 recommendations of USNRC NTTF report, especially Section 2.3 concerning the external natural disasters.
Referring to the experiences of other nuclear countries, it is recommended that TPC should conduct the following evaluations or improvements to its nuclear power stations:
  a quantitative risk assessment concerning the menace of volcanic hazard;
  installation of the second ultimate heat sink.

## Slide 32: Loss of electrical power and loss of ultimate heat sink
The original design of plant power supply system and the enhanced measures to increase robustness after Fukushima accident
General comments on utility reports regarding to Loss of electrical power and loss of ultimate heat sink
Additional areas being identified to further improve the robustness of all the units

## Slide 33
<number>
power sources
Notes: <number>

## Slide 34
Good practice
Seismic Category I
POST-FUKUSHIMA
Portable Equipment
<number>
Enhance mitigation resources – Electric power source
LOOP due to earthquake
AC power supply
DC power supply
Emergency D/G
5th (7Th)
D/G
Air-cooled
G/T
G/T black-start D/G
4.16kV power vehicle
480V portable D/G
Portable generator
Spare battery
S
S
S
S
S
S
S
S
F
F
F
F
F
Response to Fukushima Accident

## Slide 35
<number>
General comments:
The reports of the licensees essentially conform to the ENSREG requirements. The approach adopted by the licensee to re-assess the management of the loss of electrical power and loss of ultimate heat sink complies with the regulations of the ROCAEC that is based on the regulations of the country of the reactor vendor.
The regulatory body identified additional areas to further improve the robustness of all the units:
In response to the Fukushima accident, the AEC requires the TPC to accomplish the following regulatory requirements:
After the SBO event of Higashidori NPS on April 7, 2011, NISA issued a Direction to require at least 2 emergency DGs to be in an operable state all the time even when the reactor is shut down. The same position was adopted by the ROCAEC.
  If one unit is shut down with one EDG under inspection and the swing EDG is assigned to it according to the new requirement, the capability of the swing EDG to back up the other unit is restricted. Envisaged measures to resolve this issue are required.
  Loss of electrical power and loss of ultimate heat sink

## Slide 36
<number>
(2) With respect to the SBO, the TPC is required to establish the equipment, procedures, and training necessary to implement an “extended loss of all AC” time of 72 hours
  for core and spent fuel pool cooling
  for reactor coolant system and primary containment integrity
  The design of the systems supporting the 72-hour extended coping time should cover the same scope of functions as the 8-hour minimum coping time
  It can be based on realistic analysis with reasonable operator action using portable or permanently installed equipment governed by established procedures and training.
  The evaluation should include the technical items of NUMARC 87-00 with all operating states (full power operation, low power operation and shutdown) considered.
  Loss of electrical power and loss of ultimate heat sink
Notes: coping time of 8 hours
DC 24 hours
Mobile 72 hours
<number>

## Slide 37
<number>
(3)In a case of an event caused by an external hazard, all the units on a site may be affected. Sufficient supplies of emergency AC power for coping with such events is essential for enhancing robustness because resources need to be shared. Therefore TPC is required to perform an evaluation regarding to the installation of an additional air-cooled DG or equivalent measures at the NPS.
(4)TPC is required to perform an evaluation regarding to the establishment of an additional alternate heat sink such as the water fed by groundwater wells.
(5)Envisaged measures are required to increase robustness of the plant in dealing with the primary coolant pump seal LOCA issue during SBO (for Maanshan NPP only).
(6) Referring to the emergency management and requirements in Japan, the TPC is required to enhance the off-site power system and increase its reliability.
  Loss of electrical power and loss of ultimate heat sink
Notes: coping time of 8 hours
DC 24 hours
Mobile 72 hours
<number>

## Slide 38
<number>
Ultimate heat sink
Notes: Circulating Water system (CW)
emergency Service water system (ESW)
emergency circulating water system (ECW)
Nuclear Service Cooling Water (NSCW) system
AC- Independent Water Addition (ACIWA)
Spent Fuel Pool Additional Cooling System (SFPACS)

## Slide 39
POST-FUKUSHIMA
Seismic Category I
Portable Supply (additional fire truck/pump)
<number>
Enhance mitigation resources – Diversify water resources
LUHS due to tsunami
AC power supply
DC power supply
Design make-up system
RCIC/HPCI
Manual OP
RAW water make up
Creek/Well/
Lake
Sea Water/
Dam
Onsite Tank
/Condenser
S
S
S
S
F
F
F
F
Alternate
heat sink
Reactor safety cooling
S
S
S
S
S
Response to Fukushima Accident-- BWR

## Slide 42: Injecting Water into Steam Generator
<number>
diesel driven auxiliary feedwater pump
diesel engine fire pump
Fire engines

## Slide 43
RCS Water Makeup by Hydro Test Pump (RCP Seal Injection Path)
Notes: change

## Slide 44
<number>
  Loss of electrical power and loss of ultimate heat sink (cont.)
2. With respect to the SBO, the AEC requires the TPC to strengthen SBO mitigation capability at all operating and new reactors for design-basis and beyond-design-basis external events as it is recommended in item 4 of USNRC NTTF report.
3. Regarding to the nonconventional means, the AEC requires:
(1) The operability of the nonconventional means should be justified on the basis of technical data (design, operation, alignment and connections, periodic testing, preventive maintenance, etc.).
(2) A systematic review of the nonconventional provisions should be performed, focusing on the availability and appropriate operation of plant equipment in the relevant circumstances, taking account of accident initiating events, the extreme external hazards and the potential harsh working environment they may be subject to during the whole period of operation.
(3) Nonconventional means including mobile equipment, fire trucks, etc. should be stored in locations that are safe and secure even in the event of general devastation caused by events (significantly) beyond the design basis. The facilities where the mobile equipment is stored should be evaluated and reinforced if necessary.

## Slide 45
<number>
4.The operability of the URG is required to be justified on the basis of rigorous systematic review and thorough accident analysis. The importance of the justification of the URG is illustrated by the following example:
In BWR, the licensee has applied for measures aimed at using a fire water pump to sustain low-pressure feed to the reactor. These measures require depressurization of the reactor beforehand.
In URG, a two step depressurization strategy has been adopted for prolonged SBO.
  In the early stage of SBO, a slow and controlled depressurization of the reactor is performed while the RCIC is still available.
  In the second stage, a fast and emergency depressurization of the reactor is performed while the RCIC is no longer available.
In this example, the controlled depressurization should not be confused with the emergency depressurization. However, the two terminologies are not well distinguished in the utility’s stress test report.
  Loss of electrical power and loss of ultimate heat sink (cont.)
Notes: Controlled -> orderly
<number>

## Slide 46: Comparisons of Water Injection Systems
<number>
SYSTEM | Quantity and Capacity/each | Design flow/each | Pressure Range | Power
HPCI | 1×100﹪ | 4,250gpm@1120psi | 1120~150psi | DC
SRV | 10×25﹪(Including ADS×5) | 800,000 lb/hr | 1110~50psi | DC
CS | 2×100﹪ | 3,720gpm@113psid | 265~0psi | EDG A/B
LPCI | 4×33.3﹪ | 6,560gpm@20psid | 217~0psi | EDG A/B
CS ECCS design:
CS Alternative water injection:
Chin Shan Station Fire Engines |  |  |  | 
Name | Quantity | Capacity (Liter) | Discharge Pressure | Remark
Fire Foam Vehicle | 1 | 3,000 | 0～20 kg⁄cm2 | Discharge flow rate : 3000 liters/min (792 gpm)＠8.78 kg⁄cm2
Reservoir Vehicle | 1 | 10,000 | 0～20 kg⁄cm2 | Discharge flow rate : 3000 liters/min (792 gpm) ＠ 10.97 kg⁄cm2

## Slide 47
With the slow and controlled depressurization process,
  the reactor can be brought to and maintained at a relatively safe state (namely, a high/normal water level and low pressure state) while at the same time, the RCIC trip set point will not be reached.
  Under this safe state, the impact of the emergency depressurization of the reactor following the failure of RCIC will be minimized and the reactor water inventory can be supplemented by various low pressure injection methods.

## Slide 48
Without the slow and controlled depressurization process
  the reactor is at relatively danger state (namely, a high pressure state), fast depressurization of the reactor will lead to a core uncover even the water level is high before depressurization.

## Slide 49
<number>
5. The hydrogen and containment pressure control strategies in the URG shall take into account various accident scenarios.
6. The TPC is required to study the feasibility of adding the mobile heat exchanger to remove the heat from the containment and/or the reactor.
  Loss of electrical power and loss of ultimate heat sink (cont.)

## Slide 50
<number>
Procedures, training and exercises
AEC required TPC to combine the additional equipment and operations into the procedures or guideline;
AEC required TPC to re-evaluate the feasibility of EOPs and SAMGs with the involvement of new procedures/guidelines;
AEC required TPC to ensure that the SAMGs are appropriate for multi-unit events and to promote them from guidelines to procedures if required;
AEC requests TPC to strength SBO mitigation at operating reactors for design basis and beyond design basis external events;
AEC requests TPC to improve the emergency preparedness staffing and communications per NRC NTTF report.
  Severe accident management

## Slide 51
<number>
The establishment of URGs
TPC needs to identify the URG and its implementation timing, the subsequent measures and monitoring strategy after implementing URG, including the monitor of radioactive releases, backup ability of present systems and equipment, etc.
Multi-event accidents
AEC required TPC to estimate the duration of independent response capability for various severe accidents, beyond design accidents, and multi-event accidents. The materials and equipment in contracting the off-site supports should also be identified.
  Severe accident management (cont.)

## Slide 52
<number>
The improvement of main control room in case of an accident beyond design basis
AEC required TPC to:
ensure the capability of DC power for instrumentation and control systems of MCR, TSC, backup TSC, etc. in case of monitoring unit conditions during SBO accidents. The duties, associations, and implementations of these staffs should also be identified;
improve the seismic level of MCR, TSC, backup TSC, and their inside-equipment;
assess the adequacy of MCR human arrangement in case of multi-unit events.
Design and reliability of containment hardened vent with filters (only for Chinshan NPP)
Per the recommendation item 5.1 in USNRC NTTF report, AEC recommended TPC to add a robust and reliable containment system in Chinshan NPP (Mark-I), in which the hardened vent and filters are involved, for long-term operations in case of extended SBO accidents. The drywell or wetwell hardened vent system shouldn’t be shared with the other units. The hardened vent system will be able to operate either with electrical power or manual operation.
  Severe accident management (cont.)

## Slide 53
<number>
Improvements and integration of EOPs, SAMGs and EDMGs
Per the recommendation item 8 in USNRC NTTF report, AEC recommended TPC to:
  integrate EOPs, SAMGs, and EDMGs;
  identify the commands and control strategies of implementations.
The current severe accident management guidelines are designed for full power condition, which cannot cover the conditions of low power and shutdown. Each nuclear power plant should prepare the response action before revision of current SAMG.
Provide appropriate training and qualification to the decision-maker.
AEC also required TPC to involve the URG into the integration of EOPs, SAMGs, and EDMGs if URG is available.
Spent fuel pool
AEC requests TPC to enhance the spent fuel pool instrumentation per NRC NTTF report.
  Severe accident management (cont.)
Notes: FLEX

## Slide 54
<number>
Thank You
For Your Attention