## Slide 1
Ching-Hui Wu
Department of Nuclear Regulation
Atomic Energy Council, Taiwan
September 23, 2013
An Overview of PRA Activities in Taiwan

## Slide 2: A Brief History of PRA in Taiwan
Major PRA Projects (Main Sponsor) | Periods | Scope* |  |  |  |  |  |  | Application | Task Force Man-year
 |  | L1- P | L1- SM | L1- TY | L1- FR | L1-FL | L1-SD | L2 |  | 
Kuosheng (AEC) | 1983  1985 |  |  |  |  |  |  |  | Base PRA model development | 37 (4.5)#
Maanshan (AEC) | 1985  1987 |  |  |  |  |  |  |  (1992) | Base PRA model development | 27.5 (2.0)#
Chinshan (AEC) | 1988  1990 |  |  |  |  |  |  |  | Base PRA model development | 34.5 (1.0 )#
1st-3 (Taipower) | 1994  1997 |  |  |  |  |  |  |  | Few cases of justification of continued operation | 52
2nd-3 (Taipower) | 1997  2000 | DCR & experience updates (~1999) |  |  |  |  |  | CSET CPET | TIRM (risk monitor) Fire models upgrade PRAM (PRA Maintenance) OLM | 66
3rd-3 (Taipower) | 2000  2003 | DCR & experience updates (~2002) |  |  |  |  |  | LERF | TIRM-2 FT Engine developed NEI-00-02 peer review Chinshan RIFA (Risk-informed Fire Wrapping Alternatives Analysis) RI-ISI pilot | 66
4th-3 (Taipower) | 2004  2007 | DCR & experience updates (~2005) |  |  |  |  |  |  | Lungmen base PRA model SDP tool (PRiSE) developed Follow-on NEI Peer Review Maintenance Rule Implementation | 66
5th-3 (Taipower) | 2008  now | PRA model upgrade |  |  |  |  |  |  | Upgrade to meet ASME/ANS PRA standards and peer review NFPA 805 transition (potential) Typhoon model enhancement | 24
*P: Internal at-power; SM: Seismic; TY: Typhoon; FR: Internal Fire; FL: Internal Flood; SD: Shutdown; L1: Level-1; L2: Level-2 #:from US Consultant |  |  |  |  |  |  |  |  |  | 

## Slide 3: Improvement by the Suggestions from AEC Project
  Generic items:
  A.C. power reliability improvement (5th DG, G/T building)
  Emergency operating procedure improvement
  Prevention of ATWS and operator training after ATWS
  Fire protection Improvement
  Enhance seismic design
  Control room, SRV´s accumulator (CS)
  Sluice gates, EChW/NChW hold down bolts (KS)
  D.C. battery racks (MS)
  CS:
  Improve instrument air system
  Prevention of miscalibration of low-pr injection permission
  KS:
  Change 69KV switchyard to GIS
  HPCS/RCIC suction changeover
  Add H2 control system inside containment
  Replacing instrument junction boxes with in-line crimping
  MS:
  NSCW system and pump vibration
  CCW system and heat exchanger improvement
  EChW system and heat exchanger improvement
  Turbine driven AFW pump room cooling improvement
  4.16KV switchgear room flooding protection improvement

## Slide 4: On-going PRA Applications
RI-ISI program plans development for all three operating NPPs
  Kuosheng had made the first submittal in early 2012
  Maanshan’s submittal in last July is under reviewed
Base PRA models enhancement, including the Lungmen NPP, to meet ASME internal events standard (ASME/ANS 2009)
  Objective: Capability Category II in general
  Development of Internal events and internal floods PRA models for Chinshan, Kuosheng, Maanshan
  Fire PRA for Chinshan NPP
  Fire PRA for Kuosheng and Maanshan NPPs
Draft of the Fire Protection Guidelines for NPPs
  Supporting potential future NFPA-805 transition activities
Notes: <footer>
<header>
<date/time>
最後報告PRA應用未來的展望
因為台電推動PRA應用已有一段不算短的時間
總是有幾個展望,首先希望[1] 大會審查能順利完成 亦希望[2]由目前申請方式改為[]以減化申請及審查程序
目前大會OLM實施要點侷限RHR,ECW/ESW, EchW,LPCS/CS等少數系統,希望將來擴大申請範圍至其他系統如[D/G],以美國電廠OLM經驗為例.D/G OLM尚需配合AOT放寬:AOT放寬才能一次完成緊急柴油發電機線上維修工作,否則OLM效果將大打折扣.NRC已核准D/G AOT由三天延長為十四天(緊要海水系統及緊要寒水系統允許不可用時間由三天延為七天)
其他如[]係有關ILRT及LLRT之規定,ILRT LLRT符合RIPB準則,其Failure並不會造成立即的安全顧慮,且美國研究顯示 ILRT,LLRT僅影響3%的風險,現行10年3次ILRT及每次大修執行LLRT,影響電廠有限的資源分配.美國電廠目前沒有不採用Option規定的,採用option B ILRT將放寬至5年一次甚至10年一次
未來的應用方向還有[][]等等
今天我的報告到這裡,謝謝大家

## Slide 5: On-going PRA Applications (Con’d)
SDP tool (i.e. PRiSE) kernel update and enhancement
  internal at-power, SD, seismic and typhoon
Supporting Maintenance Rule implementation
  Tools for MR process and Integrated scheduling and risk monitoring
ASME/ANS PRA standards introduction
  L-1 Internal events at-power, Seismic events, Internal fires
  Screening of other external hazards

## Slide 6: ASME/ANS PRA standards
Part | Requirements | Timetable | NPPs
2 | Internal events at power PRA | 2008.12-2011.12 | CS, KS, MS
3 | Internal flood at power PRA | 2008.12-2011.12 | CS, KS, MS
4 | Fires at power PRA | 2009.12-2012.11 2013.10-2017.10 | CS KS, MS
5 | Seismic events at power PRA | 2012.07-2014.06 | CS, KS, MS
6 | Screening and conservative analysis of other external hazards at power | 2012.12-2015.11 | CS, KS, MS
7 | High wind events at power PRA |  | 
8 | External flood events at power PRA |  | 
9 | Others external hazards at power PRA |  | 
10 | Seismic margin assessment at power | 2011.07-2013.12 | CS, KS, MS
TPC will update the LP&SD, L2 and L3 models based on the dedicated ASME PRA standards.

## Slide 7: Summary of PRA Applications in Progress
Stress test supporting evaluation
  Fukushima follow-on
Update of the Seismic PRA models
  New earthquake evidences and faults re-classification
Development of other external events PRA models
  e.x. external floods including tsunami event
Supporting self management of On-line Maintenance
  OLM program plans of the 3 operating NPPs had all been approved docketed by AEC in 2011
  Risk assessment supporting (a)(4) activities

## Slide 8
Thanks for Your Attention