## Tabelle1
Implementation status of Post-Fukushima orders in Taiwan’s nuclear power plants
issued by AEC: 2013/10/01
| Name | Keywords | Original | CS | KS | MS | LM | Date | Text
1 | XX-JLD-10101 | seismic hazard | NTTF 2.1 | Jun 2014 | Jun 2014 | Jun 2014 | before fuel loading | 2012-11-05 | Requiring seismic hazard re-evaluations implementing the recommendation from the United States Nuclear Regulatory Commission (USNRC) Near Term Task Force (NTTF) Report Tier 1 recommendation 2.1 to conduct seismic and flood hazard re-evaluations.
2 | XX-JLD-10102 | flood hazard | NTTF 2.1 | Jun 2014 | Jun 2014 | Jun 2014 | before fuel loading | 2012-11-05 | Requiring flood hazard re-evaluations implementing the USNRC NTTF Report Tier 1 recommendation 2.1 to conduct seismic and flood hazard reevaluations.
3 | XX-JLD-10103 | seismic and flooding risk | AEC | Jun 2016 | Jun 2016 | Jun 2016 | before fuel loading | 2012-11-05 | Requiring TPC to simulate the mechanism of seismic and tsunami hazards and the resulting risks based on comments from an AEC review meeting.
4 | XX-JLD-10104 | DBT + 6m | J regulator + AEC | Dec 2016 | Dec 2016 | Dec 2016 | Dec 2016 | 2012-11-05 | Requiring the enhancement of the water tightness of buildings (or build seawall, or tidal barrier) to a level of 6 meters above current licensing bases based on the actions being taken at Japanese NPPs and as referred to in the USNRC NTTF Report, to address the uncertainty from the original design basis tsunami height by adding 6 meters of protection.
5 | XX-JLD-10105 | EE walkdowns | NTTF 2.3 | Mar 2013 | Mar 2013 | Mar 2013 | before fuel loading | 2012-11-05 | Requiring seismic, flood and others external events walkdowns consistent with the USNRC NTTF Report Tier 1 recommendation 2.3 to conduct seismic and flood walkdowns.
6 | XX-JLD-10106 | SBO rule | NTTF 4.1 | 6 months after NRC rulemaking | 6 months after NRC rulemaking | 6 months after NRC rulemaking | 6 months after NRC rulemaking | 2012-11-05 | Requiring TPC to take actions to address station blackout (SBO) consistent with the USNRC NTTF Report Tier 1 recommendation 4.1 on SBO regulatory actions.
7 | XX-JLD-10107 | 2 EDGs always | J regulator | Dec 2013 | Dec 2013 | Completed at Aug 2013 | Dec 2013 | 2012-11-05 | Requiring more than 2 emergency diesel generators (EDGs) to be in an operable state all the time even when the reactor is shut down so that if one unit is shut down with one EDG under maintenance and the swing EDG is assigned to it according to the new requirement, the capability of the swing EDG to back up the other unit is restricted.
8 | XX-JLD-10108 | DC 8h, 24h load shedding | AEC | completed | Jan. 2014, Oct. 2014 | Nov. 2016, April 2017 | End 2013 | 2012-11-05 | Requiring TPC to enhance emergency DC power supply to secure the batteries storage capacity of at least 8 hours without isolating the load and at least 24 hours after the unnecessary loads are isolated.
9 | XX-JLD-10109 | SBO coping 24h | AEC | AEC requests TPC to submit the proposal, including the completion schedule, at end of 2013 in the order issued in Nov. 2012. | AEC requests TPC to submit the proposal, including the completion schedule, at end of 2013 in the order issued in Nov. 2012. | AEC requests TPC to submit the proposal, including the completion schedule, at end of 2013 in the order issued in Nov. 2012. | AEC requests TPC to submit the proposal, including the completion schedule, at end of 2013 in the order issued in Nov. 2012. | 2012-11-05 | Requiring TPC to extend the SBO coping time to at least 24 hours based on specific issues for Taiwan's NPP in that the original requirements of USNRC Regulatory Guide (RG) 1.155 do not include the effects resulting from earthquake and tsunami.
10 | XX-JLD-10110 | 6th (8th) EDG/GT | AEC | Dec 2013 | Oct 2013 | Feb 2015 | before op. license | 2012-11-05 | Requiring TPC to install an extra seismic qualified gas-cooled EDG at high elevation for each NPP to address specific defence-in-depth issues with electrical power supplies for Taiwan. AEC accepts the alternatives for this order to provide the water-tightness of 5th EDG building.
11 | XX-JLD-10111 | Alternate UHS | ENSREG | Jan. 2015 | TPC has submit the proposal, under AEC review | TPC has submit the proposal, under AEC review | June 2015 | 2012-11-05 | Requiring TPC to install an alternate ultimate heat sink (UHS) consistent with recommendations from the ENSREG action plan.
12 | XX-JLD-10112 | B.5.b | USNRC | completed | completed | completed | before fuel loading | 2012-11-05 | Requiring TPC to implement the actions of the USNRC's Post-9/11 action (B.5.b) to stage response equipment on or near site to respond to extreme external events (see USNRC 10 CFR 50.54(hh)(2)).
13 | XX-JLD-10113 | equipment SBO | NTTF 4.2 | Apr 2016 | Aug 2016 | Apr 2016 | before fuel loading | 2012-11-05 | Requiring TPC to address the USNRC NTTF Report Tier 1 recommendation 4.2 on equipment covered under USNRC regulation 10 CFR 50.54(hh)(2).
14 | XX-JLD-10114 | hardened vent + filtered venting | NTTF 5.1 + AEC | May 2016, May 2017 | Dec. 2016, April 2016 | Nov. 2016, April 2017 | Dec 2015 (unit 1) | 2012-11-05 | Requiring TPC to install reliable hardened vents for Mark I and ABWR containments and request the installation of filtration for all different containment designs consistent with the recommendation of USNRC NTTF Report Tier 1 recommendation 5.1 on reliable hardened vents for BWR Mark I and Mark II containments.
15 | XX-JLD-10115 | SFP instrumentation | NTTF 7.1 | Dec. 2014, May 2014 | May 2015, April 2016 | April 2015, Dec. 2015 | before fuel loading | 2012-11-05 | Requiring TPC to install spent fuel pool (SFP) instrumentation consistent with the recommendation of the USNRC NTTF Report Tier 1 recommendation 7.1 on SFP instrumentation.
16 | XX-JLD-10116 | procedures incl. URG | NTTF 8 | 6 months after NRC rulemaking | 6 months after NRC rulemaking | 6 months after NRC rulemaking | 6 months after NRC rulemaking | 2012-11-05 | Requiring TPC to strengthen and integrate the emergency operating procedures (EOPs), severe accident management guidelines (SAMGs), and extensive damage mitigation guidelines (EDMGs) with the ultimate response guidelines (URGs) developed by TPC following the accident at Fukushima Daiichi NPP consistent with the USNRC NTTF Report Tier 1 recommendation 8 on strengthening and integration of EOPs, SAMGs, and EDMGs.
17 | XX-JLD-10117 | volcanic PRA | AEC | TPC has submit the proposal, under AEC review | TPC has submit the proposal, under AEC review | TPC has submit the proposal, under AEC review | TPC has submit the proposal, under AEC review | 2012-11-05 | Requiring TPC to perform a volcanic probabilistic risk assessment (PRA) for its NPPs and to study the impacts from ash dispersion based on comments during a high-level review meeting.
18 | XX-JLD-10118 | water-tight fire doors for el.equip. | AEC + J reg | April 2014 | Dec 2014 | Dec 2014 | Dec 2015 | 2012-11-05 | Requiring TPC to enhance the water-tightness of the fire doors of essential electrical equipment rooms based on specific concerns with the location of the equipment at Taiwan's NPPs and recommendations from the Japanese regulatory body for NPPs in Japan.
19 | XX-JLD-10119 | BDBE resistance fire brigade bdg | AEC | Evaluation completed by Dec. 2013 | Evaluation completed by Oct. 2013 | Evaluation completed by Dec. 2013 | Evaluation completed by Sep. 2013 | 2012-11-05 | Requiring TPC to enhance the seismic resistance for the fire brigade buildings to cope with beyond design basis earthquake (BDBE) conditions to address specific issues for Taiwan's NPPs and a good practices from EU peer reviews.
20 | XX-JLD-10120 | reliability offsite power | AEC + J reg | Dec 2015 | Feb 2016 | Feb 2014 | TPC has submit the proposal, under AEC review | 2012-11-05 | Requiring TPC to improve the reliability of offsite power supplies to address specific issues for Taiwan's NPPs and recommendations from the Japanese regulatory body for NPPs in Japan.
21 | XX-JLD-10121 | Seismic raw water res. + impermeable liner | AEC + J reg | TPC has submit the proposal, under AEC review | TPC has submit the proposal, under AEC review | TPC has submit the proposal, under AEC review | TPC has submit the proposal, under AEC review | 2012-11-05 | Requiring TPC to improve the seismic resistance of raw water reservoirs at the NPPs and to consider the installation of impermeable liners to address specific issues for Taiwan's NPPs and consistent with the measures being taken by TEPCO in Japan to install impermeable liners.
22 | XX-JLD-10122 | PARs | ENSREG | TPC has submit the proposal, under AEC review | TPC has submit the proposal, under AEC review | Dec 2016 | TPC has submit the proposal, under AEC review | 2012-11-05 | Requiring TPC to install passive autocatalytic recombiners (PAR) to prevent hydrogen explosions consistent with recommendations in the ENSREG action plan.
23 | CS-JLD-101101 | requal to 0.4g | AEC | Dec 2016 | - | - | - | 2012-11-05 | An Order of the Executive Yuan, requiring TPC to conduct an enhancement evaluation of safety related structures, systems and components (SSCs) for the Chinshan Nuclear Power Plant followed by the upgrading of the licensing basis safe shutdown earthquake (SSE) from 0.3g to 0.4g for specific SSCs relied upon to respond to an accident.
24 | MS-JLD-101301 | RCP seal LOCA | AEC + ENSREG | - | - | TPC has submit the proposal, under AEC review | - | 2012-11-05 | Requiring TPC to address the issue with the PWR reactor coolant pump (RCP) seal loss-of-coolant-accident leakage issue for Maanshan Nuclear Power Plant consistent with the ENSREG action plan.
1 | HQ-JLD-1013001 | EPZ | AEC | Completed | Completed | Completed | Completed | 2012-11-05 | Requiring TPC to update "radiation protection measures and planning for the residents within emergency planning zone (EPZ) of Nuclear power plant" in response to the expanded EPZ from 5 km to 8 km based on the lessons learned from Fukushima accident for all nuclear plants in Taiwan.
2 | XX-JLD-1013002 | staffing and communication for EP | NTTF 9.3 | Aug 2013 | End 2013 | Sep 2013 | End 2013 | 2012-11-05 | Requiring TPC to addressing staffing and communications issues for emergency preparedness consistent with the USNRC NTTF Report Tier 1 recommendation 9.3 on emergency preparedness regulatory actions.
| XX-JLD-1013004 | staffing and communication for EP | NTTF 9.3 | Aug 2013 | End 2013 | Sep 2013 | End 2013 | 2012-11-05 | Requiring TPC to addressing staffing and communications issues for emergency preparedness consistent with the USNRC NTTF Report Tier 1 recommendation 9.3 on emergency preparedness regulatory actions.
3 | XX-JLD-10104(DNT) | seismic reinforced TSC | AEC | submittal under AEC review | Jan. 2014 | Oct. 2013 | - | 2012-11-05 | Requiring TPC to reinforce the structure of the existing non-seismically qualified technical support centre (TSC) used for emergency response to address specific seismic concerns of the NPPs in Taiwan.
4 | XX-JLD-1013003 | new seismically isolated TSC | J reg + IAEA | - | End 2015 | End 2015 | before fuel loading | 2012-11-05 | Requesting TPC to consider building a seismically isolated TSC building based on the practice being implemented in Japan in light of the accident at Fukushima Daiichi NPP and consistent with lessons learned provided by the International Atomic Energy Agency.
1 | RL-JLD-1012042 | 40 mobile detection equipment | AEC | End 2013 | End 2013 | End 2013 | End 2013 | 2012-11-05 | Requiring TPC to procure 40 mobile detection equipment with automatic data transmission capability for four NPPs to enhance capability of radiation fallout monitoring in a timely manner.
2 | RL-JLD-1012043 | 13 radiation monitor. stations in EPZ | AEC | End 2013 | End 2013 | End 2013 | End 2013 | 2012-11-05 | Requiring TPC to install 13 radiation monitoring stations within the EPZ of NPPs to set up a radiation monitoring preparedness platform and strengthen radiation monitoring capability.
3 | RL-JLD-1012044 | vehicles for mobile detection equipment | AEC | July 2013 | July 2013 | July 2013 | July 2013 | 2012-11-05 | Requiring TPC to procure four radiation detection vehicles to enhance mobile radiation monitoring capability.
1 | XX-JLD-10201 | fault displacement analysis | NEA | submit before July 2013, under review | submit before July 2013, under review | submit before July 2013, under review | submit before July 2013, under review | 2013-06-06 | Requiring TPC to conduct fault displacement analysis for new evidences of Shanchiao and Hengchun Faults near (within a radius of 8 km) the nuclear power plants.
2 | XX-JLD-10202 | interface post-earthquake and post-tsunami proc. | NEA | submit before July 2013, under review | submit before July 2013, under review | submit before July 2013, under review | submit before July 2013, under review | 2013-06-06 | Requiring TPC to provide the interface between existing post-earthquake and post-tsunami operating procedures of NPPs.
3 | XX-JLD-10203 | event combination flooding and natural EE | NEA | submit before July 2013, under review | submit before July 2013, under review | submit before July 2013, under review | submit before July 2013, under review | 2013-06-06 | Requiring TPC to systematically assess the combinations of events in the areas of flooding and extreme natural events at NPPs.
4 | XX-JLD-10204 | PMP with topo. maps | NEA | submit before July 2013, under review | submit before July 2013, under review | submit before July 2013, under review | submit before July 2013, under review | 2013-06-06 | Requiring TPC to examine the probable maximum precipitation with regional topographical maps of NPPs.
5 | HQ-JLD-10201 | local seismic network small earthquakes | NEA | - | - | - | - | 2013-06-06 | Requiring TPC headquarters to deploy a local seismic network (one in the north and one in the south) to capture small earthquakes in order to understand whether or not the pattern of the epicenters indicate correlation with postulated tectonic features.
item HQ-JLD-10201 just for headquater of TPC, submit before July 2013, under review
Note on B43: AEC: submit before July 2013, under review (for headquater of TPC)