## Tabelle1
Implementation status of envisaged measures of the National Report
submitted by AEC: 03/09/2013
Answer to mail of PRT to AEC of 15/08/2013
Implementation status of envisaged measures | [7 empty] | Date:September 3, 2013
Chapter | Number | NPP | Item | A (analysis) P (procedure) H (hardware measure) | implementation status |  |  |  | comment (only if necessary, e.g. link to the items of ENSREG "Compilation of recommendations and suggestions")
[5 empty] | com-pleted | in progress | sche-duled comple-tion date (year) | in consider-ation
2.2.1.2 | 1 | CS | Gas Turbine seismic enhancement program | A | x
2.2.1.2 | 2 | CS | additional boron is procured and its mobile injection measure | PH | x
2.2.1.2 | 3 | CS | nitrogen gas bottles and mobile air compressors | H | x
2.2.1.2 | 4 | CS | mobile injection equipment | H | x
2.2.1.2 | 4 | CS | Review of Ultimate Heat Sink | PH |  | x | JLD-10111
2.2.1.2 | 4 | CS | seismic enhancement of raw water reservoir | A | x |  | JLD-10121 under review
2.2.1.2 | 4 | CS | seismic enhancement of RCIC and RHR B injection paths | A | x
2.2.1.2 | 4 | CS | seismic enhancement of RCIC and RHR B injection paths | H |  | x | #1 2014.11 #2 2014.03
2.2.1.2 | 1 | KS | Gas Turbine seismic enhancement program | A | x
2.2.1.2 | 2 | KS | RCIC system (including I&C and control power) seismic enhancement | A | x
2.2.1.2 | 2 | KS | RCIC system (including I&C and control power) seismic enhancement | H |  | x | Dec. 2017
2.2.1.2 | 2 | KS | manual startup of RCIC | P | x
2.2.1.2 | 3 | KS | seismic enhancement of RCIC and RHR B injection paths | A | x
2.2.1.2 | 3 | KS | seismic enhancement of RCIC and RHR B injection paths | H |  | x | Dec. 2017
2.2.1.2 | 4 | KS | mobile air compressors | H | x
2.2.1.2 | 4 | KS | installation of an additional emergency air charging pipe with connector | H | x
2.2.1.2 |  | MS | upgraded seismic fragility for gas turbine generator | A | x
2.2.1.2 |  | LM | Shorten the time needed to establish fire water flow path | P | x
2.2.1.2 |  | LM | Upgrade the seismic capability of raw water system | H |  | x | JLD-10121 Dec. 2014
2.2.1.2 |  | LM | Intake from raw water system through fire water pump | P | x
2.2.3.3 | 1.(1) | CS | upgraded the seismic resistance for the 100,000 metric ton and two sets of 3000 metric ton raw water reservoirs structures | A | x |  | JLD-10121 under review
2.2.3.3 | 1.(2) | CS | installed baffle plate on the entrance and exit in each essential building | H | x
2.2.3.3 | 2.(1) | CS | monitoring of the two Streams | P | x
2.2.3.3 | 2.(2) | CS | mudslide warning alert | P | x
2.2.3.3 |  | KS | installed baffle plate for the Gas Turbine Building and Diesel Generator Building | H | x
2.2.3.3 |  | MS | upgrade seismic resistance of raw water storage reservoirs, firefighting water tank | H |  | x | JLD-10121 Dec. 2014
2.2.3.3 |  | LM | install baffle plates at the external gates on ground floor of each important building | H |  | x | Before Fuel Loading
3.1.3.3 |  | CS | ground elevation at Chinshan Power Plant is 80cm lower than the original designed elevation (12 m) | P | x
3.1.3.3 |  | KS | install water-proof walls for emergency circulating water pump (ECW), and watertight doors | H | x
3.1.3.3 |  | LM | Small leakage has been found on the penetration holes on the underground exterior walls of control building | H | x
3.1.3.3 |  | LM | the sealing material for openings of the RBSW pump houses | H | x
3.1.3.3 |  | LM | The integrity of the RBSW pump house structure as the dynamic force from tsunami | A | x
3.1.3.4 | 1 | CS | DCR-C0-3307 | H | x
3.1.3.4 | 2 | CS | DCR-C0-308 | H | x
3.1.3.4 | 3 | CS | DCR-C0-3283 | H | x
3.1.3.4 | 4 | CS | MMR-C0-0407 (5th EDG) | H |  | x | Dec. 2013
3.1.3.4 | 5 | CS | MMR-C0-0416 | H | x
3.1.3.4 | 1 | KS | install 63 flood barrier plates at the openings of important equipment buildings | H |  | x | Dec. 2014
3.1.3.4 | 2.1 | KS | DCR-K0-3886 | H | x
3.1.3.4 | 2.2 | KS | DCR-K0-4057 | H | x
3.1.3.4 | 2.3 | KS | DCR-K1-4074/K2-4075 | H | x
3.1.3.4 | 2.4 | KS | DCR-K1-4043/K2-4044 | H | x
3.1.3.4 | 2.5 | KS | MMR-K0-257 | H | x
3.1.3.4 | 2.6 | KS | MMR-K0-259 | H | x
3.1.3.4 | 1 | MS | DCR-M0-4275 | H | x
3.1.3.4 | 2 | MS | DCR-M0-4276 | H | x
3.1.3.4 | 3 | MS | DCR-M0-4277 | H | x
3.1.3.4 | 4 | MS | DCR-M0-4285 | H | x
3.1.3.4 | 5 | MS | MMR- M0-0672 | H | x
3.1.3.4 | 6 | MS | MMR-M0-0683 | H | x
3.1.3.4 | 7 | MS | MMR-M0-0732 | H |  | x | Dec. 2014
3.1.3.4 | 8 | MS | MMR-M1-0733/MMR-M2-0734 | H |  | x | Dec. 2014
3.1.3.4 | 9 | MS | MMR-M1-0735/MMR-M2-0736 | H |  | x | Dec. 2014
3.1.3.4 | 10 | MS | MMR-M1-0737/MMR-M2-0738 | H |  | x | Dec. 2014
3.1.3.4 | 11 | MS | MMR-M1-0739/MMR-M2-0740 | H | x
3.1.3.4 | 1.(1) | LM | Adding water-tight doors in reactor building | [5 empty] | this item will be deleted due to status change
3.1.3.4 | 1.(2) | LM | Install flood barrier plates of 1 meter high | H |  | x | Before Fuel Loading
3.1.3.4 | 2 | LM | RAP-LM-01-12-001 | H |  | x | JLD-10110 May 2015 |  | before the operating license
3.1.3.4 | 3 | LM | mobile drainage pumps | H | x
3.2.3 | 1 | CS | build seawall | H |  | x | Dec. 2016
3.2.3 | 2, 5 | CS | flooding walkdown | A | x
3.2.3 | 3 | CS | Six flood gates | PH | x
3.2.3 | 4 | CS | tsunami protection of ESW system | A | x
3.2.4 | 4 | CS | tsunami protection of ESW system | H |  | x | Dec. 2016
3.2.3 | 6 | CS | procured 8 gasoline/diesel-driven drainage pumps | H | x
3.2.3 | 7 | CS | mudslide monitoring | P | x
3.2.3 | 8 | CS | MMR-C0-0407 (seawall) | H |  | x | Dec. 2016
3.2.3 | 1 | KS | build seawall | H |  | x | Dec. 2016
3.2.3 | 2 | KS | watertight of ECW pump room | H | x
3.2.3 | 3 | KS | Preliminary assessmentof the flooding design | A | x
3.2.3 | 4 | KS | mudslide warning, prevention, and mitigation | P | x
3.2.3 | 6 | KS | flooding walkdown | A | x
3.2.3 | 7 | KS | install flood protection walls or rubber packing at entrance/exit doors or roller shutter doors of all main equipment buildings | H |  | x | Dec. 2014 |  | Change to "install flood barrier plates at the openings of important equipment buildings"
3.2.3 | 8 | KS | procured 6 engine-driven, mobile and submersible pumps | PH | x
3.2.3 | 1 | MS | build seawall | H |  | x | Dec. 2016
3.2.3 | 1 | MS | installing grid covers at the service water intake pool | H | x
3.2.3 | 1 | MS | watertight doors and flood barrier plates in the motor area of the NSCW pump rooms | H | x
3.2.3 | 2 | MS | Preliminary assessmentof the flooding design | A | x
3.2.3 | 2 | MS | install 1 meter high flood barrier plates at the openings of important buildings | H |  | x | Dec. 2014
3.2.3 | 3 | MS | to evaluate the feasibility of installing flood protection plates at doors of safety related buildings | A | x
3.2.3 | 3 | MS | improvement program to increase water-tightness of critical fire-proof doors or explosion-proof doors at safety related buildings | H |  | x | JLD-10118
3.2.3 | 4 | MS | procured 30 diesel engine drainage pumps | H | x
3.2.3 | 5 | MS | procured a fire truck with water tank | H | x
3.2.3 | 1 | LM | protection against very heavy rain or typhoons | P | x
3.2.3 | 2 | LM | Preliminary assessmentof the flooding design | A | x
3.2.3 | 3 | LM | install flood barrier plates or fill rubber packing at entrance/exit doors or roller shutter doors of all main equipment buildings | H |  | x | Before Fuel Loading |  | Change to "Install flood barrier plates of 1 meter high"
3.2.3 | 4 | LM | mobile drainage pumps | PH | x
4.1.3 | 1 | CS | Response measures to extreme weather | P | x
4.1.3 | 2.(1) | CS | installed with grids, fixed screens of ESW intake | H | x
4.1.3 | 2.(2) | CS | routine and post-natural disaster walkdown inspection procedure | P | x
4.1.3 | 2.(3) | CS | mobile equipment and procedure | PH | x
4.1.3 | 2.(4) | CS | mobile drainage pumps | H | x
4.1.3 | 2.(5) | CS | MMR-C0-0407 | H |  | x | Dec. 2013
4.1.3 | 2.(6) | CS | procured additional diesel generators | H | x
4.1.3 | 2.(7) | CS | procured one 4.16kV mobile diesel generators | H | x
4.1.3 | 2.(8) | CS | power loading management procedure | P | x
4.1.3 | 1 | KS | Response measures to extreme weather | P | x
4.1.3 | 2.(1) | KS | install flood barrier panels at the gate of the security booth and southeast gate of the plant | H |  | x | Dec. 2014
4.1.3 | 2.(2) | KS | install 1-meter high flood barrier panels at entrances/exits of main buildings | H |  | x | Dec. 2014
4.1.3 | 2.(3) | KS | Mitigation equipment (such as drainage pumps) is placed at high locations | P | x
4.1.3 | 1 | MS | Response measures to extreme weather | P | x
4.1.3 | 2.(1) | MS | grating cover installed on top of the intake pool of NSCW pump house. Watertight motor rooms. | H | x
4.1.3 | 2.(2),2.(3) | MS | procedures | P | x
4.1.3 | 2.(4) | MS | mobile equipment and procedure | PH | x
4.1.3 | 2.(5) | MS | mobile equipment | H | x
4.1.3 | 2.(6) | MS | enhance waterproof capability of electrical equipment room in control building | A |  | x | JLD-10118 Dec. 2014
4.1.3 | 2.(7) | MS | mobile drainage pumps | H | x
4.1.3 | 2.(8) | MS | mobile diesel generators | H | x
4.1.3 | 2.(9) | MS | 4.16 kV mobile diesel generators | H | x
4.1.3 | 1 | LM | Response measures to extreme weather | P | x
4.1.3 | 2.(1) | LM | adds flood barrier plates | H |  | x | Before Fuel Loading |  | (Install flood barrier plates of 1 meter high)
4.1.3 | 2.(2) | LM | procedures | P | x
5.1.2.3 | 1 | CS | flood barrier panels will be installed at doors and openings of the buildings of unit 1, unit 2, 5th EDG and ESW pump room | H |  | x | Dec. 2013
5.1.2.3 | 2 | CS | SFPACS is regarded as an alternative RHR system | A | x
5.1.2.3 | 3 | CS | procedures | P | x
5.1.2.3 | 4 | CS | Enhanced measures to provide emergency AC power | PH | x
5.1.2.3 | 5 | CS | RCIC Emergency DC power | P | x
5.1.2.3 | 6 | CS | Mobile Injection Equipment | H | x
5.1.2.3 | 1 | KS | Enhanced measures (Flood barrier panels) for EDG Building waterproofing | H |  | x | Dec. 2014
5.1.2.3 | 2 | KS | Enhanced measures for ECW pump Room waterproofing | H | x
5.1.2.3 | 3 | KS | Power supply enhancement | PH | x
5.1.2.3 | 4 | KS | Enhancement of the emergency operation capability of RCIC & SRV | PH | x
5.1.2.3 | 5 | KS | Enhancement of reactor water makeup capability | PH | x
5.1.2.3 | 1 | MS | to install flood barrier panel at the gates of the buildings enclosing safety-related systems. | H |  | x | Dec. 2014 |  | ( install 1 meter high flood barrier plates at the openings of important buildings)
5.1.2.3 | 1 | MS | to improve the water-tight capability for the fire protection door or explosion protection door of buildings with safety-related systems | H |  | x | JLD-10118
5.1.2.3 | 2 | MS | seismic evaluation of gas turbine-generator and raw water reservoir | A | x
5.1.2.3 | 2 | MS | seismic evaluation of raw water reservoir | H |  | x | Dec. 2014
5.1.2.3 | 3 | MS | a safe crane parking point and a crane locking device | H | x
5.1.2.3 | 4 | MS | capacity of battery sets | H | x |  |  |  | purchase 480V mobile DG can charge battery sets
5.1.2.3 | 5 | MS | 5th air-cooled diesel generator to provide emergency AC power to both units simultaneously | PH | x
5.1.2.3 | 6 | MS | EDGs of each unit can support each other | P | x
5.1.2.3 | 7 | MS | mobile 4.16kV diesel generators and connectors | H | x
5.1.2.3 | 8 | MS | 480V mobile diesel generators and connectors | H | x
5.1.2.3 | 9 | MS | small mobile generators | H | x
5.1.2.3 | 10 | MS | water tanker fire engines, Offsite water sources | PH | x
5.1.2.3 | 11 | MS | mobile air compressors | H | x
5.1.2.3 | 1 | LM | flood barrier panel installation and door seal rubber modification | H |  | x | Before Fuel Loading |  | door seal rubber modification changed to install flood barrier plates of 1 meter high
5.1.2.3 | 2.(1) | LM | Construction of two gas turbine generators | H |  | x | JLD-10110 May 2015 |  | before the operating license
5.1.2.3 | 2.(2) | LM | Black-start diesel generators of G/T to provide power to 4.16kV Bus | H |  | x | May 2015
5.1.2.3 | 2.(3) | LM | 4.16kV mobile generators | H | x
5.1.2.3 | 2.(4) | LM | 11.4kV security system EDG to provide power to 4.16kV Bus | H | x
5.1.2.3 | 2.(5) | LM | Swing EDG simultaneously provides power to both units | P | x
5.1.2.3 | 2.(6) | LM | Unit 1 EDGs and Unit 2 EDGs can support each other in case of emergency | P | x
5.1.2.3 | 2.(7) | LM | 480V mobile diesel generators | H | x
5.1.2.3 | 3 | LM | the duration of DC power supply to RCIC and SRV/ADS can be extended to 24 hours with load shedding | P | x
5.1.3.5 | 1 | CS | Operation of RCIC/HPCI without DC supply (manual startup) | P | x
5.1.3.5 | 1 | KS | Enhancement of the emergency operation capability of RCIC & SRV | PH | x
5.1.3.5 | 1 | MS | the duration of DC power supply can be extended with load shedding | P | x
5.1.3.5 | 2 | MS | mobile diesel generators | H | x
5.1.3.5 | 1 | LM | RCIC loss of DC power (manual start) | P | x
5.1.3.5 | 2 | LM | 480 VAC mobile diesel generator | H | x
5.1.3.5 | 3 | LM | mobile equipment and procedure | PH | x
5.1.4.3 | 1 | CS | Ultimate Heat Sink Enhancement - spare ESW motors | PH | x
5.1.4.3 | 2 | CS | Increase heat removable path - SFPACS connected to RHR system | H |  |  |  | x
5.1.4.3 | 3 | CS | Reactor water make-up | H |  | x | Dec. 2014
5.1.4.3 | 4 | CS | containment venting capability | H |  | x | May 2017
5.1.4.3 | 5 | CS | Makeup water source structure integrity evaluation and enhancement | H | x
5.1.4.3 | 1 | KS | Enhancement of the heat removal capability of primary containment | P | x
5.1.4.3 | 2 | KS | Enhancement of ECW | PH | x
5.1.4.3 | 1 | MS | Steel grids was installed on the top of NSCW intake pool | H | x
5.1.4.3 | 2 | MS | water-proof walls and water-tight doors of NSCW pumps | H | x
5.1.4.3 | 4 | MS | trash is removed manually at NSCW intake | P | x
5.1.4.3 | 6 | MS | spared NSCW pump motors | PH | x
5.1.4.3 | 7 | MS | water tank fire engines | H | x
5.1.4.3 | 1 | LM | Ultimate Heat Sink Enhancement - spare motors | PH | x
5.1.4.3 | 3 | LM | Reactor water make-up - mobile diesel generators, temporary pump | H | x
5.1.4.3 | 4 | LM | Primary/Secondary containment venting - mobile diesel generators and necessary components | H | x
5.1.4.3 | 5 | LM | Make up water source structure integrity evaluation and enhancement | H |  | x | Dec. 2014
5.1.5.3 | 2 | MS | Containment standby water injection - fire engines | H | x
5.1.5.3 | 6 | MS | mobile diesel generators | H | x
5.1.5.3 | 8. (1) | MS | seismic capability and integrity of raw water reservoir and connected piping | H |  | x | Dec. 2014
5.1.5.3 | 8. (2) | MS | above-ground raw water pipeline | H | x
5.1.5.3 | 8. (3) | MS | seismic improvement of raw water pipes | H |  | x | Dec. 2014
5.2.3.5 | 1 | CS | mobile equipment | H | x
5.2.3.5 | 2 | CS | mobile equipment | H | x
5.2.3.5 | 3 | CS | mobile equipment | H | x
5.2.3.5 | 4 | CS | mobile equipment | H | x
5.2.3.5 | 5 | CS | mobile equipment | H | x
5.2.3.5 | 6 | CS | mobile equipment | P | x
5.2.3.5 | 7 | CS | NEI 06-12 makeup and spray capability | H | x
5.2.3.5 | 8 | CS | seismic class of the new cooling system | H | x
5.2.3.5 | 9 | CS | SFP in 1x4 pattern newly discharge spent fuels | P | x
5.2.3.5 | 2.(1) | KS | strengthen spent fuel pool water makeup capability | H | x
5.2.3.5 | 2.(2) | KS | strengthen spent fuel pool water makeup capability | H | x
5.2.3.5 | 2.(3) | KS | spray to the spent fuel pool | H | x
5.2.3.5 | 2 | MS | DCR-M0-4325 | H | x
5.2.3.5 | 3, 4 | MS | DCR-M1-4145/M2-4246 | H | x
5.2.3.5 | 5 | MS | DCR-M1-4304/M2-4305 | H | x
5.2.3.5 | 6 | MS | diesel engine fire pump to make up water from fire water tank to SFP | H | x
5.2.3.5 | 7 | MS | DCR-M1-4269/M2-4270 | H | x
5.2.3.5 | 8 | MS | DCR-M1-4273/M2-4274 | H | x
5.2.3.5 | 9 | MS | spray to the spent fuel pool | H | x
5.2.3.5 | 10 | MS | mobile euqipment | H | x
5.2.3.5 | 11 | MS | mobile euqipment | H | x
5.2.3.5 | 12 | MS | fire engines and offsite water sources | H | x
5.2.3.5 | 13 | MS | operating parameters that have to be monitored in main control room | AP | x
5.2.3.5 | 14 | MS | E-M1-100125/M2-100126 | H |  | x | Dec. 2015
5.2.3.5 | 15 | MS | crane locking device | H | x
5.2.3.5 | 1 | LM | Mobility of Water Injection Equipment | H | x
5.2.3.5 | 3 | LM | enhance the flooding prevention capability of RB, AFB, and EDG Building | H |  | x | before fuel loading |  | (Install flood barrier plates of 1 meter high
5.2.3.5 | 4 | LM | mobile euqipment | H | x
5.2.3.5 | 5 | LM | mobile euqipment | H | x
5.2.3.5 | 6 | LM | mobile euqipment | H | x
5.2.3.5 | 8 | LM | mobile euqipment | H | x
5.2.3.5 | 9 | LM | mobile euqipment | H | x
5.2.3.5 | 10 | LM | NEI 06-12 requirement | PH |  | x | before fuel loading
5.2.3.5 | 11 | LM | above-ground piping system, upgrade piping seismic category of raw water reservoir | H |  | x | Dec. 2014
5.2.3.5 | 12 | LM | 1x4 pattern of newly discharge spent fuels | P | x
5.2.4.3 | 1.(1) | CS | spare ESW motor | H | x
5.2.4.3 | 1.(2) | CS | upgraded SFPACS cooling tower and related piping to Seismic I | H | x
5.2.4.3 | 1.(3) | CS | watertight of 5th EDG and ESW pump room | H |  | x | Dec. 2013
5.2.4.3 | 1.(4) | CS | 4.16kV mobile diesel generators. | H | x
5.2.4.3 | 1.(1) | LM | spare RBSW motor | H |  | x | before commercial operation
5.2.4.3 | 1.(2) | LM | Install above-ground piping system and upgrade piping seismic category of raw water reservoir | H |  | x | Dec. 2014
5.2.4.3 | 1.(3) | LM | install flood barrier and water tight device at the doors and openings | H |  | x | before fuel loading |  | install baffle plates at the external gates on ground floor of each important building
5.2.4.3 | 1.(4) | LM | 4.16kV mobile diesel generators. | H | x
5.2.5.3 | 1 | LM | mobile equipment | H | x
5.2.5.3 | 2 | LM | mobile equipment | H | x
5.2.5.3 | 3 | LM | SFP makeup | P | x
5.2.5.3 | 4 | LM | SFP makeup | P | x
5.2.5.3 | 5 | LM | mobile DG | H | x
5.2.5.3 | 6 | LM | SFP emergency water makeup response procedures | P | x
5.2.5.3 | 7 | LM | NEI 06-12 SFP enhancement | H |  | x | before fuel loading
5.2.5.3 | 8 | LM | Install above-ground piping system and upgrade piping seismic category of raw water reservoir | H |  | x | Dec. 2014
5.2.5.3 | 9 | LM | SFP in checkerboard pattern spent fuels | P | x
6.1.1.2 |  | ALL | each nuclear power plant has collaboration agreements with military, local hospitals and local police stations for supports in case of nuclear accidents | P | x
6.1.1.3 |  | ALL | the content and frequency of these exercises and trainings are being made more extensive and frequent | P | x