## Information-instructions
Questions - Replies - Topical Peer Review II on 'Fire Protection at nuclear installations' (under Article 8e of Directive 2014/87/Euratom) [14 Feb - 30 April 2024]

## TPR experts
Question ID | Reviewer (TPR experts - AFP, PFP, FSA) | Country/NAR | Fire Protection Thematic (for experts' questions) | Chapter and relevant section of TS (for experts' questions) | Page no. in NAR (if specified) | Installation type (NPP, RR, SFS…) | Installation name | Question - installation specific (experts' questions) | Question - General (including generic/general experts' questions for type of installation) | Country's response | Cross reference to to another question-reply (Question ID) | Any remarks
AT-E-1 | FSA | AT | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Triga Mark-II | The scope of the deterministic assessment is not stated. Does it cover in particular situations where the reactor is not in service, for instance during non-working hours? [page 18][Section 2.1.1][Assumption 1/]
AT-E-2 | FSA | AT | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Triga Mark-II | Could you please provide information on the results of the risk analysis carried out? [page 19][Section 2.1.1][Assumption 2/ 4/]
AT-E-3 | FSA | AT | Fire safety analysis | PSR and modifications |  | Research reactor | Triga Mark-II | 1 - From commissioning to 2021 continuous upgrades of TRIGA and institutes buidings, including fires area are ongoing (1962, 1963, 1980, 1984, 1991, 1993, 1995, 2005, 2008, 2010, 2014, 2018). What was the reason (or basis) for all this upgrades, PSR or other? [pages 23-25][section 2.1.5.1] 2 - The NAR does not mention anything regarding PSR, have they been carried out and what were the results? [23-25][section 2.1.5.1] [topic 3/] |  | NHRT6UYKIU
AT-E-4 | FSA | AT | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Triga Mark-II | 1 - How often is the inspection related to to fire protection conducted? [page 26][Section 2.1.7.2] [topic 2/] 2 - Could you give some examples of deficiencies and corrective measures identified relating to fire protection? [page 26][Section 2.1.7.2] [topic 2/] 3 - The NAR mentioned "the existing fire safety analysis as part of the safety report is sufficient for the TRIGA reactor in Vienna". Is fire safety analysis reviewed by the regulator?[page 25][Section 2.1.6] [topic 2/]
AT-E-5 | FSA | AT | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Triga Mark-II |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
AT-E-6 | PFP | AT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Triga Mark-II |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
AT-E-7 | PFP | AT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Triga Mark-II | How are the fire classes for fire barriers defined?
AT-E-8 | PFP | AT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Triga Mark-II |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
AT-E-9 | PFP | AT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Triga Mark-II |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
AT-E-10 | PFP | AT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Triga Mark-II | 3.4 Licensee's experience content is not in accordance with template detailes (page 41-43) only information about the departmental structure was provided not on incidents, events or experiences that have occured. Please provide information on incidents and events and the lessons learned from.
AT-E-11 | PFP | AT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Triga Mark-II |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
AT-E-12 | AFP | AT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | Triga Mark-II |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
AT-E-13 | AFP | AT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | Triga Mark-II | Section 3.2. The information on the fire resistance limits of fire alarm cables is missing. Please provide this information.
AT-E-14 | AFP | AT | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | Triga Mark-II |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
AT-E-15 | AFP | AT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Triga Mark-II |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
AT-E-16 | AFP | AT | Active fire protection | Licensee and regulatory experience |  | Research reactor | Triga Mark-II |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
BE-E-17 | FSA | BE | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | KCD3 Doel site | To 5/ (pp. 22-37): a) Information should be given how the performance levels are achieved through the aoted design and plant layout.
BE-E-18 | FSA | BE | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | KCD3 Doel site | To 2/ (regulator, pp. 22-37): A9 and b) It is mentioned that wekanesses were identified by the FHA and Fire PSA. However, these mainly concern the methodologies for the analyses. Details on the plant weaknesses are not provided. Clarification and additional informatiion is needed.
BE-E-19 | FSA | BE | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | KCD3 Doel site |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
BE-E-20 | FSA | BE | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Tihange 3 | P. 23 & p. 24 When are the L2 Fire PSA and the methodology for addressing the seismically-induced fires in Fire PSA expected to be completed? Are there any preliminary results available? (1/ & 4/)
BE-E-21 | FSA | BE | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Tihange 3 | (, p 31, ch 2.1.6.), Q1: Which weaknesses identified in the design for protection against internal fires have resulted in hardware modifications?.
BE-E-22 | FSA | BE | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Tihange 3 | To 5/ (pp. 22-37): General results of the Fire PSA have been provided in the NAR. How has the acceptability of results provided from Fire PSA been justified? Which results of the Fire PSA are the basis for the action plan?
BE-E-23 | FSA | BE | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Tihange 3 | (p 31, ch 2.1.6.) Q2: Regarding conservatisms in the Fire PSA, are there plans to update the Fire PSA?
BE-E-24 | FSA | BE | Fire safety analysis | Licensee and regulatory experience |  | NPP | Tihange 3 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
BE-E-25 | FSA | BE | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | BR2 | To 1/ (pp. 36-39): a) Can you please provide precise information on how shutdown states of the reactor are treated? b) Can you please describe if and which bounding scenarios are applied as basis for justification of the assessment?
BE-E-26 | FSA | BE | Fire safety analysis | PSR and modifications |  | Research reactor | BR2 | To section 2.2.3, topic 1/, p.38: - Can you please explain, how do you manage "improvement of fire compartmentalization"? Were some buildings/plant areas/rooms modified, etc.?
BE-E-27 | FSA | BE | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | BR2 |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
BE-E-28 | FSA | BE | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | BR3 | To 1/ (p. 38): b) Can you please provide details on the licensee´s experience?
BE-E-29 | PFP | BE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | KCD3 Doel site | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: • Considering that the NAR refers to fire prevention at the "Power Reactor", it should be clarified how "Fire prevention" is adapted to the decommissioning plant; Please provide additional information.
BE-E-30 | PFP | BE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | KCD3 Doel site | * Page 13, point 1.1.3.9. What is the intended end state of decommissioning for the facility? *Page 48. Section 3.1.1.2. Overview of arrangements for management and control of fire load and ignition sources; Fire prevention during hot work – fire permit. Assumption 3/. "Work may only start if the persons carrying out the work are in possession of a valid work permit. A “hot work” permit is also required for work involving a fire hazard…." Is any type of check carried out prior to carrying out hot work? Such as, for example, checking the status of the work area, the tools, the instructions given to the personnel, training of the person in charge of carrying out the work? (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) *Page 56. Section 3.1.1.4. Regulator’s assessment of the fire prevention. Assumtpion 5/. "See under §3.5.1." I am not able to find section §3.5.1. On which page of the NAR is the information referring to this section related to KCD3 found? Should include subsections 3.1.4.1 and 3.1.4.2 of Annex 2 of the TS. Please provide information about the above.
BE-E-31 | PFP | BE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | KCD3 Doel site |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
BE-E-32 | PFP | BE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | KCD3 Doel site |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
BE-E-33 | PFP | BE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | KCD3 Doel site | *Page 89. Section 3.3.2.1 Design approach. Assumption 1/. "The separation between compartments is achieved by means of walls, ceilings, floors and doors of a fire resistance Rf 2h according to NBN 713-020 [16]. The degree of fire resistance of compartmentalization elements such as doors or cable penetrations has also been established in accordance with [16]." Is the fire resistance of the compartments taken into account when allowing temporary and/or fixed storage? *Page 90. Section Wall penetrations, e.g. for electrical cables, are sealed with materials having a fire resistance at least equal to that of the wall they pass through. Assumption 2/. Are the seals installed by qualified personnel and using certified materials?, in page 91 NAR says "A dedicated team is responsible for opening fire penetrations. Once the work has been completed and the fire penetration sealed, a qualification on the fire penetration is carried out." What kind of qualification? * Assumption 4/ is missing. In several sections information about access routes is given, but not how access for fire fighting are maintained. Please complete this information.
BE-E-34 | PFP | BE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | KCD3 Doel site |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
BE-E-35 | PFP | BE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | KCD3 Doel site | *Page 95. Section Performance and management requirements under fire conditions. Assumption 1/. "The smoke extraction ducts are thermally insulated. Smoke extraction aims to: • Allow entry into an affected area; • Limit smoke damage and spread to surrounding areas." Specific information about smoke extraction in access routes is not given. Please provide information on that topic.
BE-E-36 | PFP | BE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | KCD3 Doel site |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
BE-E-37 | PFP | BE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | KCD3 Doel site | *Page 99. Section 3.4. Licensee’s experience of the implementation of the fire protection concept; 3.4.1. Nuclear Power Plants. Asumption 1/. A subsection with strengths and weaknesses is missing. Please provide the information on strengths and weaknesses.
BE-E-38 | PFP | BE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Tihange 3 | page 46, 48/Section 3.1.1.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior?
BE-E-39 | PFP | BE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Tihange 3 | A.II.3.4 Licensee’s experience of the implementation of fire protection concept section should be specified. (page 63)
BE-E-40 | PFP | BE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Tihange 3 | /3/ p. 51: "The Fire Load Index (FLI) is one of the main indicators used for the management of the mobile fire loads in facilities. In particular, it provides an overview of deviations from fire load expectations established in the reference procedure. This index makes it possible to correctly display and monitor fire load violations after which corrective measures can be taken to eliminate these as quickly as possible. The management of the Fire Load Index is described in a specific procedure that defines the roles and responsibilities in all stages (selection of premises to be assessed, periodicity, stakeholders, corrective actions and communication) leading to the completion of the fire risk assessment related to the presence of mobile fire loads." Please can you provide the parameters which define the FLI.
BE-E-41 | PFP | BE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Tihange 3 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
BE-E-42 | PFP | BE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Tihange 3 | Page 89. Some of the fire doors currently installed have only half the fire resistance (i.e. 1h fire rated door in a 2h fire-rated wall), which has been justified on the basis of a specific risk analysis.. Why do some of fire doors have only half the fire resisrance?
BE-E-43 | PFP | BE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Tihange 3 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
BE-E-44 | PFP | BE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Tihange 3 | page 94/Section 3.3.1.2/2/ How are the ventilation systems in fire compartments separating redundant trains? page 94/Section 3.3.1.2/2/ Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences? page 94 /Section 3.3.1.2/3/ Describe the case where a ventilation system serves more than one fire compartments to prevent the spread of fire?
BE-E-45 | PFP | BE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Tihange 3 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
BE-E-46 | PFP | BE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Tihange 3 | Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
BE-E-47 | PFP | BE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Tihange 3 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
BE-E-48 | PFP | BE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | BR2 | Please provide more information on the practise of temporary fire load management.
BE-E-49 | PFP | BE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | BR3 |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
BE-E-50 | PFP | BE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | BR2 | How are the fire classes for fire barriers defined?
BE-E-51 | PFP | BE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | BR3 |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
BE-E-52 | PFP | BE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | BR2 | Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers?
BE-E-53 | PFP | BE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | BR3 |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
BE-E-54 | PFP | BE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | BR2 |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
BE-E-55 | PFP | BE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | SCG Doel (dry) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
BE-E-56 | PFP | BE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | SCG Doel (dry) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
BE-E-57 | PFP | BE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | SCG Doel (dry) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
BE-E-58 | PFP | BE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | SCG Doel (dry) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
BE-E-59 | AFP | BE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | KCD3 Doel site |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
BE-E-60 | AFP | BE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | KCD3 Doel site | TS 3.2.1 - p.62 (Design approach) ---> Indicate please provisions to cope with obsolescence of the fire detection system. (As it was reported for CNT3)
BE-E-61 | AFP | BE | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | KCD3 Doel site |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
BE-E-62 | AFP | BE | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | KCD3 Doel site | 3.2.22 pag. 67/68 (Types, main characteristics ....) ---> It isn't clear if automatic extinguishing systems are installed. Please clarify what fire extinguishing systems are used. 3.2.1.2. Fire suppression provisions - P. 68 Management of harmful effects and consequential hazards - The NAR states 'During normal operation of the reactor....'. Considering that the KCD3 plant is being decommissioned, please clarify the meaning of 'During normal operation of the reactor....'. (TS 3.2.2.3.) pag. 68--> For portable fire extinguishers, it would be necessary to know what agents are used. Please clarify the issue.
BE-E-63 | AFP | BE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | KCD3 Doel site |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
BE-E-64 | AFP | BE | Active fire protection | Licensee and regulatory experience |  | Decommissioning | KCD3 Doel site |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
BE-E-65 | AFP | BE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Tihange 3 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
BE-E-66 | AFP | BE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Tihange 3 | Page 61-63 Section 3.2.1.1 Topic 1 - no discussion of Nuclear Safety Class for the fire detection system - is there one? The description of the fire detection system only appears to cover that for the reactor building, what is provided for the other buildings on the site?.
BE-E-67 | AFP | BE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Tihange 3 | Page 61-63 Section 3.2.1.1 Topic 2 There is no discussion of the level of resilience of the fire detection system, its hazard tolerance (eg. seismic) or the fire rating of the cables or enclosures. The role of EMIT for the fire detection system is not discussed. Please provide further detail with regard to these issues.
BE-E-68 | AFP | BE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Tihange 3 | /1/ p. 61 From the given description it does not really become clear where fire detectors are installed, however the number of installed detectors in the NPP (p. 63) is quite considerable. Please mention by what criteria the rooms in which fire detectors are installed are selected? Also please explain rationale for rooms where detection is excluded.
BE-E-69 | AFP | BE | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Tihange 3 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
BE-E-70 | AFP | BE | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Tihange 3 | Page 64-68 Section 3.2.1.2 Topic 1 - does not discuss the required capacity of the fire systems, only what is provided. How does the licensee know that the system will provide adequate supplies to extinguish a worst case fire?
BE-E-71 | AFP | BE | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Tihange 3 | Page 64-68 Section 3.2.1.2 Topic 4- There is no discussion of retention of fire water - how does the licensee control secondary effects of the generation of fire water, flooding spread of contamination etc.?
BE-E-72 | AFP | BE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Tihange 3 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
BE-E-73 | AFP | BE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Tihange 3 | Page 76 Section 3.2.1.3 Topic 5 - There is no detail of the external fire brigade being provided with familiarisation training of the facility (should this be required). Please provide the relevant information.
BE-E-74 | AFP | BE | Active fire protection | Licensee and regulatory experience |  | NPP | Tihange 3 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
BE-E-75 | AFP | BE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | BR2 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
BE-E-76 | AFP | BE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | BR2 | Section 3.2.2.1. The information on the cables parameters of the automatic fire alarm systems (in particular, on fire resistance, non-propagation of flame a.g.) is missing. Please provide this information.
BE-E-77 | AFP | BE | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | BR2 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
BE-E-78 | AFP | BE | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | BR2 | Section 3.2.2.2 1. Lack of information on the neutralization (removal) of gas and foam from the premises after activation of the gas and foam fire extinguishing system. Please provide this information. 2. Lack of information on the use of special fire-extinguishing agents instead of water (which agents and where they are used). Please provide this information.
BE-E-79 | AFP | BE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | BR2 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
BE-E-80 | AFP | BE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | BR2 | p 83 : "There are multiple firefighting and rescue vehicles in the fire station": it is not clear, what type of vehicles and capacities ? Could more details be provided?
BE-E-81 | AFP | BE | Active fire protection | Licensee and regulatory experience |  | Research reactor | BR2 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
BE-E-82 | AFP | BE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | SCG Doel (dry) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
BE-E-83 | AFP | BE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | SCG Doel (dry) | In order to overcome complete non-compliance with the TS-Annex 2, ---> it is requested to report for Active FP: 3.2.1.1. Design approach 3.2.1.2. Types, main characteristics and performance expectations 3.2.1.3. Alternative/temporary provisions ---> Please highlight weaknesses and any related improvement measures.
BE-E-84 | AFP | BE | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | SCG Doel (dry) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
BE-E-85 | AFP | BE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | SCG Doel (dry) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
BE-E-86 | AFP | BE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | SCG Doel (dry) | In order to overcome complete non-compliance with the TS-Annex 2, ---> it is requested to report for Active FP: 3.2.3. Administrative and organisational fire protection issues ---> Please highlight weaknesses and any related improvement measures.
BE-E-87 | AFP | BE | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | SCG Doel (dry) |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
BG-E-88 | FSA | BG | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | Kozloduy 4 NPP | Please provide further information on FHA realized: Outcomes, methodology, assumptions, rules, mains results ? (p 103) : "During the decommissioning process, the functional fire hazard class of unit 4 of Kozloduy NPP is maintained. According to Regulation Iz-1971, it is designated with hazard class - F5, subclass - F5.1 of fire hazard ". More details? Are there specific fire protecion means to be installed and associated particular requirements? "The degree of fire resistance of the building is determined according to Regulation No. Iz-1971. The building is of the 2ndI degree of fire resistance". Give more precisions: Which fire resistance rating? Are there these fire resistance ratings associated with maximum fire loads?
BG-E-89 | FSA | BG | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | Kozloduy 4 NPP | To 1/ (pp. 45-47): b) Can you please provide information on the scope, and particularly assumptions and methods applied?
BG-E-90 | FSA | BG | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | Kozloduy 4 NPP | To 2/ (pp. 45-47): a) and b) Can you clarify how the fire prevention and protection measures to be adopted to the decommissioning activities are identified?. The list given in the table is needed but not suffiicient for the review.
BG-E-91 | FSA | BG | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Kozloduy 4 NPP | To 1/ (pp. 45-47): The licensee´s experience and assessment is missing. The licensee has identified the following needing improvement: "The main improvement identified from this study is to strengthen the protection of the Pool Loop cooling pumps by improving the automatic fire detection in the compartment".
BG-E-92 | FSA | BG | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Kozloduy 4 NPP |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
BG-E-93 | FSA | BG | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Kozloduy Unit 5 | p27 : Does the Fire PSA consider fire door failure? p28 This contribution is determined by the failure of the fire brigade to extinguish the fire. Does that mean fire walls are not sufficient in case of failure of the brigade? P. 26: Could you specify what are the "appropriate fire simulator models" used?
BG-E-94 | FSA | BG | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Kozloduy Unit 5 | p. 22, Assumption 4/ There is mentioned that PSA level 1 was updated in 2020-2022. What about Level 2 PSA, was it also updated based on that?
BG-E-95 | FSA | BG | Fire safety analysis | Licensee and regulatory experience |  | NPP | Kozloduy Unit 5 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
BG-E-96 | FSA | BG | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site | Please provide the information in the degree of detail requested in the Section 02.4 of the Technical Specifications. Please confirm if electrical fires or and/or HEAF fires have been considered as potential fire initiators in the switchgear room. If they have been, please provide explanation.
BG-E-97 | FSA | BG | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site | 1) P. 41 in 2.4.1 What are the possible consequences and recovery actions in case of loss of power or loss of control systems? Report says that acceptance criteria is met for all initiating events. 2) Has any probabilistic assessment been performed?
BG-E-98 | FSA | BG | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | Wet SFSF Kozloduy site |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire safety analyses with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Inventory make-up: Please provide a higher level of detail on the systems used to make-up inventory. 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 5. Additional analyses: Please provide details about: a) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for spent fuel storage facilities in your country? b) Some countries mention that a periodic safety review is performed for spent fuel storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 6. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
BG-E-99 | FSA | BG | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Raw storage facility Kozloduy (BG) | P44 - Are there further information available from the Updated SAR from the SDRAW, which address the bullet points 0-6/ (TS 02.5)?
BG-E-100 | FSA | BG | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Raw storage facility Kozloduy (BG) | The fire safety analysis for the SFCRAW facility is conducted within the Updated Safety Analysis Report of SDRAW Kozloduy. The main conclusion of the Updated SAR is that a fire in SFCRAW is possible from a short circuit in the electrical circuits of the transport-technological equipment and cranes, and it is assumed that such an event will not affect the protective barriers, especially since SFCRAW does not store combustible substances and materials that help spread the fire.
BG-E-101 | FSA | BG | Fire safety analysis | Licensee and regulatory experience |  | Waste | Raw storage facility Kozloduy (BG) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
BG-E-102 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Kozloduy 4 NPP | Some topics, for the "Fire Prevention" are not present for the facilities under decommissioning (see List of detailed contents for the TS - annex 2), in particular: • "3.1.1 Design considerations and prevention means" (and related subparagraphs) • "3.1.2 Overview of arrangements for management and control of fire load and ignition sources" (and related subparagraphs) • "3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) • "3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) Please provide information about the above.
BG-E-103 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Kozloduy 4 NPP |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
BG-E-104 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Kozloduy 4 NPP | *Page 10 What is the intended end state of the decommissioning for the facility? *Page 64. Section 3.1.7. Fire prevention in the facilities under decommissioning; Unit 4 of Kozloduy NPP. Assumptions 1/ to 5/. Fire prevention in the facilities under decommissioning, is described in a single point, not differentiating the items indicated in the TS . Points 3.1.1, 3.1.2, 3.1.3 and 3.1.4 from TS are missing for Kozloduy 4 or under decommissioning installations. The information is mixed, there is not a sections for hot works, and a section for fire load management. Please provide more information about the topics above. REGARDING HOT WORKS. (Taking into account the state of the plant, or indicate if it does not apply) -> generic question (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) REGARDING FIRE LOADS AND IGNITION SOURCES.(Taking into account the state of the plant, or indicate if it does not apply) -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) *Page 65. Section 3.1.7. Fire prevention in the facilities under decommissioning. Assumption 3/. "For activities with increased fire risk, if necessary, a special on-duty firefighting vehicle of RDFSPP-NPP is provided." What is the process by which it is determined that a special on-duty firefighting vehicle of RDFSPP-NPP must be provided? *Page 64. Section 3.1.7. Fire prevention in the facilities under decommissioning. Assumption 3/. "On the territory of unit 4, there are no separate rooms for storing and working with combustible materials. When the need to use combustible materials arises, the instructions for safe use of the manufacturer are followed and they are used in quantities that do not change the fire hazard category and the functional purpose of the premises. The procedure for collecting and removing combustible waste is determined by an internal order." How is the process to verify that the fire hazard category and the functional purpose of the premises do not change? Please describe the process and controls.
BG-E-105 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Kozloduy 4 NPP | Some topics for the "Passive fire Protection" are not present (see List of detailed contents for the TS - annex 2), in particular: • "3.3.1.1 Design approch" • "3.3.1.2 Description of fire compartments and/or cells design and key features" • "3.3.1.3 Performance assurance through lifetime" • "3.3.2.1 Ventilation system design: segregation and isolation provisions (as applicable)" • "3.3.2.2 Performance and management requirements under fire conditions" Please provide information on the above. • NAR section 3.3.5.1 pag .103 --> Could you describe the passive fire protection measures for the units 1-4? • NAR section 3.3.3.1 pag.101 --> Could you clarify whether analysis and verifications have been used to declare the structures fire-resistant. Please also clarify whether there are certifications in this regard.
BG-E-106 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Kozloduy 4 NPP | *Page 103. Section 3.3.5. Passive fire protection in the facilities under decommissioning; 3.3.5.1. SDD Kozloduy 1-4 – Prevention of fire spreading (barriers). Assumptions 1/ to 7/. There is no information about assumptions 1/ to 7/. Only some regulations are cited. Please provide information on the above or justify whether that is not necessary given the state of the installation.
BG-E-107 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Kozloduy 4 NPP |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
BG-E-108 | PFP | BG | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Kozloduy 4 NPP | (a) Please clarify whether and how the filtering units and fan units of the ventilation system are segregated. '(a) NAR section 3.3.5.2 pag.103 -> The air extracted from the intake ventilation systems is used to clean the aerosols and iodine filters. Please clarify the characteristics of this system in particular in the "fire in progress" situation.
BG-E-109 | PFP | BG | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Kozloduy 4 NPP | *Page 103. Section 3.3.5.2. SDD Kozloduy 1-4 – Ventilation systems. Assumption 1/ "In the controlled area, the facilities are divided into separate hermetic rooms, which provides physical protection in the event of a fire." What is the fire resistance rating of ventilation system? Specific information about smoke extraction in access routes is not given. Please provide information on that topic. Assumptions 2/ and 5/ (In case that ventilation system serves more than one fire compartment) How the design guaranteed that a fire in one room will not propagate to another room? Please give additional information on the means avaible to prevent the spread of fire.
BG-E-110 | PFP | BG | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Kozloduy 4 NPP |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
BG-E-111 | PFP | BG | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Kozloduy 4 NPP | (a) 'NAR section 3.4 pag. 106 -> Are the modernizations of the fire alarm systems for unit 5 and 6 also applied to the units 1-4? (b) NAR section 3.5 pag.113 -> In the event of non-conformities with existing requirements, how should the licensee eliminate them and how is the interface with the supervisory authority?
BG-E-112 | PFP | BG | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Kozloduy 4 NPP | *Page 104. Section 3.4. Licensee’s experience in the implementation of the fire protection concept. Assumption 1/. Is not described for Kozloduy 4. So section 3.4 from TS Annex 2 is missing. What is the licensee´s experience on the implementation of the fire protection concept? What strengths and weaknesses have been identified by the licensee? And what actions to address them? What are the lessons learnt? *Page 112. Section 3.5. Regulator’s assessment of the protection concept and conclusions. Assumption 2/. Is not described for Kozloduy 4. So section 3.5 from TS Annex 2 is missing. What is the assessment from regulator for the fire protection concept? What is the experience from inspection on the implementation of the fire protection concept? What strengths and weaknesses have been identified by the regulator? What are the regulator conclusions? In NAR we can find this section "3.6. Conclusions on the adequacy of the fire protection concept and its implementation", but is not specific for Kozdoluy 4, only for Kozdoluy 5 and 6. Please provide this information.
BG-E-113 | PFP | BG | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Kozloduy 4 NPP |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
BG-E-114 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Kozloduy Unit 5 | page 50/Section 3.1.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 50/Section 3.1.2/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
BG-E-115 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Kozloduy Unit 5 | Which regulation do measures 21111, 18111 and 18121 refer to? Page 92
BG-E-116 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Kozloduy Unit 5 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
BG-E-117 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Kozloduy Unit 5 | page 94/Section 3.3.1.2/ 1/What is the definition for fire zone, fire sector, fire compartment and fire cells?
BG-E-118 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Kozloduy Unit 5 | The required fire resistance of the doors is certified by Test Reports according to the requirements of EN 1361-1, EN1634-1 or Certificates from authorized laboratories Page 95 What are the criteria for the selection of authorized companies?
BG-E-119 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Kozloduy Unit 5 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
BG-E-120 | PFP | BG | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Kozloduy Unit 5 | /Section 3.3.2.1/1/ Do you have installed HEPA filters in ventilation systems? /Section 3.3.2.1/2/ How are the ventilation systems in fire compartments separating redundant trains? /Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences? /Section 3.3.2.1/3/ Describe the case where a ventilation system serves more than one fire compartments to prevent the spread of fire?
BG-E-121 | PFP | BG | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Kozloduy Unit 5 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
BG-E-122 | PFP | BG | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Kozloduy Unit 5 | Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
BG-E-123 | PFP | BG | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Kozloduy Unit 5 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
BG-E-124 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Dry SFSF Kozloduy site |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
BG-E-125 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Dry SFSF Kozloduy site |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
BG-E-126 | PFP | BG | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Dry SFSF Kozloduy site |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
BG-E-127 | PFP | BG | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Dry SFSF Kozloduy site |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
BG-E-128 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site | Some topics, for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: • (b)"3.1.1 Design considerations and prevention means" (and related subparagraphs) • (b)"3.1.2 Overview of arrangements for management and control of fire load and ignition sources" (and related subparagraphs) • (b)"3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) • (b)"3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) Please provide missing information on the above.
BG-E-129 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
BG-E-130 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site | Some topics for the "Passive fire Protection" are not present (see List of detailed contents for the TS - annex 2), in particular: • (b)"3.3.1.1 Design approch" • (b)"3.3.1.2 Description of fire compartments and/or cells design and key features" • (b)"3.3.1.3 Performance assurance through lifetime" • (b)"3.3.2.1 Ventilation system design: segregation and isolation provisions (as applicable)" • (b)"3.3.2.2 Performance and management requirements under fire conditions" " Please provide missing information from the above. • (b))NAR section 3.3.3.1 pag.101 --> Please clarify whether analysis and verifications have been used to declare the structures fire-resistant; also clarify whether there are certifications in this regard.
BG-E-131 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site |  | Management of movable and fix fire loads: How is fire safety evaluated when changes in the instalation are produce due to dismantling activities? [generic]: o Compartmentation (as applicable): How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
BG-E-132 | PFP | BG | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site | (a) Please clarify whether and how the filtering units and fan units of the ventilation system are segregated?
BG-E-133 | PFP | BG | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site |  | [generic] o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
BG-E-134 | PFP | BG | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Wet SFSF Kozloduy site | (a) Please clarify whether paragraphs 3.4, 3.5 and 3.6 also concern WET SFSF
BG-E-135 | PFP | BG | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Wet SFSF Kozloduy site |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
BG-E-136 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Raw storage facility Kozloduy (BG) | Section 3.1.6; P.63. Please clarify whether the fire load in SFCRAW is really close to zero. However, in another section 2.5, P.45 of the NAR it is indicate “...that a fire in SFCRAW is possible from a short circuit in the electrical circuits of the transport-technological equipment and crane”. Section 3.1.6; P.63. Please provide information about fire loads and the different types of potential ignition sources of RAW storage facility Kozloduy. What are the permissible limits for permanent and temporary fire loads and how are they determined? Section 3.1.6; P.63. Please provide information on how fire prevention is ensured during the transportation and handling of radioactive waste in the RAW storage facility Kozloduy.
BG-E-137 | PFP | BG | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Raw storage facility Kozloduy (BG) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
BG-E-138 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Raw storage facility Kozloduy (BG) | Section 3.3.1.2; (1, 7). Please clarify whether the SRSB-3 (Special Radwaste Storage Building) complex is divided into separate fire departments and how? Section 3.3.4.1; P.102. It is not clear if the "Control Center" room and switchboards are in the same building/compartment/room as SFCRAW or how they are seperated. Please provide information to clarify the above. Section 3.3.1. Please provide information how it is ensured that the expected fire resistance of fire compartment penetration component are fulfilled.
BG-E-139 | PFP | BG | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Raw storage facility Kozloduy (BG) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
BG-E-140 | PFP | BG | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Raw storage facility Kozloduy (BG) | Section 3.3.4.2; 103; (1). How are the ventilation system designed to maintain access routes for firefighting?
BG-E-141 | PFP | BG | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Raw storage facility Kozloduy (BG) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
BG-E-142 | PFP | BG | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Raw storage facilityè Kozloduy (BG) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
BG-E-143 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Kozloduy 4 NPP |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
BG-E-144 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Kozloduy 4 NPP | /1/ p. 88: "3.2.6.1. SDD Kozloduy 1-4 - Fire detection and alarm provisions In the supervised area, which includes the TB of unit 4, MCR-4 and electrical distribution panels of unit 4, relay panels, ventilation center and the controlled area the following are provided: Fire alarms (FAS) and Fire extinguishing systems (FES)." It does not become clear by which criteria rooms for FAS or FES are selected. It reads like FAS and FES come together. Please clarify the issue
BG-E-145 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Kozloduy 4 NPP |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
BG-E-146 | AFP | BG | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Kozloduy 4 NPP |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
BG-E-147 | AFP | BG | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Kozloduy 4 NPP | /3/ p. 65 "For the implementation of internal control on fire safety in SDD Kozloduy 1-4, three jobs are planned for the position of chief expert "Fire and occupational safety". The persons occupying this position must possess the relevant professional qualification in the field of fire safety." These jobs are planned but how the gap is currently filled?
BG-E-148 | AFP | BG | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Kozloduy 4 NPP |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
BG-E-149 | AFP | BG | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Kozloduy 4 NPP | p. 104 and following and p. 112 and following: Regarding the licensee's experience (sect. 3.4) and the regulator's assessment (sect. 3.5) the reviewer could not find any information dedicated to Kozloduy unit 4. Please provide the relevant information.
BG-E-150 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Kozloduy Unit 5 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
BG-E-151 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Kozloduy Unit 5 | Page 66-70 Section 3.2.1 Topic 1 - emergency power supplies are mentioned but there is no detail of what are these and how long do they provide back up power? What is the Nuclear Safety Class of the fire detection and alarm system.
BG-E-152 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Kozloduy Unit 5 | Page 66-70 Section 3.2.1 - NAR does not provide detail of the resilience of the fire detection and alarm system or its hazard tolerance (eg. seismic). No discussion of the fire rating of the system cables or enclosures. Further information in these areas would be useful.
BG-E-153 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Kozloduy Unit 5 | Section 3.2.1.1 p. 67. It is stated: "Fire alarm lines are designed to remain operational in fire conditions for at least 30 minutes", however, no information is provided regarding the fire resistance limits of fire extinguishing cables of the installations. Could you provide an additional information? Please provide fire resistance properties of the cables used for active fire protection control and supply.
BG-E-154 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Kozloduy Unit 5 | Page 66 of pdf, section 3.2.1, assumption 1. There is no information about incipient detection (air sampling systems or similar). Is this type of technology installed in the plant? - Page 68 of pdf, section 3.2.1.2, assumption 1. "The three computer stations are located at workplaces with 24-hour duty". "Each operator of fire protection systems receives information on the current status". Is the information received in the main control room (MCR)? Which are the tasks of these operators during normal operation and during a fire? - Page 68 of pdf, section 3.2.1.2, assumption 1. In general, are SSC important to safety covered by fire detectors? If not, please explain. - Page 70 of pdf, section 3.2.1.3, assumption 4. Explain in general the types of compensatory measures in case of impairment of fire detection systems.
BG-E-155 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Kozloduy Unit 5 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
BG-E-156 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Kozloduy Unit 5 | Page 70-80 Section 3.2.2 Topic 1 - there is a significant amount of detail provided on various suppression systems across the facility. However, it is not always clear what the capacity requirements are and how they have been derived. There is no mention of the Nuclear Safety Class of the suppression systems or the standards against which they have been designed. Please could clarification be provided on these points?
BG-E-157 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Kozloduy Unit 5 | Page 70-80 Section 3.2.2 Topic 2 - Have hazards to the fire protection equipment been considered beyond seismic?
BG-E-158 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Kozloduy Unit 5 | Page 70-80 Section 3.2.2 Topic 4 - What are the retention arrangements for the fire fighting water?
BG-E-159 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Kozloduy Unit 5 | Section 3.2.2.2.5 p. 73. There is no information on powering the active fire extinguishing system equipment: electric valves, valves, etc. in cases of complete station blackout. Section 3.2.2.2.5 p. 78. There is no information on neutralization (removal) measures after the powder fire extinguishing system is activated. Please provide more information on this two issues
BG-E-160 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Kozloduy Unit 5 | Page 71 of pdf, section 3.2.2.2, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown or any similar provision? - Page 71 of pdf, section 3.2.2.2.1, assumption 2. There is a volume of 70 m³ of water in each tank for stationary water automatic fire extinguishing systems for the cable rooms of the safety systems. Which is the suppression duration supposed to calculate this capacity? - Page 72 of pdf, section 3.2.2.2.2, assumption 2. There are 3 electric main fire pumps and 2 emergency diesel pumps in each CWPS; and 2 CWPS. Which is the capacity of these pumps (100%, 50% or other)? Has loss of off-site power been considered in their design? Are they connected to redundant Class 1E emergency electrical buses? Are they seismically qualified? Is each fire pump with its motor and controls located separately from the other fire pumps by fire resistant walls? In the control room, is there an alarm signal to indicate pumps running, driver unavailability, failure to start and low water pressure in the main external ring? - Page 80 of pdf, section 3.2.2.3, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain. - Page 81 of pdf, section 3.2.2.4, assumption 3. Explain in general the types of compensatory measures in case of impairment of fire suppression systems.
BG-E-161 | AFP | BG | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Kozloduy Unit 5 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
BG-E-162 | AFP | BG | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Kozloduy Unit 5 | Page 81-85 Section 3.2.3 Topic 1- What criteria are there for contacting the off-site fire brigade - is this done every time a fire is detected?
BG-E-163 | AFP | BG | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Kozloduy Unit 5 | Page 83 of pdf, section 3.2.3.2, assumption 4. "The RSFSPP-NPP is located in close proximity to the plant". How far from the plant? Which is the minimum staffing? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? Is there an onsite fire brigade or only offsite fire brigade? - Page 84 of pdf, section 3.2.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 84 of pdf, section 3.2.3.2, assumption 1. Which is the minimum number of drills per year for each member of the fire brigade?
BG-E-164 | AFP | BG | Active fire protection | Licensee and regulatory experience |  | NPP | Kozloduy Unit 5 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
BG-E-165 | AFP | BG | Active fire protection | Licensee and regulatory experience |  | NPP | Kozloduy Unit 5 | Page 113 of pdf, section 3.6, and all the assumptions. Strengths and weaknesses are not clearly mentioned in the NAR, can you confirm that there are no strengths / weaknesses or otherwise mention them if there are any?
BG-E-166 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Dry SFSF Kozloduy site |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
BG-E-167 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Dry SFSF Kozloduy site | (Dry SNF Storage Facility - DSFSF) Considering that the chapter refers to "Buildings and productions on the territory of units 5 and 6" without addressing the facility in question, ---> Indicate the systems included in the Dry facility. ---> Please highlight weaknesses and any related improvement measures.
BG-E-168 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Dry SFSF Kozloduy site |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
BG-E-169 | AFP | BG | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Dry SFSF Kozloduy site |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
BG-E-170 | AFP | BG | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Dry SFSF Kozloduy site | (Dry SNF Storage Facility - DSFSF) ---> Please highlight weaknesses and any related improvement measures.
BG-E-171 | AFP | BG | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Dry SFSF Kozloduy site |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
BG-E-172 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
BG-E-173 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site | (TS 3.2.1 - Fire detection and alarm provisions) pag. 66 et seq. --> --> Concerning also PSFS facilities, report the design approach (3.2.1.1.), types, main characteristics and performance expectations (3.2.1.2.) as the chapter refers to "Buildings and productions on the territory of units 5 and 6" and it is not evident that it also deals with the facility in question. Please provide the relevant information. 'Alternative/temporary provisions (TS 3.2.1.3. and 3.2..2.4 Alternative/temporary provisions) pag. 70,80 --> In addition to when and why alternative/temporary provisions are taken, it would be necessary to know what the mainprovisions are. --> Please highlight weaknesses and any related improvement measures.
BG-E-174 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site |  | The description of fire suppression provisions seems missing or are superficially discussed for the wet storage. • Clarify use of fixed fire extinguishing systems (type, location, …). • Clarify possible adverse effects of fire extinguishing systems and activities on nearby safety equipment. • Clarify type and number of portable/mobile fire extinguishers. • Clarify strategic approach and organizational arrangements for use of external firefighting resources. [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
BG-E-175 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site | (TS 3.2.1 --> Clarify whether the structure can be protected by the external fire suppression system (Page 72 3.2.2.1.), as this system is not mentioned in 3.2.4.2. (PSFSF and DSFSF - Fire Suppression Provisions). 'Alternative/temporary provisions (TS 3.2.1.3. and 3.2..2.4 Alternative/temporary provisions) pag. 70,80 --> In addition to when and why alternative/temporary provisions are taken, it would be necessary to know what the main provisions are. --> Please highlight self-identified weaknesses and any related improvement measures. • Clarify use of fixed fire extinguishing systems (type, location, …). • Clarify possible adverse effects of fire extinguishing systems and activities on nearby safety equipment. • Clarify type and number of portable/mobile fire extinguishers.
BG-E-176 | AFP | BG | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site |  | ---> Clarify strategic approach and organizational arrangements for use of external firefighting resources. [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
BG-E-177 | AFP | BG | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | Wet SFSF Kozloduy site | Clarify strategic approach and organizational arrangements for use of external firefighting resources.
BG-E-178 | AFP | BG | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Wet SFSF Kozloduy site |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
BG-E-179 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Raw storage facility Kozloduy (BG) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
BG-E-180 | AFP | BG | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Raw storage facility Kozloduy (BG) | /1/ (p. 63) "Based on the complete analysis of the combustible load, a justification of the fire protection of the object was made. Regarding the category of fire hazard, the site is category F5D according to Regulation No. Iz-1971 [8]. For objects of this category, the installation of automated fire extinguishing and fire alarm systems is not required. There are no combustible materials in SFCRAW, the structure and stored objects are mainly made of reinforced concrete, and the fire load is assumed to be 0 (zero)." The "[8] Regulation No. Iz-1971 of 29.10.2009 on Construction and Technical Rules and Regulations for Ensuring Fire Safety, 2009" seems to be a non-nuclear regulation. The term "category F5D" according to the regulation is not explained in the NAR. Fire loads from electrical installations or from paintings like decontamination coatings are not discussed. Transient fire loads (construction works, vehicles etc.) are not discussed. Please provide information that this arrangement is justified in fire safety analysis.
BG-E-181 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Raw storage facilityè Kozloduy (BG) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
BG-E-182 | AFP | BG | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Raw storage facilityè Kozloduy (BG) | /1/ (p. 88) "3.2.5.2. SFCRAW - Fire suppression provisions According to national legislation, and more specifically the requirements of Appendix 1, to Article 3, Paragraph 2 of Ordinance No. Iz-1971 on the construction and technical rules and norms for ensuring safety in case of fire [8], for closed warehouses for the storage of non-combustible materials, the construction of a fire extinguishing installation is not required, and none has been built." Fire suppression means are limited to fire extinguishers. Is this based on a nuclear or conventional directive?
BG-E-183 | AFP | BG | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Raw storage facilityè Kozloduy (BG) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
BG-E-184 | AFP | BG | Active fire protection | Licensee and regulatory experience |  | Waste | Raw storage facilityè Kozloduy (BG) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
CH-E-185 | FSA | CH | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | Mulheberg NPP | (p49): No fire was assumed in the interim storage facility due to the low fire loads => What is the limit value underneath fire is not assumed?
CH-E-186 | FSA | CH | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | Mulheberg NPP | To 1/ (pp. 49-52): a) and b) Can you clarify how the methodology used from the operating NPP has been adapted to the decommissioning phase in its different stages?
CH-E-187 | FSA | CH | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Mulheberg NPP |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
CH-E-188 | FSA | CH | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Gosgen | (, p 37, ch 2.1.7.3.) Is there any timetable for ENSIs identified various methodological needs for improvement in the fire PSA of the KKG?
CH-E-189 | FSA | CH | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Leibstadt | (, p 33, ch 2.1.6.) Need of timetable for ENSIs ongoing supervisory process. No weaknesses have been pointed out - please confirm that there are no weaknesses
CH-E-190 | FSA | CH | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Gosgen | (p 37, ch 2.1.7.3.) Is there any timetable for the various methodological needs for improvement in the fire PSA of the KKG identified by the regulator (ENSI)?
CH-E-191 | FSA | CH | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Leibstadt | (p 33, ch 2.1.6.) Can you please provide a timetable for ENSI's ongoing supervisory process?
CH-E-192 | FSA | CH | Fire safety analysis | Licensee and regulatory experience |  | NPP | Beznau I & II |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
CH-E-193 | FSA | CH | Fire safety analysis | Licensee and regulatory experience |  | NPP | Gosgen |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
CH-E-194 | FSA | CH | Fire safety analysis | Licensee and regulatory experience |  | NPP | Leibstadt |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
CH-E-195 | FSA | CH | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | Nasslager | More details are needed as information requested in the section 02.5 on the Technical Specifications is not present in the NAR for this installation.
CH-E-196 | FSA | CH | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | Nasslager | P. 39 & p. 47 (2.4.1 & 2.4.7.1) Due to the very low fire load, the separation and the special design features, fires cannot endanger residual heat removal function. What is the fire load density (MJ/m2) in the compartments containing SSC important to safety?
CH-E-197 | FSA | CH | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | Nasslager |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire safety analyses with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Inventory make-up: Please provide a higher level of detail on the systems used to make-up inventory. 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 5. Additional analyses: Please provide details about: a) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for spent fuel storage facilities in your country? b) Some countries mention that a periodic safety review is performed for spent fuel storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 6. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
CH-E-198 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Mulheberg NPP | *Page 3. Key parameters. - Please describe the intended end state of decommissioning. * Sections 3.1.3.1 and 3.1.4.1 from TS Annex 2 is missing for Mülheberd NPP, because strengths and weaknesses are not mentioned in the NAR. Please indicate if strengths or weaknesses have been identified. *Page 59. Section 3.1.2 Overview of arrangements for management and control of fire load and ignition sources; Mühleberg Nuclear Power Plant (KKM). Assumption 3/. "Due to the ongoing decommissioning of systems and dismantling, the ignition sources and fire loads are continuously reduced in SP2 and thus the hazard potential for fire development is further reduced." Due to the dismantlig activities It is understood that hot works are carried out so: REGARDING HOT WORK (Taking into account the state of the plant, or indicate if it does not apply) -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) REGARDING FIRE LOADS "The fire loads and fire stresses are recorded and evaluated for each building on the site in the "Fire loads and fire stresses" list. The periodic overall review of this list is usually carried out at least every five years or on the occasion of significant changes due to plant modifications, decommissioning or dismantling.". " Flammable substances may only be present in the workplace in quantities necessary for the progress of work in a day shift (controlled handling)." -> generic question (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.)
CH-E-199 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Mulheberg NPP |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CH-E-200 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Mulheberg NPP | *Page 97. Section 3.3.1.2 Description of fire compartments and/or cells design and key features; Mühleberg Nuclear Power Plant (KKM). Assumption 1/. Please provide a description on the characteristics of fire barriers forming fire compartments (walls, ceilings, doors, penetrations...). What are the fire rates? "Passages and other openings in building components that form fire compartments must be closed off with fire-resistant fire closures." What is the fire rate of these closures? Is it the same as the one on the wall it crosses? *Page 97. Section 3.3.1.2 Description of fire compartments and/or cells design and key features; Mühleberg Nuclear Power Plant (KKM). Assumption 4/. "Sufficient escape and rescue routes are ensured throughout the decommissioning phase." Please, provide more information on how firefighting access routes are maintained. *Page 97. Section 3.3.1.2 Description of fire compartments and/or cells design and key features; Mühleberg Nuclear Power Plant (KKM). Assumption 2/. How it is ensured that the expected fire resistance and stability ratings are fulfilled ?
CH-E-201 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Mulheberg NPP |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CH-E-202 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Mulheberg NPP | *Page 100. Section 3.3.2 Ventilation systems 3.3.2.1 Ventilation system design: segregation and isolation provisions (as applicable). Assumption 1/. A description of the ventilation system and the elements with which this separation of compartments is guaranteed is necessary. Specific information about smoke extraction in access routes is not given. Please provide information on that topic. Assumption 4/. "Fire compartments are isolated by automatic fire controls and by means of fire dampers. " Are fire dampers checked periodically? What is the fire resistance rating of ventilation system? Assumptions 5/ Please provide more information about the means avaible to prevent the spread of fire.
CH-E-203 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Mulheberg NPP | Section 4.3.; P.121; (1). Report states that „In the event of a fire, depending on the design of the ventilation system, the type of components housed in the fire compartment and its use, as well as the nuclear and radiological protection objectives pursued, the ventilation systems are switched off or continue to operate“. Please provide more detail information about when the ventilation system is switched off and when it continues its operation.
CH-E-204 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Mulheberg NPP |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CH-E-205 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Mulheberg NPP | *Page 108. Section 3.4 Licensee's experience of the implementation of the fire protection concept; 3.4.1 Overview of strengths and weaknesses identified. Assumption 1/. Strengths and weaknesses found by the licensee are not mentioned in the NAR. Please provide this information.
CH-E-206 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Mulheberg NPP |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
CH-E-207 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Beznau I & II | page 57/Section 3.1.2/ 3/Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 57/Section 3.1.2/ 3/How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
CH-E-208 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Beznau I & II | p57/3/ What are the key aspects in the control of hot work? Could you describe the provisions for hot work in more detail?
CH-E-209 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Beznau I & II |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CH-E-210 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Gosgen | page 57/Section 3.1.2/ 3/Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 57/Section 3.1.2/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
CH-E-211 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Gosgen | p57/3/ What are the key aspects in the control of hot work? Could you describe the provisions for hot work in more detail?
CH-E-212 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Gosgen |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CH-E-213 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Leibstadt | page 58/Section 3.1.2/ 3/Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 58/Section 3.1.2/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
CH-E-214 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Leibstadt | p58/3/ -What are the key aspects in the control of hot work? Could you describe the provisions for hot work in more detail?
CH-E-215 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Leibstadt |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CH-E-216 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Beznau I & II | p100/4/ -As is there is only one stairway mentioned in the report that is overpressured, is there another stairwell that is also overpressurized in case of fire? How are the safe escape and fire brigade access assured, if that first stairwell is lost?
CH-E-217 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Beznau I & II |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CH-E-218 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Gosgen |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CH-E-219 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Gosgen | 4/ Could you describe the access routes for firefighting in more detail? (housekeeping/ventilation/multiple entries/etc.)
CH-E-220 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Leibstadt | 4/ Could you describe the access routes for firefighting in more detail? (housekeeping/ventilation/multiple entries/etc.)
CH-E-221 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Leibstadt |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CH-E-222 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Beznau I & II | /Section 3.3.2.1/2/ How are the ventilation systems in fire compartments separating redundant trains? /Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences?
CH-E-223 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Beznau I & II |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CH-E-224 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Gosgen | /Section 3.3.2.1/2/ How are the ventilation systems in fire compartments separating redundant trains? /Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences?
CH-E-225 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Gosgen |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CH-E-226 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Leibstadt | /Section 3.3.2.1/2/ How are the ventilation systems in fire compartments separating redundant trains? /Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences?
CH-E-227 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Leibstadt |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CH-E-228 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Beznau I & II | page 107/Section 3.4/1/ Did you have OSART, WANO missions? What were lessons learnt from OSART and WANO missions? Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
CH-E-229 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Beznau I & II |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
CH-E-230 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Gosgen | page 107/Section 3.4/1/ Did you have OSART, WANO missions? What were lessons learnt from OSART and WANO missions? Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
CH-E-231 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Gosgen |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
CH-E-232 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Leibstadt | page 107/Section 3.4/1/ Did you have OSART, WANO missions? What were lessons learnt from OSART and WANO missions? Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
CH-E-233 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Leibstadt |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
CH-E-234 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Zwilag |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CH-E-235 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Zwibez |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CH-E-236 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Zwilag |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CH-E-237 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Zwibez |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CH-E-238 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Zwilag |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CH-E-239 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Zwibez |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CH-E-240 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Zwilag |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
CH-E-241 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Zwibez |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
CH-E-242 | PFP | CH | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | Nasslager |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CH-E-243 | PFP | CH | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | Nasslager |  | [generic]: o Compartmentation (as applicable): How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CH-E-244 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | Nasslager | (a) NAR section 3.3.2.1 pag.99 -> Please clarify whether the technical rooms where the fans and filter benches are located are redundant and separate (segregation and isolation).
CH-E-245 | PFP | CH | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | Nasslager |  | [generic] o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CH-E-246 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Nasslager | (a) NAR section 3.1.4.2 pag.66--> Based on what is reported in the section 3.1.4.2 please clarify if there is an inspection plan.
CH-E-247 | PFP | CH | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Nasslager |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
CH-E-248 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Mulheberg NPP |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
CH-E-249 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Mulheberg NPP | Page 82 of pdf, section 3.2.1.3, assumption 4. Explain the types of compensatory measures in case of impairment of fire detection systems.
CH-E-250 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Mulheberg NPP |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CH-E-251 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Mulheberg NPP | Page 86 of pdf, section 3.2.2.1, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to fire hoses/hydrants or any similar provision? - Page 86 of pdf, section 3.2.2.1, assumption 3. Explain please in general the procedures established for the examination, inspection, maintenance and testing of extinguishing systems.
CH-E-252 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Mulheberg NPP |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
CH-E-253 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Mulheberg NPP | Page 96 of pdf, section 3.2.3.2, assumption 4. Explain the differences between the plant fire brigade and the intervention group, especially regarding their training, firefighter qualifications, organisation, minimum staffing, minimum knowledge and physical conditions. - Page 96 of pdf, section 3.2.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 96 of pdf, section 3.2.3.2, assumption 4. Regarding drills and exercises of the onsite fire brigade or intervention group: explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade and content.
CH-E-254 | AFP | CH | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Mulheberg NPP |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
CH-E-255 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Beznau I & II |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
CH-E-256 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Beznau I & II | /1/ P. 67: "All existing fire detectors and fire alarm control panels are recorded in the fire alarm control systems. Exceptions are the fire detectors that are subordinate to a halon extinguishing control centre." What kind of monitoring is undertaken for the halogen extinguishing control centers? Is only the actuation of the halogen system monitored?
CH-E-257 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Beznau I & II | Section 3.2. Absence of information on cable products of automatic fire alarm systems, in particular fire resistance, non-propagation of flame, etc. Please provide more datailed information on the issue.
CH-E-258 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Gosgen |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
CH-E-259 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Gosgen | /1/ p. 68: "Fire alarm system All buildings are fully monitored with a fire alarm system in accordance with the VKF fire protection guidelines. Individual rooms are not included in the monitoring scope of the fire alarm system. These are usually rooms that do not need to be monitored according to the VKF fire protection guidelines or have a high radiation exposure." How far the non-nuclear VKF-guidelines do consider nuclear protection targets for fire detection? Rooms with a high radiation exposure principally should be protected by a fire detection system. Why individual solutions like aspiration detectors etc. were not applied for such areas (cf. p. 70) ?
CH-E-260 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Gosgen | 1. Section 3.2. Absence of information on cable products of automatic fire alarm systems, in particular fire resistance, non-propagation of flame, etc. Please provide more detailed information on the issue. 2. Section 3.2.1.1 Arrangement of automatic fire alarm (types of detectors - smoke, thermal, etc., fire-fighting equipment, availability/absence of the upper level of the system, etc.). Please specify type of automatic fire detection.
CH-E-261 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Leibstadt |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
CH-E-262 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Leibstadt | /1/ p. 68: "Fire alarm system In principle, the principle of full monitoring via the fire alarm system (FAS) applies in the KKL. The fire alarm system in the KKL is equipped in accordance with the VKF fire protection guidelines. Individual areas are excluded from full monitoring due to internal circumstances (e.g. radiation)." How far the non-nuclear VKF-guidelines do consider nuclear protection targets for fire detection? Rooms with a high radiation exposure principally should be protected by a fire detection system. Why individual solutions like aspiration detectors etc. were not applied for such areas (cf. p. 70) ? [BF] /2/ The design of the fire detection system against earthquake is not mentioned.
CH-E-263 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Leibstadt | 1. Section 3.2. Absence of information on cable products of automatic fire alarm systems, in particular fire resistance, non-propagation of flame, etc. 2. Section 3.2.1.1 Arrangement of automatic fire alarm (types of detectors - smoke, thermal, etc., fire-fighting equipment, availability/absence of the upper level of the system, etc.).
CH-E-264 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Beznau I & II |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CH-E-265 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Beznau I & II | The NAR say there is still halon extinguishing system? is this right ? If yes, please explain why it is acceptable to continue to use a halon system. If no, what system is supplied.
CH-E-266 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Beznau I & II | /1/ p. 33: "The lack of spatial separation of the safety and emergency systems in the annular space of the reactor building by passive fire barriers is compensated for by spatial distance and basic fire protection measures, such as minimisation of fire loads and ignition sources and the presence of extinguishing equipment." p. 36: "Manual fire extinguishing by the fire brigade has only been considered in a few fire scenarios in the deterministic fire analysis of the KKB, as the critical fire Chapters are mostly protected by automatic fire extinguishing systems." At which locations and for which systems the lack of passive fire protection (by structures or by distance) is compensated by active measures? How this is done in detail?
CH-E-267 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Beznau I & II | 1. Section 3.2. Absence of requirements for fire extinguishing systems of safety systems (qualification of equipment with regard to external hazards, in particular seismic resistance, classification by functions, etc.). 2. Section 3.2.2.3. Measures to neutralize (remove) gas from the premises after actuation of the gas fire extinguishing system.
CH-E-268 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Beznau I & II | p. 114: "The main steam blowdown station was identified as a critical plant area at the KKB due to the lack of fire protection separation of the individual safety lines under narrow spatial conditions (National area for Swiss National Assessment Report Topical Peer Review 2023 ENSI 115 improvement, Chapter 2.1.7.1). Concrete measures are planned here to further reduce the probability of a fire." Reducing the probability of a fire mainly adresses fire loads and ignition sources. Which role active fire protections plays now and in connection with improving the blowdown station?
CH-E-269 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Gosgen |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CH-E-270 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Gosgen | 1. Section 3.2. Absence of requirements for fire extinguishing systems of safety systems (qualification of equipment with regard to external hazards, in particular seismic resistance, classification by functions, etc.). 2. Section 3.2.2.3 Measures to neutralize (remove) gas from the premises after actuation of the gas fire extinguishing system.
CH-E-271 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Leibstadt |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CH-E-272 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Leibstadt | 1. Section 3.2. Absence of requirements for fire extinguishing systems of safety systems (qualification of equipment with regard to external hazards, in particular seismic resistance, classification by functions, etc.) 2. Section 3.2.2.3 Measures to neutralize (remove) gas from the premises after actuation of the gas fire extinguishing system
CH-E-273 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Beznau I & II |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
CH-E-274 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Gosgen |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
CH-E-275 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Leibstadt |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
CH-E-276 | AFP | CH | Active fire protection | Licensee and regulatory experience |  | NPP | Beznau I & II |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
CH-E-277 | AFP | CH | Active fire protection | Licensee and regulatory experience |  | NPP | Gosgen |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
CH-E-278 | AFP | CH | Active fire protection | Licensee and regulatory experience |  | NPP | Leibstadt |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
CH-E-279 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Zwilag |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
CH-E-280 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Zwilag | inadmissible ambient conditions for the waste only or for waste and the whole facility, containing the fire detection and alarm system too?, Please clarify the issue. /3/ p.94, 3.3.1.1 Design approach, nothing is mentioned to describe maintenance under hazard conditions, Please clarify the issue. /4/ p. 72, 3.2.1.3 Alternative/temporary provisions, nothing is mentioned for alternative arrangements, just an exception for building H (fire detection and alarm system is not required), but no explanation. Please clarify the issue.
CH-E-281 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Zwibez |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
CH-E-282 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Zwibez | No further information for /1/, /2/, /3/; /4/, p.81, 3.2.2.4 Alternative/temporary provisions, It is not explained why alternative arrangements are "assesed as not relevant by the operator". Please provide the relevant information.
CH-E-283 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Zwilag |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CH-E-284 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Zwilag | p.74, 3.2.2.1 Design approach, it is not mentioned who decides to activate the deluge system manually; /2/ no further information about water distribution network etc. /5/ no further information about accessibility Please provide the relevant information
CH-E-285 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Zwibez |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CH-E-286 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Zwibez | p.84, 3.2.3.2, /5/ no further information about accessibility Please provide the relevant information.
CH-E-287 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Zwibez |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CH-E-288 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Zwibez | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. It is not substantiated why the installation building is not equipped with a fire extinguishing system. Please provide the relevant information.
CH-E-289 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Zwilag |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
CH-E-290 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Zwilag | Information given for /1/ to /4/ but no overall information about safety culture involving all information. Please provide learning from sections /1/ to /4/.
CH-E-291 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Zwibez |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
CH-E-292 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Zwibez | Information given for /1/ to /4/ but no overall information about safety culture involving all information. Please provide learning from sections /1/ to /4/.
CH-E-293 | AFP | CH | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Zwilag |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
CH-E-294 | AFP | CH | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Zwilag | p64. 3.1.4.1, several weaknesses are mentioned by regulator (no valid documents, no required fire load register, etc.) but no plan how to deal with it. Please explain how the weaknesses will be addressed.
CH-E-295 | AFP | CH | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Zwibez |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
CH-E-296 | AFP | CH | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Zwibez | [CN] /2/ p.65, 3.1.4.1, a fundamental revision and division of the fire protection concept in accordance with the current VKF regulations is required by ENSI but no further information how to deal with it. Please explain how this issue will be addressed.
CH-E-297 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | Nasslager |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
CH-E-298 | AFP | CH | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | Nasslager | (at GOSGEN NPP - KKG) Considering the in the NAR is reported (3.1.1 pag.63) "Redundant safety system equipment is located in different fire compartments", ---> Please specify which redundant systems are actually to be physically separated. (a) Please specify if the Fire Detection System is interfaced with the fire dampers control system
CH-E-299 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | Nasslager |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CH-E-300 | AFP | CH | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | Nasslager | (at GOSGEN NPP - KKG) Considering that in the wet storage building the extinguishing water is retained through the free volume in the basement, ---> Clarify how this potentially radiologically contaminated water is managed. (p.78) The NAR states that a number of places with cable ducts, cable distributions, cable rooms and cable floors, electrical stores are equipped with sprinkler systems. Clarify whether water from the sprinkler could have any adverse effect on these electrical components. (p.80) Clarify any potential adverse effects of fire water on electric components and on sub-criticality of the spent fuel pool.
CH-E-301 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | Nasslager |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
CH-E-302 | AFP | CH | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | Nasslager | (at GOSGEN NPP - KKG) Please highlight weaknesses in the active fire protection approach and any related improvement measures planned or implemented.
CH-E-303 | AFP | CH | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Nasslager |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
CZ-E-304 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Temelin | Can you please provide information in how far and how the different plant operational states (POSs) are considered in the deterministic fire safety analysis (chapter 2.1.A.1, 2.1.A.2, 2.1.A.3)?
CZ-E-305 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Temelin | p21 : Firefighting in bituminous areas : How is the risk from bitumen as fire load taken into account? (exothermic chemical reactions? 1997 Tokai Mura fire/explosion feedback?) P22 : Can you please explain what τe and k8 values are?
CZ-E-306 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Dukovany | New deterministic fire safety analysis of all safety significant buildings exist. It remains unclear how the operational states are incorporated in the above mentioned analysis [2.1.B.2.].
CZ-E-307 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Dukovany | p31 : The electrical Fire Detectors, where installed, is functional. Does this mean that the 3rd level of defence is not independent of the 2nd? Does this mean that the 3rd level of defence is not sufficient in the absence of detection?
CZ-E-308 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience |  | NPP | Temelin NPP | page 35, section 2.1.7.3 topic 2/ Which the period of periodic inspections on fire protection? Could you provide some identified weakness or non-compliences during the inspection?
CZ-E-309 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience |  | NPP | Temelin NPP |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
CZ-E-310 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience |  | NPP | Dukovany | page 35, section 2.1.7.3 topic 2/ Which the period of periodic inspections on fire protection? Could you provide some identified weakness or non-compliences during the inspection?
CZ-E-311 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience |  | NPP | Dukovany |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
CZ-E-312 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Research reactor LVR 15 | To 1/ (pp. 36-40): Can you please address the scope of the analyses covering also shutdown states during outages more clearly (and not only implicitly)?
CZ-E-313 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Research reactor LVR 15 | To p.36, 1/: Could you specify, if the PSA, especially fire PSA performed for LVR-15? If yes, what are the main contributors (events) and dominant contributes (or sequences for each considered event), and are any measures (except for emergency planning zone issues) identified based on the results?
CZ-E-314 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Research reactor LVR 15 | To 4/ (p. 40): b) The licensee mentions that the INSARR mission in 2020 revealed the need for fire hazard reduction (disposal of older technologies) and for comprehensive instructions for personnel response (emergency procedures and instructions) also in case of fire. Can you give some information on this?
CZ-E-315 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Research reactor LVR 15 | , p.40, 2/ The information on regulatory oversight, and inspections on fire safety was covered is missing. How often the periodic inspections on fire safety are performed? Is there any significant insight into fire safety from this inspection?
CZ-E-316 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Research reactor LVR 15 |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
CZ-E-317 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Temelin NPP | page 46/Section 3.1.A.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 46/Section 3.1.A.2/3/ Describe how management and control of hot work is carried out (e.g in case of maintenance, modification...)? page 46/Section 3.1.A.2/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
CZ-E-318 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Temelin NPP |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CZ-E-319 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Dukovany | page 50/Section 3.1.B.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 50/Section 3.1.B.2/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
CZ-E-320 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Dukovany |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CZ-E-321 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Temelin NPP | page 112/Section 3.3.A.1.2/ 1/Describe how the plant is divided into fire compartments and fire cells? Please define the terms: fire compartment, fire sections, fire cell? page 112/Section 3.3.A.1.1/2/ Are the fire resistances for fire barriers (fire walls, fire doors, fire dampers) for 15 minutes acceptible? Are fire resistance of fire barriers in compliance with national fire standards? page 113/Section 3.3.A.1.3/2/ How it is ensured that the expected fire resistance and stability ratings are fulfilled?
CZ-E-322 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Temelin NPP |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CZ-E-323 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Dukovany | page 118/Section 3.3.B.1.2/1/ Describe how the plant is divided into fire compartments and fire cells? Please define the terms: fire compartment, fire sections, fire cell? page 118/Section 3.3.B.1.2/2/ How it is ensured that the expected fire resistance and stability ratings are fulfilled?
CZ-E-324 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Dukovany |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CZ-E-325 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Temelin NPP | /Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences?
CZ-E-326 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Temelin NPP |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CZ-E-327 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Dukovany | /Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences?
CZ-E-328 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Dukovany |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CZ-E-329 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Temelin NPP | Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements. page 124/Section 3.4/1/ Did you have OSART missions? What were lessons learnt from OSART missions?
CZ-E-330 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Temelin NPP |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
CZ-E-331 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Dukovany | page 124/Section 3.4/1/ What were lessons learnt from OSART missions? Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
CZ-E-332 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Dukovany |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC?
CZ-E-333 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Research reactor LVR 15 | Please provide more information on the practise of temporary fire load management.
CZ-E-334 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Research reactor LVR 15 | It is declared that a special process in the management system has been implemented. What special process is used at LVR 15?
CZ-E-335 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Research reactor LVR 15 |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CZ-E-336 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Research reactor LVR 15 | How are the fire classes for fire barriers defined?
CZ-E-337 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Research reactor LVR 16 |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CZ-E-338 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Research reactor LVR 15 | Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers?
CZ-E-339 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Research reactor LVR 16 |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CZ-E-340 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Research reactor LVR 15 |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
CZ-E-341 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
CZ-E-342 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
CZ-E-343 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
CZ-E-344 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
CZ-E-345 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Temelin NPP |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
CZ-E-346 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Temelin NPP | Page 60-65 Section 3.2.A.1 Topic 2 - No detail on level of system resilience, hazard tolerance or what EMIT is required and how it is controlled.
CZ-E-347 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Temelin NPP | Page 61 of pdf, section 3.2.A.1.2, assumption 1. "Multi-criteria (combined) detector AlgoRex and SINTESO - new generation detector, working on the principle of measuring and comparing several different variables characteristic for fire (more than 5000 units installed)". Please, explain the main features, variables compared, design standards and other general information regarding this type of detectors. - Page 61 of pdf, section 3.2.A.1.2, assumption 1. "Video smoke detection system - uses a conventional CCTV camera connected to a central unit, analyses incoming images frame by frame and decides if they contain smoke". "This feature allows the system to detect smoke efficiently and quickly even when traditional detection techniques are ineffective (aspirating, linear and spot smoke detectors)". Please, explain the main features, design standards and other general information regarding this type of detectors. - Page 61 of pdf, section 3.2.A.1.2, assumption 1. In general, are SSC important to safety covered by fire detectors? If not, please explain.
CZ-E-348 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Dukovany |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
CZ-E-349 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Dukovany | No detail on level of system resilience, hazard tolerance or what EMIT is required and how it is controlled. (As for Temelin.)
CZ-E-350 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Dukovany | Page 85 of pdf, section 3.2.B.1.2, assumption 1. In general, are SSC important to safety covered by fire detectors? If not, please explain. - Page 89 of pdf, section 3.2.B.1.3, assumption 4. Explain the procedures established for the examination, inspection, maintenance and testing of fire detection and alarm features.
CZ-E-351 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Temelin NPP |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CZ-E-352 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Temelin NPP | Page 65-81 Section 3.2.A.2 Topic 1- large amount of detail regarding the various suppression systems provided on site but it is not clear how it is determined whether the suppression provisions are adequate to extinguish a fire (where this is required) or what the safety classification or design standards against which these systems have been designed. Please could clarification be provided on these points?
CZ-E-353 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Temelin NPP | Page 65-81 Section 3.2.A.2 Topic 4 - No discussion of hazard effects of suppression systems and retention arrangements for fire fighting water. Please could clarification be provided on these points?
CZ-E-354 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Temelin NPP | 1. Section 3.2.A.2.3. Requirements for fire resistance of power (6 and 0.4 kV) and control cables of safety systems and compliance of these cables with established requirements - see paras. (3.2.A.) 2. Section 3.2.A.3.1 Information on availability of safe emergency hydrogen discharge from the turbogenerator in the event of a problem with the sealing system.
CZ-E-355 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Temelin NPP | Page 69 of pdf, section 3.2.A.2.2, assumption 1. "Foam Semi-Stable Extinguishers in Diesel Generating Stations: The equipment is designed to extinguish fires arising in the buildings of diesel generating stations. This equipment does not have its own extinguishing agent tank or its own extinguishing agent pump and works in synergy with mobile firefighting equipment". How long does it take to deploy the mobile firefighting equipment and start suppression activities? Is this special arrangement considered in the training program? Which is the water and foam capacity (volume and suppression time) of the mobile firefighting equipment? - Page 72 of pdf, section 3.2.A.2.2, assumption 2. Fire water supply system - seismic resistant: "Water source - the permanent fire water supply consists of a steel tank with a volume of 70 m3". Which is the suppression duration supposed to calculate this capacity? - Page 77 of pdf, section 3.2.A.2.3, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain.
CZ-E-356 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Dukovany |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CZ-E-357 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Dukovany | As for Temelin.
CZ-E-358 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Dukovany | Page 90 of pdf, section 3.2.B.2.2, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown or any similar provision? - Page 96 of pdf, section 3.2.B.2.2, assumption 1. Are there fixed suppression systems based on foam? - Page 99 of pdf, section 3.2.B.2.3, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain. - Page 101 of pdf, section 3.2.B.2.4, assumption 3. Explain the procedures established for the examination, inspection, maintenance and testing of extinguishing systems.
CZ-E-359 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Dukovany | 1. Section 3.2.A.2.3 Requirements for fire resistance of power (6 and 0.4 kV) and control cables of safety systems and compliance of these cables with established requirements - see paras (3.2.A.) 2. Section 3.2.A.3.1. Information on availability of safe emergency hydrogen discharge from the turbogenerator in the event of a problem with the sealing system.
CZ-E-360 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Temelin NPP |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
CZ-E-361 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Temelin NPP | Page 81 - 84 Section 3.2.A.3 Topic 5 - no detail provided of fire drills and exercises. Please could clarification be provided on this point?
CZ-E-362 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Temelin NPP | Page 81 - 84 Section 3.2.A.3 Topic 3 - no detail provided on EMIT of fire protection measures. Please could clarification be provided on this point?
CZ-E-363 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Temelin NPP | 1. There is no detailed information on the NPP's strategy regarding improvement of the active fire protection, including modernization of the fire protection system. Please provide missing information. 2. Section 3.2.A.3 The information on the organization of safe staff work performance related to fire-hazardous activities is missing. Please provide missing information.
CZ-E-364 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Temelin NPP | Page 81 - 84 Topic 1 Section 3.2.A.3 - no detail provided on whether the internal fire brigade would need to call on the external fire brigade. If so, what are the criteria and how are the external fire brigade contacted? Please could clarification be provided on these points?
CZ-E-365 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Temelin NPP | Page 81 of pdf, section 3.2.A.3, assumption 4. "The firefighters perform repressive activities in four shifts, each with 18 firefighters + 1 driver". Explain the training, organisation, minimum knowledge and physical conditions of the fire brigade. - Page 81 of pdf, section 3.2.A.3, assumption 1. "The maximum time of arrival of the FRSU to the most important buildings of the nuclear power plant (MPU) is 4 minutes from the occurrence of a fire that is detected by EFD". Please, give evidence of the time of arrival from real events and drills. - Page 83 of pdf, section 3.2.A.3.2, assumption 1. Drills and exercises are not described. Please explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade, content and main lessons learnt. - Page 83 of pdf, section 3.2.A.3.2, assumption 2. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 83 of pdf, section 3.2.A.3.2, assumption 2. Explain the coordination between the onsite fire brigade and the offsite response group. - Page 83 of pdf, section 3.2.A.3.2, assumption 2. Explain the written procedures in place defining responsibility and actions of staff in responding to any fire in the installation.
CZ-E-366 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Dukovany |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
CZ-E-367 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Dukovany | As for Temelin.
CZ-E-368 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Dukovany | Page 102 of pdf, section 3.2.B.3, assumption 4. "The 70 firefighters perform repressive activities in four shifts, each with 12 firefighters on the day shift and 11 firefighters on the night shift divided into 3 fire teams". Explain the training, organisation, minimum knowledge and physical conditions of the fire brigade. - Page 102 of pdf, section 3.2.B.3, assumption 1. "The maximum time of arrival of the FRSU to the most important buildings of the nuclear power plant (MPU) is 4 minutes from the occurrence of a fire that is detected by EFD". Please, give evidence of the time of arrival from real events and drills. - Page 104 of pdf, section 3.2.B.3.2, assumption 1. Drills and exercises are not described. Please explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade, content and main lessons learnt. - Page 104 of pdf, section 3.2.B.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 104 of pdf, section 3.2.B.3.2, assumption 2. Explain the coordination between the onsite fire brigade and the offsite response group. - Page 104 of pdf, section 3.2.B.3.2, assumption 2. Explain the written procedures in place defining responsibility and actions of staff in responding to any fire in the installation.
CZ-E-369 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Dukovany | 1. There is no detailed information on the NPP's strategy regarding improvement of the active fire protection, including modernization of the fire protection system. Please provide missing information. 2. Section 3.2.A.3 The information on the organization of safe staff work performance related to fire-hazardous activities is missing. Please provide missing information.
CZ-E-370 | AFP | CZ | Active fire protection | Licensee and regulatory experience |  | NPP | Temelin NPP |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
CZ-E-371 | AFP | CZ | Active fire protection | Licensee and regulatory experience |  | NPP | Temelin NPP | Page 125 of pdf, section 3.6, and all the assumptions. Strengths and weaknesses are not clearly mentioned in the NAR, can you confirm that there are no strengths / weaknesses or otherwise mention them if there are any?
CZ-E-372 | AFP | CZ | Active fire protection | Licensee and regulatory experience |  | NPP | Dukovany |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
CZ-E-373 | AFP | CZ | Active fire protection | Licensee and regulatory experience |  | NPP | Dukovany | Page 125 of pdf, section 3.6, and all the assumptions. Strengths are not clearly mentioned in the NAR, can you confirm that there are no strengths or otherwise mention them if there are any? - Page 125 of pdf, section 3.6, and all the assumptions. Weaknesses are not clearly mentioned in the NAR, can you confirm that there are no weaknesses or otherwise mention them if there are any?
CZ-E-374 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | Research reactor LVR 15 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
CZ-E-375 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | Research reactor LVR 15 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
CZ-E-376 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Research reactor LVR 15 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
CZ-E-377 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Research reactor LVR 15 | Composition of the "shift" dedicated to firefighting. p 125 : "Thanks to the presence of the Fire Rescue Service Unit directly on the site" : it is not clear for the status of this team: public or private ?
CZ-E-378 | AFP | CZ | Active fire protection | Licensee and regulatory experience |  | Research reactor | Research reactor LVR 15 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
CZ-E-379 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
CZ-E-380 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
CZ-E-381 | AFP | CZ | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
CZ-E-382 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | Spent Fuel Storage facility |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
CZ-E-383 | AFP | CZ | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Spent Fuel Storage facility |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
DE-E-384 | FSA | DE | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | NPP not defueled | (p32) : "Within the German design approach, detailed considerations of the fire effects (e.g. temperature, pressure, smoke, soot) within a fire sub-compartment are not necessary because, as a rule, all SSC in the affected fire sub-compartment are conservatively assumed to fail in the event of fire" .. What is the difference between fire compartment and fire sub-compartment? Are fire-ratings different? Is the failure of fire doors due to fire overpressure effect taken into account in the FHA?.
DE-E-385 | FSA | DE | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | Karlsruhe FCF | "For the events with thermal impact, load class BK3 (corresponding to a thermal impact lasting 60 min at 800 °C) is assumed to be sufficiently conservative. Both the cell wing and the ventilation system withstand this event." Can you give information on load class BK? Is it linked with quantity,type, distribution of fire loads in a room? How smoke and soots resulting from the fire are considered for the behavior (efficiency) of HEPA filters?
DE-E-386 | FSA | DE | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | Karlsruhe FCF | Information regarding fire detection performance or human presence to support the statement that "incipient fires will be extinguished directly with available fire extinguishers" is requested.
DE-E-387 | FSA | DE | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | NPP not defueled |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
DE-E-388 | FSA | DE | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | NPP defueled |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
DE-E-389 | FSA | DE | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Karlsruhe FCF |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
DE-E-390 | FSA | DE | Fire safety analysis | Assumptions (TS 02.3) |  | Fuel fabrication facilities | ANF Lingen | p.49,§2.3.1: the text doesn't give any clear information on the type and scope of the fire safety analyses, but focusses rather on the different protection goals. What kind of fire analyses were applied (FHA, deterministic,...). §2.3.2 (p.50): the text gives no information on the key assumptions and methodologies used to perform fire safety analyses. (See report of Romania as a much better example of what is to be put in these sections).
DE-E-391 | FSA | DE | Fire safety analysis | Licensee and regulatory experience |  | Fuel fabrication facilities | ANF Lingen |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Radiological/criticality consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. c) Criticality: How has the criticality aspect been taken into account in the analysis and the impact on the fire protection features. d) How have the radiological hazards (radiological, criticality) been taken into account in the development of the fire brigade procedures (onsite, offsite brigades)? 5. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 6. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 7. Results and revisions of the Fire Safety Analyses, additional analyses: Please provide details about: a) Treatment of modifications and changes in the installations as well as updates of the analysis should be addressed. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for fuel fabrication facilities in your country? 8. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
DE-E-392 | FSA | DE | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | FRM II |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
DE-E-393 | FSA | DE | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | FRMZ (TRIGA Mark-II) |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
DE-E-394 | FSA | DE | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) | Give information on safety functions to be maintained in case if fire? "A fire safety analysis was prepared by a specialist planner" => Could you give more informations?
DE-E-395 | FSA | DE | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Waste storage facility North (ZLN) (DE) | Give information on safety functions to be maintained in case if fire?
DE-E-396 | FSA | DE | Fire safety analysis | Licensee and regulatory experience |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
DE-E-397 | FSA | DE | Fire safety analysis | Licensee and regulatory experience |  | Waste | Waste storage facility North (ZLN) (DE) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
DE-E-398 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | NPP not defueled | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: • Considering that the NAR refers to fire prevention at the "Power Reactor", it should be clarified how "Fire prevention" is adapted to the decommissioning plant; • "3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) • "3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) Please provide information on the above. NAR section 3.1.1 pag. 73 -> If separation of the fire load from unavoidable potential ignition sources is not practicable for technical reasons or operational needs, what other fire protection measures are available to achieve an equivalent level of protection?
DE-E-399 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | NPP not defueled | * Page 10, pint 1.1.3.9. Please give information about the intended end state of decommissioning. *Page 73. Section 3.1 Fire prevention; 3.1.1 Design considerations and fire prevention means; Nuclear power plants. Assumption 2/. " Unavoidable fire loads are:principally segregated in a way that the safety system and the emergency equipment cannot be inadmissibly impaired. If such a separation is not practicable for engineering reasons or due tooperational needs, other fire protection measures are available to achieve an equivalent level of protection" What kind of measures?. This could be imporant for spent fuel pool refrigeration systems (in case of spent fuel in the pool). *Page 77. Section 3.1.2 Overview of arrangements for management and control of fire load and ignition sources; Nuclear power plants. Assumption 3/. "Workplaces must be kept clean. All materials must be removed at the end of work." Who is responsible for checking that the work area is clean and is this checked by another person? REGARDING FIRE LOADS(Taking into account the state of the plant, or indicate if it does not apply) -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) REGARDING HOT WORK (Taking into account the state of the plant, or indicate if it does not apply) -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.)
DE-E-400 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | NPP not defueled |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-401 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | NPP defueled | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: • (b) Considering that the NAR refers to fire prevention at the "Power Reactor", it should be clarified how "Fire prevention" is adapted to the decommissioning plant; • (b)"3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) • (b)"3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) Please provide information about the above. NAR section 3.1.1 pag. 73 -> If separation of the fire load from unavoidable potential ignition sources is not practicable for technical reasons or operational needs, what other fire protection measures are available to achieve an equivalent level of protection?
DE-E-402 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | NPP defueled |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-403 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Karlsruhe FCF | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: • Considering that the NAR refers to fire prevention at the "Power Reactor", it should be clarified how "Fire prevention" is adapted to the decommissioning plant; • "3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) • "3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) Please provide information on the above. NAR section 3.1.1 pag. 73 -> If separation of the fire load from unavoidable potential ignition sources is not practicable for technical reasons or operational needs, what other fire protection measures are available to achieve an equivalent level of protection?
DE-E-404 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Karlsruhe FCF | * Page 20. Please provide information about the intended end state of decommissioning. * Sections 3.1.3 and 3.1.4 of theTS Annex 2 (Detailed contents list for the NARs) are missing. *Page 81. Section 3.1.2 Overview of arrangements for management and control of fire load and ignition sources; Installations under decommissioning. Assumption 3/. REGARDING HOT WORKS. (Taking into account the state of the facility, or indicate if it does not apply) -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) REGARDING FIRE LOADS AND IGNITION SOURCES.(Taking into account the state of the facility, or indicate if it does not apply) -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.)
DE-E-405 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Karlsruhe FCF |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-406 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | NPP not defueled | Some topics for the "Passive fire Protection" are not present (see List of detailed contents for the TS - annex 2), in particular: NAR section 3.3.1.1 pag.122 -> Please clarifiy the compensatory measures if higher fire loads are present. NAR section 3.3.1.1 pag.126 -> How (technique and reference standards) were all the reinforced concrete parts made fire resistant? NAR section 3.3.1.2 pag.127 -> Is a study planned or underway to demonstrate the fire protection function of cable penetrations? | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-407 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | NPP not defueled | *Page 122. Section 3.3 Passive fire protection ;3.3.1 Prevention of fire spreading (barriers); 3.3.1.1 Design approach. Assumption 1/. "Fire compartments may be combined if this does not result in unacceptably high fire risks. This will be particularly the case if the fire loads in these fire compartments have become sufficiently low due to the dismantling of SSC with the result that the fire risk as such is low in each of the fire compartments to be merged." How is the process to make this decission? *Page 126. Section 3.3.1.2 Description of fire compartments and/or cells design and key features; Nuclear power plants. Assumption 1/. "The fire resistance rating of the fire barrier elements is basically the same as the required fire resistance rating of the fire barriers. In the case of pipe penetrations, the function of the partitioning is ensured both in the event of a fire and during specified normal operation. Penetrations of piping systems as well as openings in fire barriers between fire compartments and fire sub-compartments are always sufficiently fire-resistant sealed." What means "sufficiently fire-resistant sealed "?. What are the criteria to select the pipe penetration fire rate? *Page 122. Section 3.3 Passive fire protection ;3.3.1 Prevention of fire spreading (barriers); 3.3.1.1 Design approach. Assumption 4/. "During decommissioning and dismantling, at the latest when all fuel elements have been removed, the requirement for a separation of redundant trains does no longer apply. In this respect, fire sub compartments that have served for separation of redundant trains are no longer needed. Access and escape routes are maintained in accordance with requirements." Please provide a brief description of how access routes are maintained.
DE-E-408 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | NPP defueled | Some topics for the "Passive fire Protection" are not present (see List of detailed contents for the TS - annex 2), in particular: NAR section 3.3.1.1 pag.122 -> Please clarifiy the compensatory measures if higher fire loads are present. NAR section 3.3.1.1 pag.126 -> How (technique and reference standards) were all the reinforced concrete parts made fire resistant? NAR section 3.3.1.2 pag.127 -> Is a study planned or underway to demonstrate the fire protection function of cable penetrations?
DE-E-409 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | NPP defueled |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-410 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Karlsruhe FCF | Some topics for the "Passive fire Protection" are not present (see List of detailed contents for the TS - annex 2), in particular: NAR section 3.3.1.1 pag.122 -> Please clarifiy the compensatory measures if higher fire loads are present. NAR section 3.3.1.1 pag.126 -> How (technique and reference standards) were all the reinforced concrete parts made fire resistant? NAR section 3.3.1.2 pag.127 -> Is a study planned or underway to demonstrate the fire protection function of cable penetrations?
DE-E-411 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Karlsruhe FCF |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-412 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Karlsruhe FCF | *Page 7. Section 1.1.1.6 Installations under decommissioning. "In the process building of the WAK, all process engineering components have been removed and thus most of the activity. In the other WAK facilities, the systems have been emptied and some of them have been dismantled or are being dismantled. Only measures for decontamination and the removal of pipe penetrations and a few remaining facilities are still ongoing. This means that the majority of fire loads has been removed. " Taking into account the state of the facility: Assumption 1/. Are there currently fire-resistant barriers that are still necessary to prevent the release of radioactive material into the environment?, in that case: How is it guaranteed that in the event of a fire there is no emission of smoke and contamination of radioactive material due to the remaining activity?. Are there elements like fire doors, fire dampers...etc to compartmentalize the areas where there is radioactive material in WAK? Are checks carried out on these elements to guarantee their proper functioning? For VEK : *Page 129. Section 3.3.1.2 Description of fire compartments and/or cells design and key features. Assumption 1/. "The VEK building is partitioned into fire sub-compartments. The boundaries of fire sub-compartments are fire-resistant walls. Closures of openings are formed by fire-resistant structural elements. Pipe and cable penetrations as well as doors are also made of fire-resistant structural elements that form the fire compartment boundaries. All passive fire protection features are important in terms of safety and regularly inspected." What fire-resistance do closures of openings have? Is it the same as the boundaries? Assumption 4/. Please, provide information about how access routes for firefigthing are mantained.
DE-E-413 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | NPP not defueled | NAR Section 3.3.2.1 page 134 -> Is the creation of mechanical systems aimed at preventing the penetration of smoke into stairwells underway or planned, if stairwells do not have openings for the evacuation of smoke? (b) NAR section 3.3.2.2 pag.141 -> Is there an upgrade of the ventilation ducts to make them fire resistant?
DE-E-414 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | NPP not defueled | *Page 134. Section 3.3.2 Ventilation systems; 3.3.2.1 Ventilation system design: segregation and isolation provisions (as applicable). Assumption 2/. "The ventilation supply to the control room and the emergency control room is also ensured in the event of a fire in an adjacent fire sub-compartment. However, this does not apply to fire in the ventilation systems supplying the control room and the emergency control room. In the event of a fire in the ventilation system, the continued operation of the control room and the emergency control room can be ensured by manual measures." What are the means to detect a fire in the ventilation system? *Page 134. Section 3.3.2 Ventilation systems; 3.3.2.1 Ventilation system design: segregation and isolation provisions (as applicable). Assumption 1/. "In necessary stairwells, openings for smoke removal need to be provided. If this is not possible for reasons of plant operation or radiation protection, mechanical systems are to be provided to prevent the penetration of smoke into necessary stairwells or to remove any smoke entered from necessary stairwells." Could you descibe the mechanical systems aimed to prevent the penetration of smoke into stairwells.
DE-E-415 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | NPP not defueled |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
DE-E-416 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | NPP defueled | NAR Section 3.3.2.1 page 134 -> Could you descibe the mechanical systems aimed to prevent the penetration of smoke into stairwells. Could you describe the interaction with the ventilation system? NAR section 3.3.2.2 pag.141 -> Is there an upgrade of the ventilation ducts to make them fire resistant?
DE-E-417 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | NPP defueled |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
DE-E-418 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Karlsruhe FCF | NAR Section 3.3.2.1 page 134 -> Could you descibe the mechanical systems aimed to prevent the penetration of smoke into stairwells. Could you describe the interaction with the ventilation system? (b) NAR section 3.3.2.2 pag.141 -> Is there an upgrade of the ventilation ducts to make them fire resistant?
DE-E-419 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Karlsruhe FCF | 1) assumptions: p. 79 " Incipient and small fires are extinguished directly from the inside with available fire extinguishers" , what are the fire detection means allowing for early fire detection?
DE-E-420 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Karlsruhe FCF |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
DE-E-421 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | NPP not defueled |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
DE-E-422 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | NPP defueled |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
DE-E-423 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Karlsruhe FCF |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how?
DE-E-424 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel enrichment facilities | Urenco Gronau | page 75/Section 3.1.1/3/Describe how hot work are performed under the work permit procedure? page 75/Section 3.1.1/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered? page 80/Section 3.1.1/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 82/Section 3.1.3 and 3.1.4/4,5/Missing chapter 3.1.3 "Licensee experince of the implementation of the fire prevention and chapter" and chapter 3.1.4 "Regulator assessment of the fire prevention". Please provide information in the missing chapters. Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
DE-E-425 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel enrichment facilities | Urenco Gronau |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-426 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel enrichment facilities | Urenco Gronau | page 125/Section 3.3.1/1,2,5,7/Describe deficiencies regarding prevention of fire spreading (fire barriers)? Describe improvements or modifications regarding prevention of fire spreading (fire barriers). page 139/Section 3.2.2/3/Describe deficiencies regarding ventilation systems? Describe improvements or modifications regarding ventilation systems.
DE-E-427 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel enrichment facilities | Urenco Gronau |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-428 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | ANF Lingen | topics 4/ and 5/: the proposed table of contents related to licensee's experience and regulator's assessment for fire prevention was not followed: §3.1.3 and 3.1.4 are missing, so there is no clear information on weakness/strengths identified, lessons learned and overview of actions + implementation status for fire prevention. Similarly information on management of flammable gases, combustible gases etc in relation to building design is not available. Please provide the above sections and additional information.
DE-E-429 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | ANF Lingen |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-430 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | ANF Lingen | § 3.1.7, p.79: There seem to exist operationally admissible fire loads and maximum additional fire load quantities. How are these determined (in the part 'Fire safety analysis' there is no information to be found about which fire safety analyses were performed and link with fire loads)?
DE-E-431 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | ANF Lingen | p.127, §3.3.1.2 : there are no values mentioned for required fire resistance of walls, doors, etc. Most of the topics 1 to 7/ are not covered, only on a very high level or not covering what should be covered. For example: §3.3.1.3 (p.132): text is not covering the title (inspections on fire detection and extinguishing features are explained, but this § should be about passive fire protection). Please provide the above information.
DE-E-432 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | ANF Lingen |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-433 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | ANF Lingen | p.139, §3.3.2.1 : It should be explained why there are no fire dampers in the exhaust air system 'in order to comply with the radiological objectives': What are these objectives (no info to be found in fire analysis part)?; Does it means that ventilation and filtration is credited to keep the radiological impact acceptable (and thus no failure is assumed in radiological impact studies)? How is filter clogging or burning taken into consideration (since there are no fire dampers)?
DE-E-434 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | ANF Lingen |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
DE-E-435 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Fuel fabrication facilities | ANF Lingen |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
DE-E-436 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | FRM II | Please provide more information on the practise of temporary fire load management.
DE-E-437 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | FRM II | In-service inspections are carried out in accordance to KTA 15 while they are carried out in accordance to KTA 17 for FRMZ. Page 132 Are in-service inspections based on different documents?
DE-E-438 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | FRM II |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-439 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | FRMZ (TRIGA Mark-II) | Please provide more information on the practise of temporary fire load management.
DE-E-440 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | FRMZ (TRIGA Mark-II) | The fire dampers with fusible link trigger if the temperature of the exhaust air in the respective duct rises above 72 °C due to a fire event." What about spurious actuation? Is that taken into consideration? Page 142
DE-E-441 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | FRMZ (TRIGA Mark-II) | Deficiencies identified are documented and corrective actions taken immediately by specialist companies page 132 What kind of specialist companies are taken? Are these independent surveillance companies?
DE-E-442 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | FRMZ (TRIGA Mark-II) |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-443 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | FRM II | How are the fire classes for fire barriers defined?
DE-E-444 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | FRM II |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-445 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | FRMZ (TRIGA Mark-II) | How are the fire classes for fire barriers defined?
DE-E-446 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | FRMZ (TRIGA Mark-II) |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-447 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | FRM II | Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers? (300 fire dampers in FRMII).
DE-E-448 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | FRM II |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
DE-E-449 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | FRMZ (TRIGA Mark-II) | Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers?
DE-E-450 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | FRMZ (TRIGA Mark-II) |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
DE-E-451 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | FRM II |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
DE-E-452 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | FRMZ (TRIGA Mark-II) |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
DE-E-453 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Biblis | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: NAR section 3.1.3 Licensee's experience of the implementation of the fire prevention (and related subparagraphs). NAR section 3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs). Please provide the missing information on the above. In the NAR there is little clarity in the designations of the facilities as they all (AZB1 -AZB2 and ZLN) fall under "On-site spent fuel and a radioactive waste storage facilities". Therefore, the provisions are treated in a merged manner, without separation in the document. Please clarify the specific provisions for each the facilities. NAR section page 98. Please describe the functions regarding the caissons 2/2a?
DE-E-454 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Biblis |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-455 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Rubenow |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-456 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Biblis | NAR section 3.3.1.1 pag.122 -> Please describe the compensatory measures if higher fire loads are present. Could you describe the fire resistance characteristics of the fire compartments?
DE-E-457 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Biblis |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-458 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Rubenow | NAR section 3.3.1.1 pag.122 -> Please describe the compensatory measures if higher fire loads are present. Could you describe the fire resistance characteristics of the fire compartments?
DE-E-459 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Rubenow |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-460 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Biblis | Please clarify whether and how the filtering units and fan units of the ventilation system are segregated.
DE-E-461 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Biblis |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
DE-E-462 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Rubenow | NAR section 3.3.2.1-> pag.140. Please clarify why class B construction materials are protected by adequate measures (low flammable hydraulic oil). Please clarify whether and how the filtering units and fan units of the ventilation system are segregated?
DE-E-463 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Rubenow |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
DE-E-464 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Biblis |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
DE-E-465 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Rubenow |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
DE-E-466 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: • "3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) • "3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) Please provide information about the above. Please provide more information about the designations of the type of facilities as several of them (AZB1 -AZB2 and ZLN) are treated within the chapter "On-site spent fuel and a radioactive waste storage facilities". NAR section 3.1.1 pag.76 Please provide information regarding in-service inspections of the structural and equipment-related fire protection features. Provide information regarding the caissons 2/2a.
DE-E-467 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) | p80/3.1.2 What is the process for handling temporary fire loads?
DE-E-468 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-469 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Waste storage facility North (ZLN) (DE) | Section 3.1.2. Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined? Section 3.1.2; P.81; (1). NARs are referred to caisson, caisson 2, 2a and caisson 3. Please provide more detailed information about these caissons, indicating from what construction materials they are made of and what kind of waste are they used for.
DE-E-470 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Waste storage facility North (ZLN) (DE) | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: • "3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) • "3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) Please provide information about the above. Please provide more information about the designations of the type of facilities as several of them (AZB1 -AZB2 and ZLN) are treated within the chapter "On-site spent fuel and a radioactive waste storage facilities". NAR section 3.1.2 pag.81 -> the following is reported: "Regarding radioactive substances, combustible and other radioactive substances are stored in the hall areas in a way that they are not to be listed as a fire load application of DIN 18230, since the containers remain tight even in the event of fire. Thus, a fire does not reach the substances. The operational regulations stipulate that in the close vicinity of the storage inventory combustible other radioactive substances may only be stored in suitable containers". Please provide information about the requirements related to fire safety of the "suitable containers".
DE-E-471 | PFP | DE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Waste storage facility North (ZLN) (DE) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
DE-E-472 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) | (a) NAR section 3.3.1.1 pag.122 -> Clarification is requested regarding compensatory measures if higher fire loads are present. (b) Please information that indicates which fire resistance characteristics the fire compartments have.
DE-E-473 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-474 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Waste storage facility North (ZLN) (DE) | Section 2.5.6.2; P.67; (3). How is it ensured that during a fire, the smoke from the administrative building does not enter the adjacent ZLN waste storage? Section 3.1.2; P.81; (2). What is the fire resistance of containers with radioactive waste? Are containers with radioactive waste in ZLN storage premises always closed?
DE-E-475 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Waste storage facility North (ZLN) (DE) | (a) NAR section 3.3.1.1 pag.122 -> Clarification is requested regarding compensatory measures if higher fire loads are present. (b) Indicate which fire resistance characteristics fire compartments have
DE-E-476 | PFP | DE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Waste storage facility North (ZLN) (DE) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
DE-E-477 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) | Clarify whether and how the filtering units and fan units of the ventilation system are segregated?
DE-E-478 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
DE-E-479 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Waste storage facility North (ZLN) (DE) | Section 3.3.2.1; P.140. Please provide information about the ventilation system of the ZLN storage. What safety functions must the ventilation system provide?
DE-E-480 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Waste storage facility North (ZLN) (DE) | NAR section 3.3.2.1-> pag.140 A clarification is requested to the fact that class B construction materials are protected by adequate measures (low flammable hydraulic oil). Clarify whether and how the filtering units and fan units of the ventilation system are segregated?
DE-E-481 | PFP | DE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Waste storage facility North (ZLN) (DE) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
DE-E-482 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
DE-E-483 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Waste storage facility North (ZLN) (DE) | Section. 2.5.5; P.65; (5). For what time period is the ZLN waste storage facility PSR currently being prepared? Section Annex A2; P.167. In the Annex A2 of the NAR is presented list of GRS information notices with relevance in terms of fire protection. Please provide information in which type of NI (SFS, Waste storage, Decommissioning NPP and other) these events took place from 1983 to 1994.
DE-E-484 | PFP | DE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Waste storage facility North (ZLN) (DE) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
DE-E-485 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | NPP not defueled |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
DE-E-486 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | NPP not defueled | Page 87 Section 3.2.1 Topic 2 does not provide details on the fire rating of the cables and what EMIT is provided for the fire protection system. Is the fire detection and alarm system backed up by emergency supplies?
DE-E-487 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | NPP not defueled | Page 87 Section 3.2.1 Topic 1 What is the nuclear safety class of the fire detection and alarm system?
DE-E-488 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | NPP defueled |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
DE-E-489 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | NPP defueled | As for NPP not defuelled
DE-E-490 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Karlsruhe FCF |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
DE-E-491 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Karlsruhe FCF | Page 86/87 Section 3.2.1 Topic 1 The NAR does not provide detail on the nuclear safety class of the fire detection and alarm system
DE-E-492 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Karlsruhe FCF | Page 90 Section 3.2.1.2 Topic 1 The NAR does not provide detail on the fire rating of the cables and what EMIT is carried out for the fire protection system.
DE-E-493 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Karlsruhe FCF | Page 86/87 Section 3.2.1.2 Topic 2 Is the fire detection and alarm system backed up by emergency supplies? What hazard tolerance is designed in to the system?
DE-E-494 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | NPP not defueled |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
DE-E-495 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | NPP not defueled | Page 92 Section 3.2.2 Topic 1 does not explain the nuclear safety class of the fire suppression system.
DE-E-496 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | NPP not defueled | Page 94 Section 3.2.2 Topic 2 The NAR states that sufficient fire extinguishing water is provided but does not explain how this is determined. What capacity is required and what is provided?
DE-E-497 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | NPP defueled |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
DE-E-498 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | NPP defueled | As for NPP not defuelled
DE-E-499 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Karlsruhe FCF |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
DE-E-500 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Karlsruhe FCF | Page 93/94 Section 3.2.2 Topic 1 The NAR does not explain the nuclear safety class of the fire suppression system.
DE-E-501 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Karlsruhe FCF | Page 96 Section 3.2.2.1.1 Topic 2 - The NAR does not explain why the suppression systems as provided are deemed to be sufficient to extinguish a fire.
DE-E-502 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | NPP not defueled |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
DE-E-503 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | NPP not defueled | Page 106 Section 3.2.3 Topic 5 does not explain whether training is provided to personnel for the use of hand held and portable fire extinguishers or the frequency of training, drills and emergency exercises for on-site fire fighters. Please provide the relevant information.
DE-E-504 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | NPP not defueled | Page 107 Section 3.2.3 Topic 5 does not explain what information is provided to the off-site fire brigade to ensure familiarity with the site should they be required to attend. Please provide the relevant information.
DE-E-505 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | NPP not defueled | Pages 107 Section 3.2.3 Topic 3 what measures are in place to ensure the operability of fire protection equipment and what are the EMIT arrangements are for this equipment?
DE-E-506 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | NPP defueled |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
DE-E-507 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | NPP defueled | As for NPP not defuelled
DE-E-508 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Karlsruhe FCF |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
DE-E-509 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Karlsruhe FCF | Page 115 and 118 Sections 3.2.3.1 and 3.2.3.2 Topic 5 The NAR does not mention training for personnel for the use of hand held and portable fire extinguishers or the frequency of training, drills and emergency exercises for on-site fire fighters. The NAR does not explain what information is provided to the off-site fire brigade to ensure familitarity with the site should they be required to attend.
DE-E-510 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Karlsruhe FCF | Page 116 Section 3.2.3.2 Topic 3 - The NAR does not mention what measures are in place to ensure the operability of fire protection equipment or what the EMIT arrangements are for this equipment.
DE-E-511 | AFP | DE | Active fire protection | Licensee and regulatory experience |  | Decommissioning | NPP not defueled |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
DE-E-512 | AFP | DE | Active fire protection | Licensee and regulatory experience |  | Decommissioning | NPP defueled |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
DE-E-513 | AFP | DE | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Karlsruhe FCF |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
DE-E-514 | AFP | DE | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Karlsruhe FCF | p. 67 It is noted that many decommissioning measures have been carried out, but no information about licensee and regulatory experience is given. Please provide the relevant information.
DE-E-515 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | FRM II |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
DE-E-516 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | FRMZ (TRIGA Mark-II) |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
DE-E-517 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | FRMZ (TRIGA Mark-II) | P.96: One unique fire brigade information centre (containing fire brigade control panel, the display panel, and the route maps), located in the entrance area of the old building. This seems a vulnerability in case of fire impacting this unique area? Will this be changed, considering the construction of the new building? P.84: The RR has a fire detection and alarm system with automatic notification to the professional fire brigade of the city of Mainz as well as to two lines of the permanent on-call service team of the FR MZ. P.96: the unique fire detection display panel seems to be in the “old building”. What is the fire-related information available in the main control room to the operations staff, for decision making relate to the RR operation?
DE-E-518 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | FRM II |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
DE-E-519 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | FRM II | 1. Section 3.2.2.1, p. 93 There is no information on the availability of drainage and a tank for temporary storage of used water, as well as on measures for its neutralization (removal) after the fire extinguishing system is activated. Please provide the requested infomation 2. Section 3.2.2.1, p. 94 How the volume and pressure in the fire water supply system in the ring mains in case of its rupture/loss of integrity are ensured? Are there in place alternative organizational and technical measures that are not listed are envisaged (for example, isolation of certain areas using valves, etc.)?
DE-E-520 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | FRMZ (TRIGA Mark-II) |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
DE-E-521 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | FRMZ (TRIGA Mark-II) | P.98: it seems that the reactor hall is not protected by a fixed extinguishing system; only by portable means. Is that info correct? Why? Having a fixed system would help avoiding fire brigade having to fight fire in a zone with potential radioactive environment.
DE-E-522 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | FRM II |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
DE-E-523 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | FRM II | p 115 : "An on-site fire brigade, if required, is dedicated by the competent authorities" : No information on many subject as composition of the fire brigade if it exists. Please provide more information on fire brigade.
DE-E-524 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | FRM II | The information regarding data record keeping and exchange of the fire suppression system malfunctions is missing. Please provide missing information.
DE-E-525 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | FRMZ (TRIGA Mark-II) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
DE-E-526 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | FRMZ (TRIGA Mark-II) | • P.116: It seems that active firefighting at the FR MZ is exclusively covered by the municipal professional fire brigade. Expected intervention time for the external brigade? How much time is there between fire detection and actual start of attacking a fire in a radiological controlled area (such as the radionuclide laboratory in the reactor hall annex – see p.124)? How is the external fire brigade made familiar with the installations and with the precautions for fire fighting in a radiological controlled area? • The FR MZ site plan (p.52) seems to indicate that the new building in construction will block one of the access route to the reactor building, which was dedicated to the fire brigade. To be clarified.
DE-E-527 | AFP | DE | Active fire protection | Licensee and regulatory experience |  | Research reactor | FRM II |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
DE-E-528 | AFP | DE | Active fire protection | Licensee and regulatory experience |  | Research reactor | FRMZ (TRIGA Mark-II) |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
DE-E-529 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Biblis |  | p. 85 For some of the installations for active fire protection measures, it is not indicated which standard is applied in design and operation. p.85 - Information is missing for some of the installations on the active fire protection measures and it is not specified how they technically interact
DE-E-530 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Biblis | (Note: As per "At the Biblis site, BGZ operates two storage facilities for radioactive waste, AZB 1 and AZB 2") In the NAR in there is little clarity in the designations of the facilities as they all (AZB1 - AZB2 and ZLN) fall under "On-site spent fuel anda radioactive waste storage facilities". Therefore, the provisions are treated in a merged manner, without separation in the document. ---> Clarify the specific provisions (Types, main characteristics and performance expectations) for the Dry storage installation. (Note: For ZLN facility are illustrated more clearly.) --> Please highlight weaknesses and any related improvement measures.
DE-E-531 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Biblis |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
DE-E-532 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Rubenow |  | p. 85 For some of the installations for active fire protection measures, it is not indicated which standard is applied in design and operation. p.85 - Information is missing for some of the installations on the active fire protection measures and it is not specified how they technically interact
DE-E-533 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Rubenow | (ZLN North) (Note: As per "At the Biblis site, BGZ operates two storage facilities for radioactive waste, AZB 1 and AZB 2") In the NAR in there is little clarity in the designations of the facilities as they all (AZB1 - AZB2 and ZLN) fall under "On-site spent fuel anda radioactive waste storage facilities". Therefore, the provisions are treated in a merged manner, without separation in the document. ---> Clarify the specific provisions (Types, main characteristics and performance expectations) for the Dry storage installation. (Note: For ZLN facility are illustrated more clearly.) ---> Please highlight the motivation for the necessity of the installed system (e.g. if it is derived from the fire safety analysis or national legislation) --> Please highlight weaknesses and any related improvement measures.
DE-E-534 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Rubenow |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
DE-E-535 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Biblis |  | p. 85 For some of the installations for active fire protection measures, it is not indicated which standard is applied in design and operation. p.85 - Information is missing for some of the installations on the active fire protection measures and it is not specified how they technically interact
DE-E-536 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Biblis | (Note: As per "At the Biblis site, BGZ operates two storage facilities for radioactive waste, AZB 1 and AZB 2") In the NAR in there is little clarity in the designations of the facilities as they all (AZB1 - AZB2 and ZLN) fall under "On-site spent fuel anda radioactive waste storage facilities". Therefore, the provisions are treated in a merged manner, without separation in the document. ---> Please clarify the specific provisions (Types, main characteristics and performance expectations) for the Dry storage installation. (Note: For ZLN facility are illustrated more clearly.)
DE-E-537 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Biblis |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
DE-E-538 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Biblis | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards.
DE-E-539 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Rubenow | (ZLN North) (Note: As per "At the Biblis site, BGZ operates two storage facilities for radioactive waste, AZB 1 and AZB 2") In the NAR in there is little clarity in the designations of the facilities as they all (AZB1 - AZB2 and ZLN) fall under "On-site spent fuel anda radioactive waste storage facilities". Therefore, the provisions are treated in a merged manner, without separation in the document. ---> Please clarify the specific provisions (Types, main characteristics and performance expectations) for the Dry storage installation. (Note: For ZLN facility are illustrated more clearly.) ---> Please highligh the motivation for the necessity of the installed system (e.g. if it is derived from the fire safety analysis or national legislation) p. 85 For some of the installations for active fire protection measures, it is not indicated which standard is applied in design and operation. p.85 - Information is missing for some of the installations on the active fire protection measures and it is not specified how they technically interact --> --> pag. 103 Please provide information on the management, from a radiological point of view, of any water used for fire extinguishing. --> Please highlight weaknesses and any related improvement measures.
DE-E-540 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Rubenow |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
DE-E-541 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Rubenow | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards.
DE-E-542 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Biblis |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
DE-E-543 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Biblis | Please highlight weaknesses and any related improvement measures.
DE-E-544 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Biblis | Information should be provided on the documentary procedure for notifying volunteer units and neighboring fire departments.
DE-E-545 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Rubenow |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
DE-E-546 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Rubenow | Please highlight weaknesses and any related improvement measures.
DE-E-547 | AFP | DE | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Biblis |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
DE-E-548 | AFP | DE | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Rubenow |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
DE-E-549 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
DE-E-550 | AFP | DE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Waste storage facility North (ZLN) (DE) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
DE-E-551 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
DE-E-552 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
DE-E-553 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Waste storage facility North (ZLN) (DE) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
DE-E-554 | AFP | DE | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Waste storage facility North (ZLN) (DE) | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
DE-E-555 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
DE-E-556 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) | Information should be provided on the documentary procedure for notifying volunteer units and neighboring fire departments.
DE-E-557 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Waste storage facility North (ZLN) (DE) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
DE-E-558 | AFP | DE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Waste storage facility North (ZLN) (DE) | Information should be provided on the documentary procedure for notifying volunteer units and neighboring fire departments.
DE-E-559 | AFP | DE | Active fire protection | Licensee and regulatory experience |  | Waste | Biblis storage facility (AZB 1 and AZB 2) (DE) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
DE-E-560 | AFP | DE | Active fire protection | Licensee and regulatory experience |  | Waste | Waste storage facility North (ZLN) (DE) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
DK-E-561 | FSA | DK | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Hot Cell facility - Risø site |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified. | 1.a) The fire safety analysis carried out in the years 1998 – 2000 focused on the DR3, which at the time was considered the main potential source of radioactive releases in the case of a fire. The analysis identified areas/rooms where Systems, Structures and Components (SSC) necessary for safety could be affected by a fire or where a fire could directly lead to the release of radioactive material. Additional areas where SSC necessary for safety could be affected by a fire, but where the function of the SSC in question was ensured through additional auxiliary or back-up systems, were also identified. For each area, the inventory of flammable and combustible materials was assessed. On this basis, a set of recommendations regarding the building structure (primarily regarding fire sectioning and cable conduits), operational procedures (reduction of flammable and combustible materials) and detection systems and fire alarms (direct alerting of fire department) were developed as compensatory measures for the absence of an on-site fire department. In the analysis it was concluded that closing down the on-site fire department would result in an increased response time from 5 minutes to 10-15 minutes. The analysis further concluded that implementation of all recommended improvements would result in an overall increase in fire safety, primarily due to the increase in passive safety features; enhanced fire sectioning and automated detection and alarm systems. In consequence, it was decided to close the on-site fire department. Specifically for the Hot Cell facility: The storage facilities and installations currently under decommissioning at the Risø site were originally designed and constructed in accordance with building codes and regulations in force at the time of construction in the late 1950s. All subsequent structural changes to nuclear installations and facilities on the Risø Site have been subject to the Danish Building Regulations which specify the requirements of the Building Act, including fire safety (see chapter 1 and section 2.0 in the report). The Hot Cell facility has been subject to a number of structural modifications e.g. in connection with the transition from operations to post-closure activities and again when dismantling activities were initiated. The specific building regulations applicable to the most recent changes to the Hot Cell facility are the BR10 (the building regulations which entered into force in 2010). As for the Drum Storage, the analyses supporting these regulations have centered on ensuring fire detection, fire alert and evacuation, supported by passive means for mitigating fire spread. 1.b) The single failure criterion is not a part of the fire analyses 1.c) Combinations of fire and other events have not been included in the fire analyses 1.d) Combinations of fire and other events have not been included in the fire analyses 2) N/A 3.a) No information was supplied by the operator/licensee. Any changes applied to the Hot Cell facility must be consistent with the current Danish building regulations (BR) at the time of changes to the facility, including with respect to fire resistance. 3.b) No information was supplied by the operator/licensee. 3.c) No information was supplied by the operator/licensee. 4) No information was supplied by the operator/licensee. 5) No information was supplied by the operator/licensee. 6) The building requirements refer to standards for construction materials relevant for generation of e.g. smoke etc., but these are generally applicable requirements and not directed specifically towards the effects onto SSC. 7) No information was supplied by the operator/licensee.. 8) Yes, the response times of the fire brigade have been taken into account in the fire analyses at the Risø site. See 1.a) above 9.a) The assessment is based on a conservative approach, where the nuclide composition is conservatively estimated to derive the source term. From this, a certain percentage is evaluated as possibly releasable in the case of an explosion followed by a fire, again with an applicable in-built conservatism in estimation of particular airborne activity. From these initial assumptions, the relevant exposure source term is derived, and used for three main calculations: doses in the immediate aftermath during the emergency exposure situation to the internal workers as well as the public, doses during the clean-up to the internal clean-up teams and the public, and finally expected doses during the following existing exposure situation. These calculations are not done in any specific program other than ordinary mathematics, by applying a Gaussian spread model by hand using mathematical calculation software. 9.b) No information was supplied by the operator/licensee. 10.a) No information was supplied by the operator/licensee. 10.b) N/A 11) No information was supplied by the operator/licensee. 12.a) The fire safety analysis has not been updated. 12.b) N/A 12.c) Operational Limits and Conditions for Danish Decommissioning specify that safety related documentation must be reviewed and updated as necessary every five years. All decommissioning plans must be updated every time changes are made, which have an impact on safety. Fire protection inspections are carried out every year at all DD's facilities by external independent certified experts (RMG) who are accredited (DS/EN ISO/IEC 17020:2005). 13) As stated in the general conclusions of the NAR, it should be recognized that ensuring coordination between regulatory authorities at different hierarchical levels and with reference to different legislative requirements is challenging and presents risks of duplication of work and requirements to the licensee. In addition, risks of insufficient regulation for critical areas might arise. In this regard, clear specification of regulatory requirements regarding fire safety as well as licensee competences in the field of fire safety is key to the effective implementation of a fire protection concept. These lessons must be included in the continuous development of the fire protection concept for the remaining ongoing decommissioning activities and in the definition of a new fire protection concept for the planned storage facility at the Risø site. | DK-E-564
DK-E-562 | FSA | DK | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Drum storage facility - Risø site | /1/ P-21: No specific modelling of fire development, fire spread or timing of events leading to releases have been carried out. Based on which thought process, this decision was made? /2/and /4/ P-10: The installation is expected to provide limited containment of radioactive materials in case of a fire. How do you ensure that the safety objectives are met and the radiological consequences are acceptable? |  | 1 - The area is enclosed, not used, and the fire load as well as ignition sources are almost non-existent. 2 - Safety aspects and consequences have been assessed and have not changed since the assessment was made, so there is no immediate reason to conduct new assessments continuously.
DK-E-563 | FSA | DK | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Drum storage facility - Risø site | :"For the Drum Storage, the scenario presented a scalable assessment of the effects of the release of radioactive materials from the storage in the event of an explosion followed by a fire (p20)" + " No specific model for fire phenomena for the Drum Storage has been applied (p21)". Describe assumptions made and tools used (from fire/radiological point of view) to assess the release of radioactive materials?. |  | The assessment is based on a conservative approach, where the nuclide composition is conservatively estimated to derive the source term. From this, a certain percentage is evaluated as possibly releasable in the case of an explosion followed by a fire, again with an applicable in-built conservatism in estimation of particular air-borne activity. From these initial assumptions, the relevant exposure source term is derived, and used for three main calculations: doses in the immediate aftermath during the emergency exposure situation to the internal workers as well as the public, doses during the clean-up to the internal clean-up teams and the public, and finally expected doses during the following existing exposure situation. These calculations are not done in any specific program other than ordinary mathematics, by applying a Gaussian spread model by hand using mathematical calculation software.
DK-E-564 | FSA | DK | Fire safety analysis | Licensee and regulatory experience |  | Waste | Drum storage facility - Risø site |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified. | 1.a) The fire safety analysis carried out in the years 1998 – 2000 focused on the DR3, which at the time was considered the main potential source of radioactive releases in the case of a fire. The analysis identified areas/rooms where Systems, Structures and Components (SSC) necessary for safety could be affected by a fire or where a fire could directly lead to the release of radioactive material. Additional areas where SSC necessary for safety could be affected by a fire, but where the function of the SSC in question was ensured through additional auxiliary or back-up systems, were also identified. For each area, the inventory of flammable and combustible materials was assessed. On this basis, a set of recommendations regarding the building structure (primarily regarding fire sectioning and cable conduits), operational procedures (reduction of flammable and combustible materials) and detection systems and fire alarms (direct alerting of fire department) were developed as compensatory measures for the absence of an on-site fire department. In the analysis it was concluded that closing down the on-site fire department would result in an increased response time from 5 minutes to 10-15 minutes. The analysis further concluded that implementation of all recommended improvements would result in an overall increase in fire safety, primarily due to the increase in passive safety features; enhanced fire sectioning and automated detection and alarm systems. In consequence, it was decided to close the on-site fire department. Specifically for the Drum storage facility: The protection against releases to the environment in the event of fire is to a large extent relying on early detection and rapid extinction of fire in order to limit the potential for releases into the surroundings. The failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) has only been taken into account to a lesser degree/is not a part of the fire analysis for the Drum Storage. 1.b) The single failure criterion is not a part of the fire analyses 1.c) Combinations of fire and other events have not been included in the fire analyses 1.d) Combinations of fire and other events have not been included in the fire analyses 2) N/A 3.a) No information was supplied by the operator/licensee.. 3.b) No information was supplied by the operator/licensee.. 3.c) No information was supplied by the operator/licensee.. 4) No information was supplied by the operator/licensee.. 5) No information was supplied by the operator/licensee.. 6) The building requirements refer to standards for construction materials relevant for generation of e.g. smoke etc., but these are generally applicable requirements and not directed specifically towards the effects onto SSC. 7) Yes, the response times of the fire brigade have been taken into account in the fire analyses at the Risø site. See 1.a) above 8.a) The assessment is based on a conservative approach, where the nuclide composition is conservatively estimated to derive the source term. From this, a certain percentage is evaluated as possibly releasable in the case of an explosion followed by a fire, again with an applicable in-built conservatism in estimation of particular airborne activity. From these initial assumptions, the relevant exposure source term is derived, and used for three main calculations: doses in the immediate aftermath during the emergency exposure situation to the internal workers as well as the public, doses during the clean-up to the internal clean-up teams and the public, and finally expected doses during the following existing exposure situation. These calculations are not done in any specific program other than ordinary mathematics, by applying a Gaussian spread model by hand using mathematical calculation software. 8.b) No information was supplied by the operator/licensee. 9.a) No information was supplied by the operator/licensee.. 9.b) N/A 10) No information was supplied by the operator/licensee. 11.a) The fire safety analysis has not been updated. 11.b) N/A 11.c) Operational Limits and Conditions for Danish Decommissioning specify that safety related documentation must be reviewed and updated as necessary every five years. All decommissioning plans must be updated every time changes are made, which have an impact on safety. Fire protection inspections are carried out every year at all DD's facilities by external independent certified experts (RMG) who are accredited (DS/EN ISO/IEC 17020:2005). 12) As stated in the general conclusions of the NAR, it should be recognized that ensuring coordination between regulatory authorities at different hierarchical levels and with reference to different legislative requirements is challenging and presents risks of duplication of work and requirements to the licensee. In addition, risks of insufficient regulation for critical areas might arise. In this regard, clear specification of regulatory requirements regarding fire safety as well as licensee competences in the field of fire safety is key to the effective implementation of a fire protection concept. These lessons must be included in the continuous development of the fire protection concept for the remaining ongoing decommissioning activities and in the definition of a new fire protection concept for the planned storage facility at the Risø site. | DK-E-561
DK-E-565 | PFP | DK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Hot Cell facility - Risø site | Section II-3.1.3; (3). There is no information what type of permits exits to allow hot works and whether there are management procedures developed by the licensee. Please provide information on this topic. Section 1.1.2; P. 9; (3). Please provide detail information about contaminated blasting materials. Section II-3.1.1; (1). There is no information about permanent and temporary fire loads management and fire load density of building 227 fire compartments. Please provide information on this topic. |  | Section II-3.1.3; (3) National legislation and guidelines on firesafety are followed when performing hot work. No specific licence is required. Additionally a statutory workplace assessment (APV) is always made for each work task at the plant, in which assesses conventional safety, including fire safety Section 1.1.2; P. 9; (3) The blasting material consists of steel grit, which after use is contaminated with paint residues and radiological contamination. The contamination consists of a wide range of nuclides, of which the content of the key nuclide Cs-137 was initially estimated to be approximately 200 GBq in total. Approximately 85% of this has been extracted by the steel grit. Section II-3.1.1; (1) There is generally a very low fire load at facilities undergoing decommissioning. This is continuously ensured by regular fire inspections.
DK-E-566 | PFP | DK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Hot Cell facility - Risø site | * Page 11. The intended end state is not mentioned. The year of authorization for decommissioning is missing. *Page 33. Section: Hot Cells; II-3.1.1 Design considerations and prevention means. Assumption 3/. “In the work areas surrounding the row of Hot Cells, equipment as well as fixed installations that may act as ignition sources are present. The following is an assessment of potential sources of ignition in the areas surrounding the row of Hot Cells. • Construction switchboards • Electric Truck • Control panel for ventilation systems …" Is any of this equipment energized?, in that case, Are there maintenance proccedures for electrical equipment? Are there proccedures to avoid the storage of combustible materials near to ignitions sources (like electrical equipment)? *Page 34. Section II-3.1.2 Overview of arrangements for management and control of fire load and ignition sources. Assumption 3/. " Materials/waste that can unnecessarily increase the fire are not stored within the facility." Are the (fix and temporary) storage areas registered and clearly identified? Storage areas are approved by permits? in that case, Is it periodically checked that fire loads remain in the state in which they were approved? What type of procedures are in place to manage fire loads? *Page 34. Section II-3.1.2 Overview of arrangements for management and control of fire load and ignition sources. Assumption 3/. |  | P.11. The intended end state is release from regulatory control (greenfield). The approval from the regulatory body to begin decommissioning of Hot Cells was issued in 2008. P 33. Section II-3.1.1. The equipment used for decommissioning is energized by default and is maintained continuously according to current Danish legislation. There are no specific procedures to prevent the accumulation of combustible materials at ignition sources, but inspections are conducted regularly for this, as well as the cleanliness of the area. P. 34 Section II-3.1.2. There are specific storage areas in the hot cell facility for contaminated equipment used for decommissioning. Non-contaminated equipment is stored in areas outside the facility. These areas are not specifically marked, but this information is part of the training received by the employees working at the facility, and unauthorized personnel do not have access. Permits are not used for this type of storage in classified areas, and the fire load and ignition sources are continuously controlled through fire inspections.
DK-E-567 | PFP | DK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Hot Cell facility - Risø site |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications. | See response to DK-E-566. Safety regarding the execution of hot work is described in work plans, which must be internally approved before work commences. All personnel conducting hot work must undergo mandatory training covering occupational health and safety aspects related to welding and thermal cutting. Supervision is conducted after the completion of hot work but not before and during. There is no hydrogen production occurring, so the risk associated with hydrogen is not relevant. | DK-E-566
DK-E-568 | PFP | DK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Hot Cell facility - Risø site | *Page 41. Section Hot Cells; II-3.3.1 Prevention of fire spreading (barriers); II-3.3.1.1 Design approach. Assumtpion 1/. "In connection with preparing the facility for decommissioning in 2010, the facility was isolated from the rest of the building with gypsum board walls in fire class BD-60. The entire facility is built in areas around the row of cells, which function as fire cells with BD-30 walls and doors, and which are connected by airlocks." What criteria were taken into account to select a fire resistance of DB 60? Is taken into account this fire resistance if fire loads are introduced in the area? *Page 42. Section II-3.3.1.2 Description of fire compartments and/or cells design and key features. Assumption 2/. Is not described how it is ensured that the expected fire resistance and stability ratings are fulfilled. Please, provide this information. *Page 42. Section II-3.3.1.2 Description of fire compartments and/or cells design and key features. Assumption 4/. Is not described how access routes for firefighting are maintained. Please, provide this information. |  | P. 41 Section II-3.3.1. The criteria for selection of fire resistance of walls was chosen according to applicable (at the time of construction) Danish legislation. DD does not possess in-house fire technical expertise but relies on external accredited consultancy P. 42 Section II-3.3.1.2. The fulfilment of the expected fire resistance and stability is assessed and assured through regular internal and independent external fire inspections. P. 42 Section II-3.3.1.2. Access routes for firefighting are maintained through regular internal and external fire inspections.
DK-E-569 | PFP | DK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Hot Cell facility - Risø site |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers? | Risk is considered through the placement and construction of fire compartments and barriers. The facility has different fire ratings for walls and doors designed to contain and limit the spread of fire. Special attention is given to critical areas where a fire could pose a radiological risk. Regular assessments by external accredited advisors, particularly when changes are made, also play a crucial role in risk management. Propagation of fire is prevented or delayed through the use of fire-resistant materials and compartmentation. For example, walls in critical areas (such as the cell row itself) are constructed with concrete and an internal steel liner, and all doors are built to at least BD-30 fire resistance. Additionally, the facility employs airlocks and maintains different pressure zones to help prevent the spread of fire through air movements. The ventilation systems are designed to maintain negative pressures in specific compartments to control air flow direction, reducing the risk of spreading contaminants and fire. The system can be regulated and shut off in separate areas, enhancing the ability to isolate a fire physically and environmentally. For example, in case of a fire, ventilation can be shut off in affected areas to prevent the spread of smoke and flames. New assessments are regularly made by external advisers when changes are made that could affect fire safety, implying an ongoing improvement process based on those assessments. Management of fire safety, including compartmentation, is handled through continuous monitoring and evaluation, especially during and after any changes to the facility's structure or operation. Fire loads directly influence the design and specifications of fire barriers. Higher fire loads require barriers with higher fire-resistance ratings to ensure that fires can be contained long enough for effective response and mitigation. The facility’s design considers the likely fire load in each area, choosing appropriate materials and ratings for barriers to match the risk level.
DK-E-570 | PFP | DK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Hot Cell facility - Risø site | *Page 43. Section II-3.3.1.2 Description of fire compartments and/or cells design and key features. Assumption 1/. "REGARDING ACCESS ROUTES. • B2 Technical room on the 1st floor with ventilation filters o Walls and doors are all minimum BD 30 min o Ceilings are made of concrete o Floors are made of concrete, with individual penetrations for ventilation (there is a dispen sation for not having fire dampers in the channel penetrations, as it was assessed at the time of construction that it was more important to be able to maintain differentiated nega tive pressures in the areas of the facility)." Are there no fire dampers between B2 and the area below (D), or in the entire ventilation system? *Page 43. Section II-3.3.1.2 Description of fire compartments and/or cells design and key features. Assumptions 1/ 5/ and 3/. "The ventilation is divided so that it is possible to regulate and switch off the following separate areas: • A: The cell row • C: The area south of the cell row • E: The area north and east of the cell row • B: The areas on the 1st floor above the row of cells. • D: Car lock, with separate control of containment for vacuum cleaner" What elements are used to maintain divided ventilation in separate areas, or isolate the areas? If it is used elements like fire dampers or similar, that it is necesary to be actuated, Is its proper functioning periodically checked? Assumtpion 1/. How smoke is extracted in case of fire to maintain access routes for firefighting? |  | From technical room B2, there is an evacuation route through the area marked 'DTU'. The map on page 42 only covers the nuclear facility portion of the building; please refer to Figure 3 in Section II-3.1.1 for a map of the entire building. There is authorization from the local fire authorities not to install fire dampers in the ventilation system, and there is no provision for smoke ventilation in the event of a fire.
DK-E-571 | PFP | DK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Hot Cell facility - Risø site |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made? | Fire dampers are not installed in the ventilation system at Hot Cell facility. See response to DK-E-570. | DK-E-570.
DK-E-572 | PFP | DK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Hot Cell facility - Risø site | Section 3.4; P. 44; (1). Please provide information if it is correct that the Hot Cell's last fire analysis was carried out only in 2000 and why the fire risk analysis was not updated prior to decommissioning. Are fire risk analysis safety assessments carried out periodically? |  | P. 44 Section 3.4. There has not been an FSA specifically for Hot Cells upon the start of decommissioning in 2008, as it was assessed that the FSA from 2000, which was done for an operating research reactor (DR 3) could be assumed to be sufficient representative for the risk associated with decommissioning in case of fire (worst case). Periodic FSAs are not conducted, but assessment of risk of fire is considered during annual independent fire inspections.
DK-E-573 | PFP | DK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Hot Cell facility - Risø site |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries). | No specific changes were made to the fire strategy during the commencement of decommissioning. However, any modifications to the building, such as the construction of walls, comply with the national fire regulations that were in effect at the time of construction. Fire events is not classified or categorized. All fire related incidents are reported to the nuclear regulatory authorities, including smouldering events. DD has had 2 minor fire-related incidents in the last 10 years. One was in electrical installations in connection with the asphalt plant, which is now decommissioned. The other was in the drum dryer plant (smouldering), which is also now decommissioned. Both incidents triggered fire alarms, and the fire brigade was automatically called, so everything worked as intended.
DK-E-574 | PFP | DK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Drum storage facility - Risø site | Section I-3.1.2; (3). Please provide information about fire loads and the different types of potential ignition sources of drum storage building 212. Section I-3.1.2; (3). Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined? Section I-3.1.2; P.30. What five additional fire preventive measures are prepared and implemented? |  | The waste stored in the Drum Storage primarily consist of metal parts contained in concrete lined steel drums. The only source of ignition inside the Drum Storage is the remote-controlled crane. There is no specific permissible limits for permanent and temporary fire loads. However the authorities require that the fire load be kept as low as possible. Storage of waste in storage facilities must therefore be done with particular consideration for minimizing the fire load. This entails taking measures to limit the amount of flammable material and ensuring that any flammable materials are stored safely to reduce the risk of fire. The five fire preventive measures prepared and implemented are: • All electrical installations at the plant are carried out by authorized electricians • All electric equipment must be CE marked • Charging batteries is done outdoors or in a ventilated area. • It is ensured that no easily flammable construction materials are used • Materials/waste that can unnecessarily increase the fire are not stored within the facility
DK-E-575 | PFP | DK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Drum storage facility - Risø site |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications. | The fire load inside the Drum Storage is deemed low, as the waste stored primarily consist of metal parts contained in concrete-lined steel drums. The only source of ignition inside the Drum Storage is the remote-controlled crane. Transient fire loads comprise temporary items like maintenance equipment, waste materials, and combustible substances brought into the facility temporarily. There is no systematically documention on the inventory of fire loads (e.g. computer system). Written work instructions are made for receiving of waste from external customers and for specific tasks carried out at the facility, in which it is assessed whether further measures should be taken to increase fire safety. The inspection program for fire loads entails regular assessments conducted by external impartial experts, certified by the national accreditation body. These inspections occur every two years and involve participation from nuclear regulatory authorities. Lessons learned from these inspections primarily focus on operational safety, emphasizing the importance of minimizing ignition sources and fire loads. Hot work activities are not conducted within the Drum storage facility. There is no hydrogen production occurring, so the risk associated with hydrogen is not relevant.
DK-E-576 | PFP | DK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Drum storage facility - Risø site | Section 1.1.2; P.10; (3). Are 210 L steel drums containing flammable radioactive waste separated from drums containing non-combustible waste at the storage site and are they marked as containing flammable waste? Section 1.1.2; P.10; (2, 5). Are the 210L steel drums certified for use with combustible waste? Have these drums been tested for fire resistance? If so, what is their degree of fire resistance? |  | The drums contain historical waste from the nuclear facilities at Risø¸ and do not contain combustible waste, but metal waste. Some are embedded with bitumen, which is combustible. The drums with bitumen are stored together with the other drums, as they have been inserted chronologically over a longer period of time. The drums have not been fire tested.
DK-E-577 | PFP | DK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Drum storage facility - Risø site |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers? | The risk is considered through the structural design of the Drum Storage facility, which includes thick concrete walls and a lack of flammable materials inside the storage area. Additionally, operational procedures focus on minimizing fire loads and ignition sources. Regular inspections and compliance with legal requirements also contribute to risk assessment and management. Propagation of fire is prevented by the construction of the Drum Storage itself, with thick concrete walls acting as effective fire barriers. Furthermore, the design of the building minimizes the risk of fire spread by limiting potential ignition sources and ensuring adherence to operational procedures. While there is no direct ventilation within the Drum Storage itself, the building is equipped with a ventilation system that serves the entire facility. However, the ventilation system is manually controlled and does not shut off automatically in the event of a fire. Emergency services are responsible for manually shutting off the system if necessary. Management concerning fire compartmentation involves regular inspections and compliance with operational procedures. Fire loads are managed through operational procedures aimed at minimizing flammable materials within the facility. Compartmentation and fire barriers, such as the thick concrete walls in the Drum Storage, help contain fire and limit its spread. The fire rating of barriers ensures that they can withstand fire for a specified period, providing additional time for evacuation and firefighting efforts.
DK-E-578 | PFP | DK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Drum storage facility - Risø site | Section I-3.3.2; P. 41; (3). Does the ventilation system serve more than one fire compartment and are provisions in place to ensure separation between fire compartments? Section I-3.3.2; P. 41; (4). What is the degree of fire resistance of the ventilation system and is it possible to isolate the openings of the fire compartment with properly rated fire dampers (automatically if necessary)? Section I-3.3.2; P. 41; (3). The report states that building air is released to the atmosphere by filtering through primary and absolute filters. What type are these filters and what do they filter? |  | There is no direct ventilation in the Drum Storage itself, but the building is equipped with a ventilation system, where the air from outside is sucked into the building and heated via heating surfaces. The heating takes place to avoid freezing in the storage. From the building itself, the air is exhaustedto the atmosphere, as it is filtered through a pre-filter and an absolute filter.
DK-E-579 | PFP | DK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Drum storage facility - Risø site | page 35 states that the risk of start of a fire inside the now vacated cells is limited, as is the risk of spread of a fire from the surrounding areas to the cell blocks but notes the potentiall exception is the ventilation system, which may act as a conduit for fire spread through the system of air ducts. The report aknowledges the ventilation ducts are not fire protected. Page 41 states ventilation system is manually controlled and does not switch off automatically in the event of a fire. The decision to switch of the system manually rests with the emergency services. Has consideration been given to installing automated shutoff? Is the statement in page 35 consistent with the statement in page 43 that the ventilation is switched off automatically on heat detection? |  | This question is related to the Hot Cell facility and not the Drum Storage. The ventilation system at the Hot Cell facility shuts down automatically at high temperatures, but this does not necessarily indicate a fire, though there may be a strong correlation.
DK-E-580 | PFP | DK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Drum storage facility - Risø site |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made? | Fire dampers are not used in the ventilations system at the Drum storage facility.
DK-E-581 | PFP | DK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Drum storage facility - Risø site | Section 3.1.4.1; P.32; (2). What activities in other parts of the building can increase the risk of fire? What kind of dangerous work is done there? |  | No hazardous work is carried out in other parts of the building. The building solely contain the reception of waste and waste pressing.
DK-E-582 | PFP | DK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Drum storage facility - Risø site |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries). | Fire events is not classified or categorized. All fire related incidents are reported to the nuclear regulatory authorities, including smouldering events. DD has had 2 minor fire-related incidents in the last 10 years. One was in electrical installations in connection with the asphalt plant, which is now decommissioned. The other was in the drum dryer plant (smouldering), which is also now decommissioned. Both incidents triggered fire alarms, and the fire brigade was automatically called, so everything worked as intended.
DK-E-583 | AFP | DK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Hot Cell facility - Risø site |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? | The fire detection system records alarms from the specific fire detector, which gives the fire brigade possibility to precisely locate the fire. Fire detectors are located in all rooms (no exceptions), and often multiple fire detectors are located in larger rooms (cf. II-3.2.1.2). The fire alarm system has UPS battery backup, which is designed to support 24 hours of normal operation and then remain in alarm mode for an additional 30 minutes in the event of 15 simultaneous alarms.
DK-E-584 | AFP | DK | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Hot Cell facility - Risø site |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy. | No assesment of the adverse effcets of using fire water for fire suprression within the Hot Cell facility have been conducted. There is no on-site arrangement for fire suppression, and therefor also no emergency power supply. There is no fixed automatic fire-extinguishing equipment at DD's facilities, but instead there is equipment for manual fire-fighting at all the facilities. DD's technical staff are trained in basic firefighting, which is refreshed every two years. DD's own staff will never try to put out a fire in the Hot Cell facility itself, but always wait for the fire brigade to arrive on the scene.
DK-E-585 | AFP | DK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Hot Cell facility - Risø site |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …) | The external fire brigade is located 10 km away from the nuclear site. The expected response time from alarming until the actual firefighting starts in the field is 10-15 min in all cases (day or night). The Execute Order no. 1085 of 25 October 2019 on Risk-Based Sizing of the Municipal Rescue Service stipulates that the municipal rescue service must be able to provide a preventive, limiting, and remedial effort in relation to local risks. The municipal rescue service must identify and analyse local risks, which must form the basis for sizing the rescue service (risk profile). The municipal council determines the level of the municipal rescue service's task performance (service level) based on the risk profile as well as its organization, operations, alerting, sizing, and equipment based on the risk profile and service level. All fire alarms on the nuclear facilities go directly to external firefighting. In case the off-site fire brigade is called, they will have the lead on the firefighting operation. In accordance with the Danish model for incident command, as outlined by the Danish Emergency Management Agency, this approach adheres to the established principles where the fire incident commander leads the fire-related operations, while the police incident commander assumes overall command at the incident scene
DK-E-586 | AFP | DK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Hot Cell facility - Risø site | /1/ p. 18 "In the analysis it was concluded that closing down the on-site fire department would result in an increased response time from 5 minutes to 10-15 minutes. The analysis further concluded that implementation of all recommended improvements would result in an overall increase in fire safety, primarily due to the increase in passive safety features; enhanced fire sectioning and automated detection and alarm systems. In consequence, it was decided to close the on-site fire department." |  | No question posed. See response to DK-E-585 | DK-E-585
DK-E-587 | AFP | DK | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Hot Cell facility - Risø site |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. | No feedback from testing fire detection and suppression systems was supplied by the operator/licensee
DK-E-588 | AFP | DK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Drum storage facility - Risø site |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? | See response to DK-E-583 The fire detection system records alarms from the specific fire detector, which gives the fire brigade possibility to precisely locate the fire. Fire detectors are located in all rooms (no exceptions), and often multiple fire detectors are located in larger rooms (see II-3.2.1.2). The fire alarm system has UPS battery backup designed to operate for 4 hours at 75% load. | DK-E-583
DK-E-589 | AFP | DK | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Drum storage facility - Risø site |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy. | All fire water will be collected in the area as there are no outlets (bathtubs) and can then be pumped up and distilled. There is no on-site arrangement for fire suppression, and therefor also no emergency power supply. There is no fixed automatic fire-extinguishing equipment at DD's facilities, but instead there is equipment for manual fire-fighting at all the facilities. DD's technical staff are trained in basic firefighting, which is refreshed every two years. DD's own staff will never try to put out a fire in the Drum Storage itself, but always wait for the fire brigade to arrive on the scene.
DK-E-590 | AFP | DK | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Drum storage facility - Risø site | To provide additional information regarding the decision to close the site's fire department,. There is no data on the argumentation of the amount of forces and resources in the municipality fire department. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information. |  | See response to DK-E-585 In the report p. 18 it is stated that: "In the analysis it was concluded that closing down the on-site fire department would result in an increased response time from 5 minutes to 10-15 minutes. The analysis further concluded that implementation of all recommended improvements would result in an overall increase in fire safety, primarily due to the increase in passive safety features; enhanced fire sectioning and automated detection and alarm systems. In consequence, it was decided to close the on-site fire department." | DK-E-585
DK-E-591 | AFP | DK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Drum storage facility - Risø site |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. | See response to DK-E-585 | DK-E-585
DK-E-592 | AFP | DK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Drum storage facility - Risø site | The principle of comparative assessment of the consequences of accidents leading to the release of radioactive materials is not shown. The principle for the comparative assessment performed should be presented [linked to fire safety analysis]. To provide additional information on coordination between conventional and radiological fire safety. |  | Page 20 in the report addresses conventional versus radiological fire safety. On the Interfaces between conventional and radiological fire safety it is stated that: " Some aspects of conventional safety may impact on features relevant for radiological fire safety and reversely. For instance, the need to ventilate smoke and ensure means of escape may conflict with priorities to limit releases of radioactive materials to the surroundings. As the potential range of as-sessed radiological consequences from a fire in the Drum Storage point to significantly smaller conse-quences than the potential life-threatening scenario for a person within or in the immediate sur-roundings of the facility in case of a fire, the conduct of life-saving actions, as deemed necessary by emergency response units, is given priority."
DK-E-593 | AFP | DK | Active fire protection | Licensee and regulatory experience |  | Waste | Drum storage facility - Risø site |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. | No feedback from testing fire detection and suppression systems was supplied by the operator/licensee
ES-E-594 | FSA | ES | Fire safety analysis | Licensee and regulatory experience |  | Fuel fabrication facilities | Juzbado |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Radiological/criticality consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. c) Criticality: How has the criticality aspect been taken into account in the analysis and the impact on the fire protection features. d) How have the radiological hazards (radiological, criticality) been taken into account in the development of the fire brigade procedures (onsite, offsite brigades)? 5. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 6. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 7. Results and revisions of the Fire Safety Analyses, additional analyses: Please provide details about: a) Treatment of modifications and changes in the installations as well as updates of the analysis should be addressed. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for fuel fabrication facilities in your country? 8. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
ES-E-595 | FSA | ES | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Almaraz | What are the requirements regarding the behaviour of fire protection features other than the extinguishing subsytem under seismic conditions? - Does the transition to NFPA 805 lead the licensee to modify preventive maintenance procedures for FPM, the periods of recurrent inspections, the duration of unavailability before repair, etc? If so, how? - As Almaraz is probably one of the very few NPPs with a risk-informed, performance-based approach : What are the strenghts/ weaknesses of the approach from the regulator's point of view? PSA: There is no precise information on the consideration of the compartments boundary failure and propagation between fire compartments (only the exclusion of the risk of fire propagation between buildings is mentioned); fire initiation on the current part of the cables is not mentioned; concerning the support studies for the Fire PSA, the fire simulation code used to model the fire development and propagation is not mentioned Regarding the Human Reliability Assessment (HRA), no specific fire action was identified. At least actions to implement specific fire procedures may be identified. Also, the document does not mention any HRA quantification or the method used (IDHEAS-ECA…).
ES-E-596 | FSA | ES | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Almaraz | () The conclusions are the same for all three NPPs. Are there no differencies?
ES-E-597 | FSA | ES | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Cofrentes | The fact that the seismic FP system capability exceeds the requirements of IS-30 is it resulting from specific fire scenario? If so, can you please provide information on the scenario?
ES-E-598 | FSA | ES | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Cofrentes | The conclusions are the same for all three NPPs. Are there no differencies?
ES-E-599 | FSA | ES | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Vandellos 2 | What are the requirements regarding the behaviour of fire protection features other than the extinguishing subsytem under seismic conditions?
ES-E-600 | FSA | ES | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Vandellos 2 |  | p99 : Clarification for Passive fire protection : Almaraz and Cofrentes use the term "3h fire resistance barriers" or "3h fire rated barriers" meanwhile Vandellos use "R180". Are insulation and hot gases tightness taken into account for fire resistance of fire areas in all spanish NPP'S?
ES-E-601 | FSA | ES | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Vandellos 2 | The conclusions are the same for all three NPPs. Are there no differencies?
ES-E-602 | FSA | ES | Fire safety analysis | Licensee and regulatory experience |  | NPP | Almaraz | P. 67, 2.1.6.1.1 refers to sections 02.1.8.1.2 and 02.1.5.4, which do not exist. What should be the correct sub-sections? (1/)
ES-E-603 | FSA | ES | Fire safety analysis | Licensee and regulatory experience |  | NPP | Almaraz |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
ES-E-604 | FSA | ES | Fire safety analysis | Licensee and regulatory experience |  | NPP | Cofrentes |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
ES-E-605 | FSA | ES | Fire safety analysis | Licensee and regulatory experience |  | NPP | Vandellos 2 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
ES-E-606 | PFP | ES | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Juzbado | , p.124, §03.1.2.1, topic 2/ : a clear list of applied preventions means is missing. Please provide information on the above.
ES-E-607 | PFP | ES | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Juzbado |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
ES-E-608 | PFP | ES | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | Juzbado |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
ES-E-609 | PFP | ES | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Juzbado | , p.220 §03.3.2.2.2: Please clarify how the decision to keep ventilation in service or not takes into account the need for a filtered release (or not)?
ES-E-610 | PFP | ES | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Juzbado | There is reference to an annual inspection of fire dampers but the type of tests undertaken is not provided. Please describe the type of tests undertaken - see page 223. There is reference to the change of ventilation system dampers/ replacement. Please provide the main considerations for the replacements and implications regarding inspection/ testing?
ES-E-611 | PFP | ES | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Juzbado |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
ES-E-612 | PFP | ES | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Fuel fabrication facilities | Juzbado |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
ES-E-613 | PFP | ES | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Almaraz | The NAR provides description of combustable and flammable material management including design features relating to diesel storage and use. Are there Oil/diesel mists/ spray prevention features considered e.g. use of flange guards? The report makes reference to the use of acetylene, which is a highly reactive fluid - have safer replacements been considered? The reviewer could not find reference to fire prevention considerations in the training provided. Is this considered, and if so, please describe the main considerations?
ES-E-614 | PFP | ES | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Almaraz |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
ES-E-615 | PFP | ES | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Cofrentes | Is there oil leakage collection for RCPs? (page 97-98) Compressed gas cylinders in buildings with SSCs - has relocation to outdoor locations been considered? Apparent inconsistency with other NPPS (Vandellos - page 96-97) page 98 - How is hydrogen stored in relation to the plant layout? Noted that is stored outdoors and indoors? has removal of hydrogen storage from inside turbine building been considered? page 106 - diesel day tank retaining basin - what is the capacity? does it provide for the whole volume of the tank?
ES-E-616 | PFP | ES | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Cofrentes |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
ES-E-617 | PFP | ES | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Vandellos 2 | The NAR provides description of combustable and flammable material management including design features relating to diesel storage and use. Are there Oil/diesel mists/ spray prevention features considered e.g. use of flange guards? The report makes reference to the use of acetylene, which is a highly reactive fluid - have safer replacements been considered?
ES-E-618 | PFP | ES | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Vandellos 2 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
ES-E-619 | PFP | ES | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Almaraz | page 122 - Regarding the statement 'An analysis of the regulations on FP Passive Protections was carried out. This document was technically certified by an independent laboratory. Although a generic solution has not yet been adopted, certain scenarios for its use have been adopted.' what was the scope of the document and the main findings? page 97 - It states that the DG cubicles act as retention cubicles - do they have capacity for the tank inventories? How fire resistance of walls for transformer areas compare with Vandellos NPP (15m or R180)? the/ fire rating was not provided.
ES-E-620 | PFP | ES | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Almaraz |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
ES-E-621 | PFP | ES | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Cofrentes | Please describe the location and justification for the exception of six gates as R90 (instead of R180) - page 201 R180 barriers separating fire areas (diesel day tanks only mentioned) - Please provide information about diesel storage arrangements/ tanks and segregation arrangements? How fire resistance of walls for transformer areas compare with Vandellos NPP?/ fire rating not provided;
ES-E-622 | PFP | ES | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Cofrentes |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
ES-E-623 | PFP | ES | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Vandellos 2 | page 98: the arrangement of the hydrogen cylinder bank KH-T04A/B/C/D (located next to the west façade of the Control building) - scope of PSR is to modify layout/ have a physical barrier - Why has there been no relocation away from control building? R180 barriers separating fire areas (but only the oil diesel day tanks are mentioned) see page 106 - please describe the diesel storage arrangements (e.g. other tanks) and segregation arrangements for those page 102 - control room fire barriers fire rating not described (provided for Almaraz and Cofrentes -3hrs) . Please provide what is described before. Fire containment and fire rating of barriers and rating of penetrations is it based on full compartment fire? page 200
ES-E-624 | PFP | ES | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Vandellos 2 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
ES-E-625 | PFP | ES | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Almaraz |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
ES-E-626 | PFP | ES | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Cofrentes |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
ES-E-627 | PFP | ES | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Vandellos 2 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
ES-E-628 | PFP | ES | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Almaraz |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
ES-E-629 | PFP | ES | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Cofrentes |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
ES-E-630 | PFP | ES | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Vandellos 2 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
ES-E-631 | AFP | ES | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Almaraz |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
ES-E-632 | AFP | ES | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Almaraz | Page 129-132 Section 3.2.1.1.1 Topics 1, 2 The NAR does not detail the emergency power provisions, level of system resilience, hazard tolerance and fire rating of cables. Please could clarification be provided on these issues?
ES-E-633 | AFP | ES | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Cofrentes |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
ES-E-634 | AFP | ES | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Cofrentes | Page 130-135 Section 3.2.1.1.1 Topic 2 - detail not provided of level of system resilience, hazard tolerance and fire rating of cables. Please could clarification be provided on these issues?
ES-E-635 | AFP | ES | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Cofrentes | p137: "The displays identify the fire zone to which the alarm belongs" : Please describe if the system is addressable or not
ES-E-636 | AFP | ES | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Vandellos 2 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
ES-E-637 | AFP | ES | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Almaraz |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
ES-E-638 | AFP | ES | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Almaraz | Page 135-152 Section 3.2.1.2 Topic 4 - does not discuss provisions for retention of fire fighting water (to prevent any spread of contamination).
ES-E-639 | AFP | ES | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Almaraz | p144 : all three NPP have different design arrangements on water supply pumps. Why? Is there a standard in Spain ? Some seems low regarding necessity of redundancy and in comparison with other countries.
ES-E-640 | AFP | ES | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Cofrentes |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
ES-E-641 | AFP | ES | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Cofrentes | p 144 : all three NPP have his own design on water supply pumps. Is there a standard in Spain ? Some seems low regarding necessity of redundancy and in comparison with other countries.
ES-E-642 | AFP | ES | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Cofrentes | p 137 : "Each area with safety important SSCs is equipped with local fire detection" : why not all rooms ? Need of precision.
ES-E-643 | AFP | ES | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Vandellos 2 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
ES-E-644 | AFP | ES | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Vandellos 2 | p 144 : all three NPP have his own design on water supply pumps. Is there a standard in Spain ? Some seems low regarding necessity of redundancy and in comparison with other countries.
ES-E-645 | AFP | ES | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Almaraz |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
ES-E-646 | AFP | ES | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Cofrentes |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
ES-E-647 | AFP | ES | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Cofrentes | p 165: "The configuration of the fire brigade is as follows": This is not clear for this NPP if the on-site fire brigade is professionnal or not. Please provide the relevant information.
ES-E-648 | AFP | ES | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Vandellos 2 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
ES-E-649 | AFP | ES | Active fire protection | Licensee and regulatory experience |  | NPP | Almaraz |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
ES-E-650 | AFP | ES | Active fire protection | Licensee and regulatory experience |  | NPP | Cofrentes |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
ES-E-651 | AFP | ES | Active fire protection | Licensee and regulatory experience |  | NPP | Vandellos 2 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
FI-E-652 | FSA | FI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Olkiluoto 1, 2 | 1 - Can you please provide information on the Fire Hazard Analysis (objectives, scope, assumptions or results)? The discussion seems to refer to the Fire PSA only. [page 25][Sections B 2.1.1 through B 2.1.4] [Assumptions 0/1/2/3] 2 - What is the relative contribution of fire events to the overall PSA core damage frerquency? [page 25][Section B 2.1.4][Assumption 5/]
FI-E-653 | FSA | FI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Olkiluoto 1, 2 | Use of same PRA model for twin units, justification? Are all SSCs really the same?
FI-E-654 | FSA | FI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Olkiluoto 3 | p22 Why DiD levels are different from those of the STUK Guide YVLB,8 ?
FI-E-655 | FSA | FI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Olkiluoto 3 | Section C.2.1.2 states "To show the consistency between deterministic and probabilistic analyses, an interface analysis was performed with a focus on strange cables". Could you please clarify the contents and assumptions of this interface analysis? [page 28][Section C 2.1.2][Assumption 2/]
FI-E-656 | FSA | FI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Olkiluoto 3 | No specific method is mentioned. For OL1/Ol2 there is mentioned use of 6850 Has the 6850 or similar been used also for Ol3? The report says that the contribution of initiating event categories shows IH Fire as the largest contributor to the overall CDF (38%) and is dominated by fire in Reactor Building (remaining areas) – 5%. IH Fire is a major contributor to CDF during power states (51 %) but not during the shutdown states (~1 %) because the frequencies of Fire events are very low.
FI-E-657 | FSA | FI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Lovisa | p23 PRA The NAR contains few information on FHA and fire compartmentation. P25 Fixed extinguishing systems are very important to reduce fire risk. Is there a fire brigade?
FI-E-658 | FSA | FI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Lovisa | As a result of fire risk analysis it is identified that most of the risk consists of fire situations in the control building and the turbine building. Was the fire in the control building analysed in view of ensuring nuclear safety of NPP, and ensuring the work condition of operational personal ? 3/
FI-E-659 | FSA | FI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Lovisa | 2.1.3, p23 MCR is not mentionedin the scope, is it included? PH No specific method is mentioned. Has the NUREG/CR-6850 or similar been used?
FI-E-660 | FSA | FI | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Olkiluoto 1, 2 | 1 - PSRs are not mentioned. Is the FHA updated/reviewed during PSRs? What were the results in the past PSRs? [page 26][Section B 2.1.5.1][Topic 1/]
FI-E-661 | FSA | FI | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Olkiluoto 3 | p30 : There have been minor modifications which have had an impact to the analyses. Which ones are these?
FI-E-662 | FSA | FI | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Lovisa | P.24 NAR mentioned about regular renewal of fire equipment (every 4 years). Please describe in detail what type of equipment is updated every 4 years, is it like maintenance actions or comprehensive improvements based on the current state of development?
FI-E-663 | FSA | FI | Fire safety analysis | Licensee and regulatory experience |  | NPP | Olkiluoto 1, 2 | Apart from the not full separation of safety divisions AC and BD, what other deviations from YVL B.8 have been identified by STUK? [page 26] [B 2.1.6.1] [Topic 2/]
FI-E-664 | FSA | FI | Fire safety analysis | Licensee and regulatory experience |  | NPP | Olkiluoto 1, 2 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FI-E-665 | FSA | FI | Fire safety analysis | Licensee and regulatory experience |  | NPP | Olkiluoto 3 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FI-E-666 | FSA | FI | Fire safety analysis | Licensee and regulatory experience |  | NPP | Lovisa |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FI-E-667 | FSA | FI | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | Olkiluoto KPA |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire safety analyses with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Inventory make-up: Please provide a higher level of detail on the systems used to make-up inventory. 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 5. Additional analyses: Please provide details about: a) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for spent fuel storage facilities in your country? b) Some countries mention that a periodic safety review is performed for spent fuel storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 6. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FI-E-668 | PFP | FI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Olkiluoto 1, 2 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FI-E-669 | PFP | FI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Olkiluoto 3 | Design seems to credit FRNC cable concept however section C3.1.4.2. indicates that STUK has contracted VTT to do fire tests and analysis to verify. Does the dutyholder provide evidence of substantiation / what is the dutyholder design evidence based on if not testing that the regulator performs it? cabling has been mainly done with FRNC-cables (page 43) - is credit given to fire retardancy i.e. are fire loads excluded from consideration in the design of passive fire protection/barriers?
FI-E-670 | PFP | FI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Olkiluoto 3 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FI-E-671 | PFP | FI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Lovisa | page 37 - Human factors are seen as a major contributor to possible ignition events, especially during maintenance outages. There have been three incidents at the plant in the last 10 years that have been classified as fires. None of the fires posed a risk to plant safety systems or caused plant shutdown. There is reference to large amounts of combustibles been found in an outage at LO1 in 2012 - what were the events and causes?
FI-E-672 | PFP | FI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Lovisa |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FI-E-673 | PFP | FI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Olkiluoto 1, 2 | Two weaknesses seem to be identified (page 40 and 42) in that it recognises that the plants do not meet current regulations regarding passive fire protection and that the fire loading is high in some areas, respectively. The report does not highlight whether attempts to reduce inventories or additional measures for fire prevention/ mitigation as a result. Please describe the attemps made to resolve the above. Does the fire compartmentation consider full compartment burnout regardless of the type of cable (all combustible involved in the fire)? page 89 - Divisions AC and BD separation by distance - The plant safety systems are separated as pairs of redundant divisions AC and BD. The separation is done with fire resistant construction materials. Inside these compartments the safety systems of the two divisions are separated by distance, by protective structures, or for example by placing the equipment in different cabinets; how hazard combinations are considered in this context, any consideration of partial barriers and enhanced active fire protection? page 93 - WANO's peer review in 2020, -opening fire penetrations. A procedure published doors/hatches in between divisions is not monitored in a systematic way. This weakness was improved identifying the doors/hatches in between divisions and defining the closed position check measures. Finnish regulatory guide YVL B.8 dictates that all fire-doors and hatches at NPPs shall be self-closing and self-bolting (page 90) - are there local or remote position alarms for fire doors through divisional barriers? page 93 - Aging fire doors and penetrations have been evaluated and renewals have been planned and completed based on the evaluations. Which issues were found during the maintenance of fire dampers? page 93 - consideration of fire doors and hatches and role in managing risks of flooding. Report acknowledges that they do not currently meet industry standards - What is the link to safety assessment? Are multihazard claims on doors/ barriers/ penetrations generally derived? What extent of review of safety assessment is undertaken in this context?
FI-E-674 | PFP | FI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Olkiluoto 1, 2 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FI-E-675 | PFP | FI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Olkiluoto 3 | page 97 - doors/hatches in between divisions was not monitored in a systematic way. This weakness was improved identifying the doors/hatches in between divisions and defining the closed position check measures. For doors, are there position alarms (to a permanently occupied location, or local audible alarms)? Also, are there lobbied configurations implemented for defence in depth (through cross- divisional doors)?
FI-E-676 | PFP | FI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Olkiluoto 3 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FI-E-677 | PFP | FI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Lovisa | In relation to the shortcomings in functional plant layout as acknowledged in page 25 and also page 89 - the plant has unprotected steel structures which increase the risk of collapse in case of fire, it states that many improvements have been done to mitigate these deficiencies. Please describe the extent to which hazard analysis has been performed and the level to which engineering judgement is relied upon vs hazard loading/ characterisation. Current requirements regarding the structural separation of control room and emergency control room are not fulfilled (page 89) - Please describe how this is/will be addressed? page 87 - Renewal of fire doors phase one (2018-2022) have be finalized and the next phase is in planning phase. The extent of the activities of these improvements should be discussed/ confirmed. Apart from locking or removal of fire doors/ are there any other improvements considered - e.g. position alarms? Consideration of passive fire protection in the context of operating/ aging facilities in areas where there was not full segregation between divisions by design e.g. turbine buildings in Lovisa 1/2. How were combined hazards taken into account? For example, a turbine disintegration event leading to fire and how does this related to the location and/or protection of the additional DHR (introduced outside the Turbine building)?
FI-E-678 | PFP | FI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Lovisa |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FI-E-679 | PFP | FI | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Olkiluoto 1, 2 | page 89 - The fire zones have separate ventilation systems (except ventilation outlet pipe) How is fire protection in this area considered?
FI-E-680 | PFP | FI | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Olkiluoto 1, 2 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FI-E-681 | PFP | FI | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Olkiluoto 3 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FI-E-682 | PFP | FI | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Lovisa |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FI-E-683 | PFP | FI | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Olkiluoto 1, 2 | page 44 The oversight of a new build has been great opportunity for STUK to improve its competencies on inspections of fire protection arrangements. What key learning has STUK gathered from the activity?
FI-E-684 | PFP | FI | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Olkiluoto 1, 2 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FI-E-685 | PFP | FI | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Olkiluoto 3 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FI-E-686 | PFP | FI | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Lovisa |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FI-E-687 | PFP | FI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | Olkiluoto KPA | Some topics, for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: • (b)"3.1.1 Design considerations and prevention means" (and related subparagraphs) • (b)"3.1.2 Overview of arrangements for management and control of fire load and ignition sources" (and related subparagraphs) • (b)"3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) • (b)"3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) Please provide the missing information from the above.
FI-E-688 | PFP | FI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | Olkiluoto KPA | The fire prevention arrangements are referenced in B 3.1.2. Overview of arrangements for management and control of fire load and ignition sources (ref. 32) but there is limited information on the approach of this reference for the control of the fire load, for example, whether it is quantitative or qualitative . There are no ISFS specific considerations in the section or lessons learned specific to ISFS in relation to fire prevention page 44. Please provide additional and missing information related to the above. / (b) Please describe the approach for fire load quantification and whether control is managed in a quantitative of qualitative way
FI-E-689 | PFP | FI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | Olkiluoto KPA |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FI-E-690 | PFP | FI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | Olkiluoto KPA |  | [generic]: o Compartmentation (as applicable): How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FI-E-691 | PFP | FI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | Olkiluoto KPA | page 99 (pdf) states Load bearing structures have fire resistance rating of R 60, except in the expansion of the storage hall where the design of steel beams has been done using performance-based fire safety design. How does the fire resistance specification relate to the hazard characterisation/ analysis? What fire resitance do the storage hall columns have and how are they protected against fire?
FI-E-692 | PFP | FI | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | Olkiluoto KPA |  | [generic] o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FI-E-693 | PFP | FI | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | Olkiluoto KPA | Passive fire protection - page 99 (pdf) indicates 2 divisions and fire compartmentation. Compartmentation in the context of ventilation systems D3.3.2 0 states that the "duct networks is planned in a way that the ducts servicing areas of different redundancies are separated as far as possible" but it is not clear if they are fully segregated or there are areas where there are exceptions to segregation. Later the report confirms that for cables, switchgear, instruments and devices are in different compartments, it is not clear if ducts always are. Please clarify if there are there exceptions to segregation regarding ventilation ducts across divisional compartments? Examples?
FI-E-694 | PFP | FI | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Olkiluoto KPA |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FI-E-695 | PFP | FI | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Olkiluoto KPA | page 100 of the pdf file - D 3.3.3.1 Overview of strengths and weaknesses states that "The original fire protection concept/philosophy has mainly been found to be good, even though it does not meet the current regulations regarding passive fire protection in all respects" Please clarify regulatory requirements, the shortfalls identified and the improvement actions this refers to?
FI-E-696 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Olkiluoto 1, 2 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
FI-E-697 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Olkiluoto 1, 2 | Page 59-60 Section B.3.2.1 Topic 1 - No mention of Nuclear Safety Class of fire detection and alarm system or standards against which the system was designed. Please could clarification be provided on these points?
FI-E-698 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Olkiluoto 1, 2 | Page 59-60 Section B.3.2.1 Topic 2 - No detail of the system network arrangements, resilience or hazard tolerance. No detail of cable or enclosure fire rating or EMIT arrangements for the fire detection and alarm system. Please could clarification be provided on these points?
FI-E-699 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Olkiluoto 1, 2 | Section 3.2 p. 59 The information on connecting the video surveillance system to the fire alarm system is missing. Please provide it. It stays unclear if it possible to control video monitoring from the fire alarm panel. Please clarify this issue.
FI-E-700 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Olkiluoto 3 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
FI-E-701 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Olkiluoto 3 | Page 73 of pdf, section C.3.2.1.2, assumption 1. "Protected rescue routes are over-pressured with a signal from fire alarm system. In NI the fans are started automatically, but in TI it’s done manually. Their air intake and smoke extraction dampers are opened automatically. The position of the dampers is visible in the terminal of the Info-System in the MCR". Please, describe more in depth this part of the system. Which rescue or escape routes are over-pressured in case of fire? How are the signals transmitted and analyzed from the fire detectors to fans and dampers? Is the manual start of fans included in procedures? - Page 74 of pdf, section C.3.2.1.3, assumption 1. "In case of an evacuation of the MCR the standby operating panel in the RSS will be activated and takes over the full function of the Fire Alarm System of OL3." Please, describe the main features and components of the panel in the RSS that takes over the function of the fire alarm system. Is it necessary to take some actions from the MCR before its evacuation? Is there electrical independence between MCR and RSS (to avoid transmission of electrical failures in case of fire)?
FI-E-702 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Olkiluoto 3 | /1/ p. 72: "The tasks of the Fire Alarm System are: ... • Power supply of fire damper (230 V AC)," -> should it be "actuation" (this is already mentioned in another bullet point)?
FI-E-703 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Lovisa |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
FI-E-704 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Lovisa | Page 45 of pdf, section A.3.2.1.1, assumption 4. Explain the procedures established for the examination, inspection, maintenance and testing of fire detection and alarm features. - Page 46 of pdf, section A.3.2.1.2, assumption 1. There is no information about modern detection (air sampling systems or similar). Is this type of technology installed in the plant? - Page 46 of pdf, section A.3.2.1.2, assumption 1. "The system also includes gas detectors in emergency diesel building, which alarms if there are flammable gas leaks from fuel tanks". Please, explain the main features, design standards and other general information regarding this type of detectors.
FI-E-705 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Lovisa | /4/ p.45, A 3.2.1.3., How is it ensured that all disabled detectors are listed completly? How is t ensured that all ambient hazards (e.g. dust inducing) are known by the fire lieutenant? What is the communination path/ information exchange between fire lieutenant and work supervisor to be sure e.g. hot work is finished?
FI-E-706 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Lovisa | p.46, Why are the surveillance rounds triggered by fault or disability of half of the detectors? It should be claryfied where these 50% come from.
FI-E-707 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Olkiluoto 1, 2 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FI-E-708 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Olkiluoto 1, 2 | Page 60-64 Section B.3.2.2 Topic 1 - No mention of Nuclear Safety Class of fire suppression systems or standards against which the systems were designed. No mention of accessibility considerations for manual fire fighting. No detail provided for how the capacity requirements for the suppression systems were determined. Please could clarification be provide on these points?
FI-E-709 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Olkiluoto 1, 2 | Review of the seismic resistance issue of fire extinguishing systems.
FI-E-710 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Olkiluoto 1, 2 | Page 60-64 Section B.3.2.2 Topic 4 - No discussion of retention of fire fighting water or potential for radiological discharge with spread of fire water. Please could clarification be provide on these points?
FI-E-711 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Olkiluoto 1, 2 | What is the reason of replacing sprinkler by CO2 in the EDR ?
FI-E-712 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Olkiluoto 3 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FI-E-713 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Olkiluoto 3 | Page 75 of pdf, section C.3.2.2.2, assumption 2. Fire water pump stations and the fire protection water supply system are not described. Please describe electrical pumps and diesel-driven pumps; including flow and pressure, electrical supply, seismic category, separation between them and other relevant features. Also describe water tanks or other sources of supply; including their inventory, connections and other relevant features.
FI-E-714 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Lovisa |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FI-E-715 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Lovisa | Page 48 of pdf, section A.3.2.2.2, assumption 1. Are there fixed suppression systems based on foam? - Page 49 of pdf, section A.3.2.2.2, assumption 1. The use of standpipe hoses inside the main buildings is not described. Please, describe the type of hoses, lengths, separation between them and other features. Are all SSC important to safety covered by the jet from at least one hose? - Page 49 of pdf, section A.3.2.2.3, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain. - Page 49 of pdf, section A.3.2.2.3, assumption 2. "The fire suppression systems are not qualified against seismic events". In the event of a safe shutdown earthquake (SSE), is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown or any similar provision? How does the fire brigade suppress fires in the event of a SSE? Are there other fire extinguishing provisions qualified against seismic events? - Page 50 of pdf, section A.3.2.2.4, assumption 3. "For turbine generator water spray extinguishing system, when one subsystem is out of use, operational readiness shall be prepared for the covered area" (also in other cases). What are the features of the "operational readiness"? Which are the differences compared to a normal situation?
FI-E-716 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Lovisa | Consideration of the seismic resistance issue of fire extinguishing systems.
FI-E-717 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Lovisa | p.48, A 3.2.2.3., If fire supression system is not qualyfied for seismic event but in case of, seismic walkdowns are foreseen, are there any detailed plans (specific procedures) lists, main points of interest, etc. foreseen to be checked?
FI-E-718 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | Page 136 Section A-I.3.2.2.1 Topic - explains that any worker may use the appropriate hand-held fire fighting means but does not explain the extent of training provided to the general workforce to enable such intervention.
FI-E-719 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | Page 137 of pdf, section A-I-3.2.2.2, assumption 1. The types of fixed extinguishing system is stated very briefly. Please, describe the key features and technology of the different types of systems (spray, sprinkler, CO2, FM 200, NOVEC, foam or other types). - Page 137 of pdf, section A-I-3.2.2.2, assumption 2. Can the pumps in the fire-fighting water production system resist the Safe Shutdown Earthquake (SSE)? - Page 138 of pdf, section A-I-3.2.2.2, assumption 2. Explain if the fire ring include a double supply to buildings containing safety related SSC’s; and if this ring have isolation valves, the aim being to be able to isolate part of the main ring for maintenance or repair.
FI-E-720 | AFP | FI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Olkiluoto 1, 2 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
FI-E-721 | AFP | FI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Olkiluoto 3 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
FI-E-722 | AFP | FI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Olkiluoto 3 | Page 67 of pdf, section B.3.2.3.1, assumption 1. Drills are not described. Please explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade, content and main lessons learnt.
FI-E-723 | AFP | FI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Olkiluoto 3 | Section 3.2 p. 80 Administrative communication system (TETRA) is absent at the enterprise. Please provide information on alternative communication system (implementation of radio stations at the site).
FI-E-724 | AFP | FI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Lovisa |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
FI-E-725 | AFP | FI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Lovisa | Page 51 of pdf, section A.3.2.3.1, assumption 1. "The fire brigade has to be able to reach all facilities at plant within six (6) minutes from the alarm". Please, give evidence of the time of arrival from real events and drills. - Page 54 of pdf, section A.3.2.3.2, assumption 1. Drills are not described. Please explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade, content and main lessons learnt.
FI-E-726 | AFP | FI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Lovisa | Section 3.2 p. 80 Administrative communication system (TETRA) is absent at the enterprise. Please provide information on alternative communication system (implementation of radio stations at the site).
FI-E-727 | AFP | FI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Lovisa | /2/ A 3.2.3.1, p. 52, Is there a ranking for the possible involved persons or how is the coordination among each other to order the on-site fire brigade?
FI-E-728 | AFP | FI | Active fire protection | Licensee and regulatory experience |  | NPP | Olkiluoto 1, 2 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
FI-E-729 | AFP | FI | Active fire protection | Licensee and regulatory experience |  | NPP | Olkiluoto 3 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
FI-E-730 | AFP | FI | Active fire protection | Licensee and regulatory experience |  | NPP | Lovisa |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
FI-E-731 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | Olkiluoto KPA |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
FI-E-732 | AFP | FI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | Olkiluoto KPA | Par.1.1.1 pag. 10 - The facility was expanded in 2015 so that it can fill the need for increasing spent fuel amount. --> Considering this expansion, clarify whether existing facilities were expanded (integrated) or replaced, also in relation to the integration of technologies, existing versus state-of-the-art (new).
FI-E-733 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | Olkiluoto KPA |  | P.82 Adverse consequence of sprinklerwater (from fixed automatic fire extinguishing systems) [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FI-E-734 | AFP | FI | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | Olkiluoto KPA | (p.82) the NAR mentions rooms of the ISFS that are protected with fixed automatic fire extinguishing systems consisting of water sprinklers. The NAR does not mention possible adverse consequence of water sprinkler. Clarify this, including possible effect on sub-criticality of in the spent fuel pool, if any.
FI-E-735 | AFP | FI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | Olkiluoto KPA |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
FI-E-736 | AFP | FI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | Olkiluoto KPA | Please specify whether an inspection programme is planned and its frequency.
FI-E-737 | AFP | FI | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Olkiluoto KPA |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
FR-E-738 | FSA | FR | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Osiris RR |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FR-E-739 | FSA | FR | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Saint Laurent UNGG |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FR-E-740 | FSA | FR | Fire safety analysis | Assumptions (TS 02.3) |  | Fuel fabrication facilities | MELOX | p.63 ,IV-2.3.1: what is meant by 'a prudent deterministic approach' ? p.68: IV-2.3.4: Why are there different criteria for exposure of the public (accident situation not more than 1 mSv versus DBA in case of fire room with significant quantities of MOX power should not lead to more than 10 mSv). Also, it is not clear what are the dose results and if additional measures had to be taken to comply with the limit values.
FR-E-741 | FSA | FR | Fire safety analysis | Assumptions (TS 02.3) |  | Fuel fabrication facilities | Romans inc CERCA | p. 53: Could you provide more details on FHA, where are the highest risks in terms of plant design and why? What are the reference scnarios?
FR-E-742 | FSA | FR | Fire safety analysis | PSR and modifications |  | Fuel fabrication facilities | MELOX | p. 69: Are there ongoing or intended modifications/changes?
FR-E-743 | FSA | FR | Fire safety analysis | PSR and modifications |  | Fuel fabrication facilities | Romans inc CERCA | p.55: Can you elaborate further on the significant updates, carried out between 2018 and 2019, for the buildings containing uranium bearing materials? What have been the significant results from the prior and the current PSR?
FR-E-744 | FSA | FR | Fire safety analysis | Licensee and regulatory experience |  | Fuel fabrication facilities | MELOX |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Radiological/criticality consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. c) Criticality: How has the criticality aspect been taken into account in the analysis and the impact on the fire protection features. d) How have the radiological hazards (radiological, criticality) been taken into account in the development of the fire brigade procedures (onsite, offsite brigades)? 5. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 6. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 7. Results and revisions of the Fire Safety Analyses, additional analyses: Please provide details about: a) Treatment of modifications and changes in the installations as well as updates of the analysis should be addressed. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for fuel fabrication facilities in your country? 8. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FR-E-745 | FSA | FR | Fire safety analysis | Licensee and regulatory experience |  | Fuel fabrication facilities | Romans inc CERCA |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Radiological/criticality consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. c) Criticality: How has the criticality aspect been taken into account in the analysis and the impact on the fire protection features. d) How have the radiological hazards (radiological, criticality) been taken into account in the development of the fire brigade procedures (onsite, offsite brigades)? 5. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 6. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 7. Results and revisions of the Fire Safety Analyses, additional analyses: Please provide details about: a) Treatment of modifications and changes in the installations as well as updates of the analysis should be addressed. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for fuel fabrication facilities in your country? 8. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FR-E-746 | FSA | FR | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | Could you please clarify what is meant by the use of "aggravating factors" and how it is related to the WENRA SRLs? [page 26][Section I - 2.1.2][Assumption 3/]
FR-E-747 | FSA | FR | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | P. 29: For RP N4 the CDF from fires is 1E-05 (p. 36), while for the 900 MW series (Tricastin 1) it is 1E-06 (p. 29) - what is the main reason? (5/)
FR-E-748 | FSA | FR | Fire safety analysis | Licensee and regulatory experience |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FR-E-749 | FSA | FR | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | RHF | To 1/ (pp. 39-45): Can you please give information on the scope of the analyses, in particular if covering also shutdown states during outages?
FR-E-750 | FSA | FR | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | RHF | To 1/ (pp. 39-45): b) Can you please provide on the licensee´s experience with weaknesses from the PSR regarding fire safety?
FR-E-751 | FSA | FR | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | RHF |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FR-E-752 | FSA | FR | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | La Hague | Apart from the licensee´s review of plant configuration (every ten years), is there any other mechanism to ensure that plant configuration is maintained compatible with fire safety analysis at all times?
FR-E-753 | FSA | FR | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | La Hague | Abbreviations are not always clarified (e.g. "DAI") and a list of abbreviations is missing from the report.
FR-E-754 | FSA | FR | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | La Hague |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire safety analyses with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Inventory make-up: Please provide a higher level of detail on the systems used to make-up inventory. 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 5. Additional analyses: Please provide details about: a) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for spent fuel storage facilities in your country? b) Some countries mention that a periodic safety review is performed for spent fuel storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 6. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FR-E-755 | FSA | FR | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | La Hague Silo 130 | /1/ p. 77: Can you provide a clarification of the underlying fire hazard on which basis all the adopted prevention and protection measures to be adopted are identified?
FR-E-756 | FSA | FR | Fire safety analysis | Licensee and regulatory experience |  | Waste | La Hague Silo 130 |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
FR-E-757 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Osiris RR | 3.1.1 Even if the distribution of the fire load is well descripted; Please provide information about how fire loads are managed.
FR-E-758 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Osiris RR | * Page 14, point 1.1.3.9. Please descibe the intended end state of decommissioning. *Page 126. Section F-I-3.1.2. Overview of arrangements for management and control of fire load and ignition sources. Assumption 3/. REGARDING FIRE LOADS "The fire loads are limited to the strict minimum necessary for operation. They are subject to a geographical assessment to define, with margins, a maximum authorised fire load in operation, substantiated by the fire risks management case. A periodic check of the fire loads is therefore carried out to make sure that the authorised values are not exceeded for the different areas of the facility (annually for sensitive rooms and every three years for all the rooms)." Are the (fix and temporary) storage areas registered and clearly identified? Storage areas are approved by permits? Are there proccedures to control and minimise the amount of combustible materials and ignition sources? What type of procedures are in place to manage fire loads? Are ignition sources identified and checked to determine possible fire precursors? Are there proccedures to avoid the storage of combustible materials near to ignitions sources (like electrical equipment)? (The questions above mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) *Page 127. Section F-I-3.1.2. Overview of arrangements for management and control of fire load and ignition sources. Assumption 3/. "Concerning the risk of H2 production at the fork-lift truck loading stations, and the battery rooms, measures are taken to avoid the creation of an inflammable atmosphere (ventilation, recharging conditions, etc.)." What kind of measures? REGARDING HOT WORKS. *Page 127. Section Overview of arrangements for management and control of fire load and ignition sources; Ignition sources; Thermal sources (heating, hot work, heat engines). Assumption 3/. "The performance of hot work in rooms where this is not provided for in the safety baseline requirements is authorised subject to a hot work permit application." Is the performance of hot work in rooms where this is provided for in the safety baseline requirements, regulated by the issuance of permits ?. If not, what procedures regulate hot works in these areas? Is the impact on fire protection systems analyzed before to permit hot works? Is it proven that the person in charge of carrying out the hot work has adequate training and knows the risks and fire prevention measures that must be applied before starting the work? Is it taken into account whether there are necessary security systems near the work area and are necessary measures taken to protect said systems? How is the performance of hot work in ATEX areas managed? (The questions above mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) *Page 128. Section Section Overview of arrangements for management and control of fire load and ignition sources; Ignition sources; Thermal sources (heating, hot work, heat engines). Assumption 3/. Assumption "The entry of heat engine trucks into the OSIRIS pile hall or the ISIS pile hall is limited as much as possible. If a truck does have to enter a hall, the following measures are taken:...." Is the possible activation of smoke detection systems (and associated extinction) taken into account as a result of the smoke generated by the truck? (if these systems exist)
FR-E-759 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Osiris RR |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FR-E-760 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Saint Laurent UNGG | 3.1.1. Respecting all the level of defence in depth, the design of the decommissioning worksite is not deeply described. Please provide more information about the above.
FR-E-761 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Saint Laurent UNGG | *Page 131. Section F-II-3.1.2. Overview of arrangements for management and control of fire load and ignition sources. Assumption 3/. REGARDING FIRE LOADS "For each temporary storage request, the organisation in place provides for an estimation of the fire load of the zone, a risk analysis according to zone's risk level and defining of the corresponding countermeasures, various inspections and the responsibilities associated with the zone". Are there permanent storages?In that case, are they regulated by permits and are they checked as with temporary storage? Are the (fix and temporary) storage areas registered and clearly identified? Is it taken into account that the location of the storage is far from ignition sources? REGARDING HOT WORKS What is the process by which hot works are approved? Are permits issued? Are the fire risks and radiactive contamination spread analyzed? Is the impact on fire protection systems analyzed? (If applicable) Is it proven that the person in charge of carrying out the hot work has adequate training and knows the risks and fire prevention measures that must be applied before starting the work? How is the performance of hot work in ATEX areas managed? (If applicable)
FR-E-762 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Saint Laurent UNGG |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FR-E-763 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Osiris RR |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FR-E-764 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Saint Laurent UNGG |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FR-E-765 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Osiris RR | a)Para 3.3.2.2 Pag.236 ---> It is not clear if there are systems for the reduction of oxydising agent when it is declared "limitation of the introduction of oxidising agent". Please provide information on this topic. | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FR-E-766 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Osiris RR | *Page 236. Section F-I-3.3.2. Ventilation systems F-I-3.3.2.1.; Ventilation system design: segregation and isolation provisions (as applicable). Assumtpions1/ and 5/. "The different nuclear and industrial ventilation systems have fire dampers which serve in particular to limit the propagation of a fire." What is its fire resistance rate? Do the fire dampers operate automatically in the presence of smoke? *Page 236. Section F-I-3.3.2. Ventilation systems; F-I-3.3.2.1. Ventilation system design: segregation and isolation provisions (as applicable). Assumption 1/. "Given the technical and human resources in place, the strategy adopted for BNI No. 40 in a fire situation is to stop the ventilation as soon as a fire outbreak is confirmed." How is smoke extraction done to maintain acces routes for firefighting?
FR-E-767 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Saint Laurent UNGG | a)Para 3.3.2.2 Pag.236 ---> It is not clear if there are systems for the reduction of oxydising agent when it is declared "limitation of the introduction of oxidising agent". Please provide information on this topic.
FR-E-768 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Saint Laurent UNGG | *Page 239. Section F-II-3.3.2.1. Ventilation system design: segregation and isolation provisions (as applicable). Assumption 1/. "Whatever the case, the protections to be installed on the ventilation systems mainly concern the means for preventing or limiting propagation of the fire and its effects via the ventilation network (primarily fire dampers)." What is its fire resistance rate? Do the fire dampers operate automatically in the presence of smoke? Is there a program to check the proper functioning of the fire dampers? *Page 238. Section F-II- UNGG Saint-Laurent des Eaux - BNI 46; F-II-3.3.1. Prevention of fire spreading (barriers); F-II-3.3.1.1. Design approach. Assumption 1/. "Personnel protection is ensured by setting up protected evacuation routes" How is smoke extraction guaranteed? Important in case of access and evacuation routes.
FR-E-769 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Saint Laurent UNGG |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FR-E-770 | PFP | FR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Osiris RR |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FR-E-771 | PFP | FR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Saint Laurent UNGG |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FR-E-772 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel enrichment facilities | Georges Besse II | Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements. page 102/Section C-I-3.1.1/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
FR-E-773 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel enrichment facilities | Georges Besse II |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FR-E-774 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel enrichment facilities | Georges Besse II |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FR-E-775 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | MELOX |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FR-E-776 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | MELOX | section C-IV-3.1.2. control of combustible materials does not describe any limits that may be in place and how they are monitored. Please confirm if there are limits in place for combustible inventories and how they are monitored and controlled.
FR-E-777 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | MELOX |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FR-E-778 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Romans inc CERCA | p.106, C-II-3.1.1, topic 1/: Please describe the basis for and how the maximum fire loads were defined for each room ?
FR-E-779 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Romans inc CERCA | please describe the tracking and control of the fire loads authorised in the rooms (as the report acknowledges this as requiring improvement in page 255).
FR-E-780 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | MELOX | p.226,C-IV-3.3.1.2,,topic 1/: text in section "Protected sectors" "The fire sector access doors and hatches are rated EI60". Please clarify if it really concerns fire sector doors, or should it have been protected sector doors? Why is EI60 acceptable since for walls at least EI120 is required?
FR-E-781 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | MELOX | Diesel and hydrogen are stated as being stored outside buildings - how are separation distances defined and/ or segregation provided e.g. use of fire barriers? Is there hydrogen or other flammable gases in buildings or piped into the building (page 225)?
FR-E-782 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | MELOX |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FR-E-783 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | Romans inc CERCA | C-II-3.3.1.3. Performance assurance through lifetime; fire dampers, barriers etc are stated as being subject to in-service inspection and periodic tests, however, no insights from the inspections, or details on frequency/ approach etc. were provided. Please describe. Please also describe the design of fire barriers - are they designed to full compartment burnout?
FR-E-784 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | Romans inc CERCA |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FR-E-785 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | MELOX |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FR-E-786 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Romans inc CERCA | p.219, C-II-3.3.2.2 and p. 218 C-II-3.3.1.2, topic 6/ : to clarify what is done on the extraction side in case of fire: p.219 gives the impression that extraction in maintained as long as possible, while p.218 indicates that extraction fire dampers are closed and can be re-opened for sectors containing radioactive materials. If effectively it is first closed, on what basis is it decided to re-open them?
FR-E-787 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Romans inc CERCA | see page 220 which states that the design rules of the sectorisation and ventilation components are formalised, but there is substantial variability between the site buildings housing uranium-bearing materials, notably for historical reasons. It also states that the weakness is overcome by procedures specific to each building, particularly regarding ventilation management in fire situations. Has consideration been given to introducing passive fire protection improvements? Also, regarding the provision of protected paths for the buildings housing uranium-bearing materials - does this relate to escape routes only? How are life and radiological hazards managed in the interim and how will this be resolved?
FR-E-788 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Romans inc CERCA |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FR-E-789 | PFP | FR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Fuel fabrication facilities | MELOX | p.256, C-IV, topic 2/: In the regulator's assessment it is said that efforts should still be made for defining and control of protected routes. Is this applicable to MELOX? From the information before in the NAR it seems more related to Romans. To be confirmed.
FR-E-790 | PFP | FR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Fuel fabrication facilities | MELOX |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FR-E-791 | PFP | FR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Fuel fabrication facilities | Romans inc CERCA |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FR-E-792 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel reprocessing facilities | UP3A-La Hague |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FR-E-793 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel reprocessing facilities | UP3A-La Hague |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FR-E-794 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | Please provide information on the location of combustible inventories (diesel, hydrogen etc) in relation to nuclear safety significant plant? Routing of pipework e.g. hydrogen, is it outside buildings? (limits appear in relation to equipment with surfaces above a pre-defined threshold) - page 92 please describe the selection of battery technology. page 93: There is a statement on the management of the temporary and permanent storage areas, some of which do not meet all the requirements concerning fire loads, particularly during plant unit outages. Are there limits to fire loading in place? And if so, are fire loads fully quantified? Page 93 - Each NPP has a department in charge of risk prevention EDF considers that the organisation in place for the preparation and tracking of hot work permits is robust. However ASN's assessment does not find hot work permit tracking to be robust. How is this been proactively followed upon and improved?
FR-E-795 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FR-E-796 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | Page 202 - The physical separation of two items of equipment with respect to fire means either installing them in two separate rooms, of which one at least constitutes a fire sector, or protecting one of them with a thermal coating. Physical separation is to be preferred to another arrangement. Under which circumstances is coating used versus segregation by barriers? What is the fire resistance claim of such SSCs? The safety fire sectors (SFS) are created to physically separate the safety equipment items ensuring functional redundancy. The fire resistance rating of the walls separating the redundant equipment items must not be less than 1 hour 30 minutes - does this provide for full compartment burn out and is fire containment approach applied generally? Page 205 - information on evacuation routes- what maximum distances are expected occupants to travel to a position of safety in the event of fire? page 207: In 2020, the IGSNR considered that the maintaining of sectorisation in operation (the fire doors in particular) was improving but still required vigilance - What items were identified as weak? What actions are being taken? The report states that planned measures can improve the fire resistance of certain components (fire doors, fire sectorisation components, fire protection of electric cables, etc.) or reduce the scale or intensity of potential fires. These measures consist more specifically in replacing fire sectorisation components (fire doors for example) by components with greater fire resistance.- Which plant areas have weaknesses and what weaknesses does this refer to and how are they being prioritised? EDF has identified doors representing a safety risk that will be equipped with "door open" alarms aiming to ensure they are kept closed - will they be alarmed to a permanently occupied location? Lastly, passive sectorisation equipment will be identified as high risk for safety and their in-service requirements will be tightened - What is the nature of the current shortfalls? What provision over and above those currently in place will be implemented?
FR-E-797 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FR-E-798 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FR-E-799 | PFP | FR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FR-E-800 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | RHF | How far away from the main building is the seperate building for waste?
FR-E-801 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | RHF | "ASN prescribed measures to limit the development of a fire, particularly in the reactor building." Please provide a short explanation about the above.
FR-E-802 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | RHF |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FR-E-803 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | RHF | How are the fire classes for fire barriers defined?
FR-E-804 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | RHF |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FR-E-805 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | RHF |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FR-E-806 | PFP | FR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | RHF |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FR-E-807 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | La Hague | 'Some topics, for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: • (b)"3.1.1 Design considerations and prevention means" (and related subparagraphs) Please provide missing information from the above.
FR-E-808 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | La Hague |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FR-E-809 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | La Hague |  | [generic]: o Compartmentation (as applicable): How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FR-E-810 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | La Hague | p230/D-3.3.1.2 The electrical equipment items serving to maintain the pool D building in a safe state are installed outside the pool D building and are separated by thermal shields. How is the fire safety performance of the thermal shields justified?
FR-E-811 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | La Hague | D.3.1.1 pag. 120 ---> Please clarify if and how gas reduction in the pool is taken into account
FR-E-812 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | La Hague |  | [generic] o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FR-E-813 | PFP | FR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | La Hague | p259/3.6 D "The licensee must nevertheless pay closer attention […] the management of hot work permits and fire loads, and more generally the firefighting means specific to the work sites." Please elaborate on what are the (types of) observed problems related to the above?
FR-E-814 | PFP | FR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | La Hague |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FR-E-815 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | La Hague Silo 130 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
FR-E-816 | PFP | FR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | La Hague Silo 130 | E-3.1.3.The report states that the initial design of the silo did not take into account the fire risk associated with the types of waste stored. The waste stored in pit 43 contains graphite, magnesium and uranium. Combustion of the magnesium and graphite can be initiated in the event of impact (such as during retrieval) by uranium hydride (UH3) which forms in the presence of humidity. How is this prevented/ mitigated? How is the retrieval operation controlled to prevent impact? section E-3.1.2 Are limits to fire loading explicitly set?
FR-E-817 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | La Hague Silo 130 | Section E-3.3.1.2; P.233. Please provide information about fire compartmentation of the La Hague Silo 130.
FR-E-818 | PFP | FR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | La Hague Silo 130 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
FR-E-819 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | La Hague Silo 130 | Section E-3.3.2; P.232. Please provide information about the ventilation system in the La Hague Silo 130. Section E-3.3.2.2; P.233. How are the ventilation systems designed to maintain access routes for firefighting?
FR-E-820 | PFP | FR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | La Hague Silo 131 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
FR-E-821 | PFP | FR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | La Hague Silo 130 |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
FR-E-822 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Osiris RR |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
FR-E-823 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Saint Laurent UNGG |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
FR-E-824 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Saint Laurent UNGG | (b) Clarify what actions were taken and fire safety measures improved following the 2015 event at the Brennilis site (pag 201 par. F-II-3.2.4.2).
FR-E-825 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Osiris RR |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FR-E-826 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Saint Laurent UNGG |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FR-E-827 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Osiris RR |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
FR-E-828 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Saint Laurent UNGG |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
FR-E-829 | AFP | FR | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Osiris RR |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
FR-E-830 | AFP | FR | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Osiris RR | /2/ p. 83: "For most of the installations being decommissioned, the fire scenarios represent the accident scenarios most likely to lead to the mobilisation and dispersal of a non-negligible quantity of radionuclides within the facility or into the environment. The environmental releases may be gases/aerosols and/or liquids." The contribution of active fire fighting to reduce the potential source terms should be worked out.
FR-E-831 | AFP | FR | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Saint Laurent UNGG |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
FR-E-832 | AFP | FR | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Saint Laurent UNGG | /2/ p. 88: In Section "II-2.6.4. Main results / dominant events (licensee´s experience)" the worst case radiologic consequences are described (what is more than in many other NARs), however the fire scenario and the potential contribution of active fire protection is not brought together. Could you please describe contribution of active fire protection measures to reduce the releases to environment.
FR-E-833 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Fuel reprocessing facilities | UP3A-La Hague |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
FR-E-834 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Fuel reprocessing facilities | UP3A-La Hague | Page 169 Section C-III-3.2.1 Topic 1 The NAR does not mention whether the fire detection and alarm system has any nuclear safety classification - does it? Page 170 Section C-III-3.2.1.2 Topic 1 contains no discussion of the fire resistance of the cables of the fire detection and alarm system - is there any?
FR-E-835 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Fuel reprocessing facilities | UP3A-La Hague | Page 170 Section C-III-3.2.1.2 Topic 1 There is no discussion around whether the fire detection and alarm system actuates any protective measures (such as damper operation) - are any actuated by the system?
FR-E-836 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Fuel reprocessing facilities | UP3A-La Hague |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FR-E-837 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Fuel reprocessing facilities | UP3A-La Hague | Page 171 Section C-III-3.2.2.2 Topic 1 The NAR discusses the fire fighting systems in the facility and these all appear to be manual. There is no explanation as to why this is the case and why are no automatic suppression systems required?
FR-E-838 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Fuel reprocessing facilities | UP3A-La Hague | /1/ (cf. P. 172) "Fixed manual fire extinguishing systems" with manual connection needed (?) are used for liquid fuels (HTP, (formalin)). How long does it take until the extinction system can operate?
FR-E-839 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Fuel reprocessing facilities | UP3A-La Hague |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
FR-E-840 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Fuel reprocessing facilities | UP3A-La Hague | Page 174 Section C-III-3.2.3.2 Topic 5 The NAR alludes to training but provides no detail of the training provided to the specialised secondary response teams. What training is priovided to this team?
FR-E-841 | AFP | FR | Active fire protection | Licensee and regulatory experience |  | Fuel reprocessing facilities | UP3A-La Hague |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
FR-E-842 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
FR-E-843 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | (p.133) The NAR states “the fire detection remains functional after an earthquake of OBE intensity. It is also designed, from the robustness aspect, not to send untimely commands to other elementary PIC systems during an earthquake of DBE intensity.” Clarify why the fire detection (monitoring rooms with seismically qualified SSCs) does not remain functional at least up to the DBE level.
FR-E-844 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | Page 133 of pdf, section A-I-3.2.1.2, assumption 1. Fire detectors' technology is not described. Please, describe the systems’ key features and technology (ionization and optical smoke detectors, flame detectors, heat detectors, linear detectors, air sampling detectors or other types). - Page 133 of pdf, section A-I-3.2.1.2, assumption 1. In general, are SSC important to safety covered by fire detectors? If not, please explain. - Page 135 of pdf, section A-I-3.2.1.3, assumption 4. Explain the procedures established for the examination, inspection, maintenance and testing of fire detection and alarm features.
FR-E-845 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FR-E-846 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | • (p.137) Clarify whether the fire suppression systems protecting areas hosting seismically qualified SSCs, are today themselves seismically qualified up to the DBE level (the NAR text is a bit ambiguous). • Please provide more details about the available portable and movable fire extinguishers (type, number, typical locations, strategy). • (p.137) The NAR states: “There are several types of fixed extinguishing system depending on the risk and the equipment to protect: Water sprinkler systems, pre-action sprinkler systems, total flooding systems.” Clarify what kind of fixed fire suppression system is used in rooms with electrical equipment, such as in the electrical building (BL) and in the main control room in particular.
FR-E-847 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
FR-E-848 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | • (p.136) The NAR states: “When a fire is detected, the first recon team and the response team are sent to the place to check it is not a false alarm […]. If the alarm is confirmed, the external emergency services are called.” Once they are called, how much time does it typically take for the external fire brigade to arrive on the fire location (taking also into account time for security checks, escort, …)? • Beyond Tricastin, for all EdF plants, what is the time needed for the external brigades to reach the fire location? • Please clarify the ventilation / protection strategy for the access routes for firefighters and for escape routes.
FR-E-849 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | Page 136 Section A-I.3.2.2.1 Topic 5 - explains that any worker may use the appropriate hand-held fire fighting means but does not explain the extent of training provided to the general workforce to enable such intervention. Please provide the relevant information.
FR-E-850 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | Page 141 of pdf, section A-I-3.2.3.2, assumption 1. "The response team shall be ready for action in front of the door of the stricken room 25 minutes at the most after the alarm or reporting call". Please, give evidence of the time of arrival from real events and drills. - Page 141 of pdf, section A-I-3.2.3.2, assumption 4. "The response team deploys the internal fire-fighting means to limit the impact of the fire and prepares for the arrival of the external emergency services". What are the firefighter qualifications, organization, fitness requirements, skills, duties during normal operation and training of the response team? Is there a professional onsite fire brigade or only offsite fire brigade? How far from the plant are the external emergency services located? Which is the minimum staffing? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for the external emergency services? - Page 141 of pdf, section A-I-3.2.3.2, assumption 1. Drills and exercises are not described. Please explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade, content and main lessons learnt. - Page 141 of pdf, section A-I-3.2.3.2, assumption 2. Explain the written procedures in place defining responsibility and actions of staff in responding to any fire in the installation. - Page 142 of pdf, section A-I-3.2.3.4, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety (additionally to the FAIop described in the NAR)? Please, describe their content.
FR-E-851 | AFP | FR | Active fire protection | Licensee and regulatory experience |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
FR-E-852 | AFP | FR | Active fire protection | Licensee and regulatory experience |  | NPP | Tricastin 900 Mwe, 1300, N4, EPR | (p.263) “The rapid response capacities of the on-site fire-fighting teams must be preserved. The firefighting duties of these teams must not be placed in competition with other duties that might be assigned to them.” Please clarify and provide more details, with concrete examples if possible.
FR-E-853 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | RHF |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
FR-E-854 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | RHF |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FR-E-855 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | RHF | Section 3.2 Absence of specific technical information on active fire protection systems. Please provide the requested information.
FR-E-856 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | RHF |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
FR-E-857 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | RHF | • (p151): What is the exact role of the LIRT in case of confirmed fire? Are they expected to fight fires as well? If so, what is the criteria to involve the external fire brigades or for the LIRT to fight the fire? • Is the role and availability of LIRT members compatible or potentially conflicting with their day-to-day duties (cf Regulator comment on p.263), in case of a fire emergency?
FR-E-858 | AFP | FR | Active fire protection | Licensee and regulatory experience |  | Research reactor | RHF |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
FR-E-859 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | La Hague |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
FR-E-860 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | La Hague | (TS 3.2.1 Design approach) - pag. 183 par. D-3.2.1.1 --> Specify and differentiate cases when audio and visual alarms are transmitted in the T0 unit and/or in PSM. (TS 3.2.1.3 Alternative/temporary provisions) - pag. 183 par. D-3.2.1.3 --> clarify what are the "special measures" that are put in place for hot work.
FR-E-861 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | La Hague |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FR-E-862 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | La Hague | (TS 3.2.2.2 Types, main characteristics...) - pag. 184 par. D-3.2.2.2 ---> Clarify if mobile or manual extinguishing systems are installed. (TS 3.2.2.4 Alternative/temporay provisions) -->Clarify where automatic and manual fire extinguishers are used.
FR-E-863 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | La Hague |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
FR-E-864 | AFP | FR | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - wet | La Hague |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
FR-E-865 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | La Hague Silo 130 |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
FR-E-866 | AFP | FR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | La Hague Silo 130 | Page 187 Section E-3.2.1.2 Topic 1 - The NAR contains no discussion of the fire resistance of the cables of the fire detection system. Please provide further clarification on this point.
FR-E-867 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | La Hague Silo 130 |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
FR-E-868 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | La Hague Silo 130 | Page Section E-3.2.2.3 Topic 4 - the NAR discusses potential effects of overpressure due to operation of the automatic extinguishing system which can be compensated for by increasing the ventilation system extraction flow rate, as operation of the last filtration barriers (DNF) is monitored. How is this controlled - automatically or manually?
FR-E-869 | AFP | FR | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | La Hague Silo 130 | (SP) There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information. The descriptions and characteristics of buildings and installations should be accompanied by figures in addition to text.
FR-E-870 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | La Hague Silo 130 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
FR-E-871 | AFP | FR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | La Hague Silo 130 | Page 190 Section 3.2.3.2 Topic 5 The NAR contains no detail of the training provided to the specialised secondary response teams. Please provide the relevant information.
FR-E-872 | AFP | FR | Active fire protection | Licensee and regulatory experience |  | Waste | La Hague Silo 130 |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
HU-E-873 | FSA | HU | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Paks NPP | P. 37-38: Could you indicate what the contribution of CDF resulting of fires to the total CDF is?. What are the most important accident sequences? (5/)
HU-E-874 | FSA | HU | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Paks NPP | 2.1.5, p41 How are changes between PSR considered with regard to updating of deterministic fire analyses?
HU-E-875 | FSA | HU | Fire safety analysis | Licensee and regulatory experience |  | NPP | Paks NPP |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
HU-E-876 | FSA | HU | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Budapest Research Reactor | 1 - According to the NAR a simultaneous occurrence of several independent fires and the combined effects is excluded from the assessment. Are any corrective measures implemented to exclude such cases? [page 45][section 2.2.2][assumption 2/] 2- Is the "so-called sensitivity analysis" something like a risk analysis with FMEA or something else? Please clarify. [page 45][section 2.2.2][assumption 2/]
HU-E-877 | FSA | HU | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics | The date for submission of the HA to the regulatory body is missing. How does the regulary body follow-up the late FHA? Is there a time table?
HU-E-878 | FSA | HU | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics | To p. 52-55: As mentioned in NAR the fire risk analysis of the BME OR is being developed in parallel with TPR II. Is it the first time of fire safety analysis is being performed? If no, could you describe the previous fire analysis, approach, main results, and insight if any?
HU-E-879 | FSA | HU | Fire safety analysis | PSR and modifications |  | Research reactor | Budapest Research Reactor | 1 - As a result of the PSR some measures of modification related to experimental and measurement equipment have been identified. Could you explain these measures in more detail? [page 50][section 2.2.5.2][topic 2/]
HU-E-880 | FSA | HU | Fire safety analysis | PSR and modifications |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics | To p. 55, topic 3/: As mentioned in the NAR "One of the major outcomes of the PSR at the facility was that it identified the lack of this fire risk assessment." Could you clarify, if the fire safety analysis is out of the scope of PSR? To topic 2/ There is no any information on performed modifications based or not based on fire safety analysis, events, experience, etc. Does it mean, that there are not in place any upgrades of fire protection features from commissioning?
HU-E-881 | FSA | HU | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Budapest Research Reactor | 2/ p. 52 (2.2.7.3) "Fire SA ... found partly satisfactory. ..." Do you have more recent information on the review of the new analysis? Has it been submitted to the co-authorities?
HU-E-882 | FSA | HU | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Budapest Research Reactor | 1 - How often is the targeted inspection related to fire protection conducted? [page 52][Section 2.2.7] [topic 2/]
HU-E-883 | FSA | HU | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Budapest Research Reactor |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
HU-E-884 | FSA | HU | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
HU-E-885 | PFP | HU | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Paks NPP | page 68/Section 3.1.2.1/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 68/Section 3.1.2.1/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
HU-E-886 | PFP | HU | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Paks NPP |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
HU-E-887 | PFP | HU | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Paks NPP | page 106/Section 3.3.1.2/ 1/What is the definition for fire section? What are fire resistance for fire barriers (walls, fire doors, fire dampers, cable penetrations...)?
HU-E-888 | PFP | HU | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Paks NPP |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
HU-E-889 | PFP | HU | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Paks NPP | page 111/Section 3.3.2.1/1/ Do you have installed HEPA filters in ventilation systems? page 111/Section 3.3.2.1/2/ How are the ventilation systems in fire compartments separating redundant trains? page 111/Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences? page 111/Section 3.3.2.1/3/ Describe the case where a ventilation system serves more than one fire compartments to prevent the spread of fire?
HU-E-890 | PFP | HU | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Paks NPP |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
HU-E-891 | PFP | HU | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Paks NPP | page 114/Section 3.4/1/ What were lessons learnt from OSART and WANO missions? Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
HU-E-892 | PFP | HU | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Paks NPP |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
HU-E-893 | PFP | HU | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Budapest Research Reactor | Please provide more information on the practise of temporary fire load management.
HU-E-894 | PFP | HU | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Budapest Research Reactor |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
HU-E-895 | PFP | HU | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics | Date for submission of FHA to the regulatory body is missing. How does the regulary body follow up the late FHA? Is there a time table? (Relevent to FIRE ANALYSES thematic)
HU-E-896 | PFP | HU | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics | How much time is given to Licensee to prepare Fire Risk Analysis? Qualitative or quantitative? Page 73 (Relevent to FIRE ANALYSES thematic)
HU-E-897 | PFP | HU | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
HU-E-898 | PFP | HU | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Budapest Research Reactor | How are the fire classes for fire barriers defined?
HU-E-899 | PFP | HU | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Budapest Research Reactor |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
HU-E-900 | PFP | HU | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics | Why is there only one single fire section for the reactor? Page 106 & 107
HU-E-901 | PFP | HU | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics | How are the fire classes for fire barriers defined?
HU-E-902 | PFP | HU | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
HU-E-903 | PFP | HU | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Budapest Research Reactor | Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers?
HU-E-904 | PFP | HU | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Budapest Research Reactor |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
HU-E-905 | PFP | HU | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
HU-E-906 | PFP | HU | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Budapest Research Reactor |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
HU-E-907 | PFP | HU | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
HU-E-908 | PFP | HU | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility | NAR section 3.3.1.2.3 pag. 107 --> Considering that in the NAR is reported "There are no fire cells in the facility...", Why there are no fire cells in the facility?
HU-E-909 | PFP | HU | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
HU-E-910 | PFP | HU | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility | NAR section 3.3.1 table point 3.4 page 102 -> Please clarify what was stated: "If the fire protection requirements for the separation of safety-important systems and their placement in separate fire sections conflict with the requirements for the functional design of the storage facility, it is necessary to ensure the separation of security systems from a fire protection point of view with distance protection and the creation of a fire cell"? NAR section 3.3.1.2.3 pag.107 -> Have the architectural fire protection requirements been adapted to current legislation?
HU-E-911 | PFP | HU | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
HU-E-912 | PFP | HU | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility | NAR section 3.3.2.1.3 pag.113 -> Is the inactive and clean exhaust system that expels air from inactive rooms still monitored at the exhaust?
HU-E-913 | PFP | HU | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
HU-E-914 | PFP | HU | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
HU-E-915 | AFP | HU | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Paks NPP |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
HU-E-916 | AFP | HU | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Paks NPP | Page 74, 79-81 Section 3.2.1 Topic 1 - no detail of nuclear safety class of the fire detection and alarm system, emergency power provisions, actuation of protective measures by the fire and alarm detection system. Please could you provide clarification on these issues?
HU-E-917 | AFP | HU | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Paks NPP | Page 74, 79-81 Section 3.2.1 Topic 2 - No information on the resilience or hazard tolerance of the fire detection and alarm system. No information on the fire rating of cables or enclosures or EMIT provisions. Please could you provide clarification on these issues?
HU-E-918 | AFP | HU | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Paks NPP | Section 3.2.1.1.1. Some cases are described for the rooms, which do not have fire detection system. In such cases stated that technological signals are used. Please describe how the assessment of technological signals from these locations done? Please provide more details on the measurement devices values of the technological signals/parameters. Its stays unclear which signals\parameters are used for that. Please provide information on this issue.
HU-E-919 | AFP | HU | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Paks NPP | Page 79 of pdf, section 3.2.1.2.1, assumption 1. Are non-interruptible emergency power supplies available to feed the fire detection and alarm features? Explain these power supplies. - Page 84 of pdf, section 3.2.1.3.1, assumption 4. Explain more in depth the types of compensatory measures in case of impairment of fire detection systems.
HU-E-920 | AFP | HU | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Paks NPP |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
HU-E-921 | AFP | HU | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Paks NPP | Page Section 3.2.2 - no detail on how the capacity of the suppression systems has been determined. No information on the water sources for the water based suppression systems. No consideration of the accessibility of the plant for manual fire fighting. Please could you provide clarification on these issues?
HU-E-922 | AFP | HU | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Paks NPP | Page Section 3.2.2 - No mention of seismic qualification or consideration of combined hazards, retention of fire fighting water or potential for spread of contamination by fire fighting water. Please could you provide clarification on these issues?
HU-E-923 | AFP | HU | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Paks NPP | Page 89 of pdf, section 3.2.2.2.1, assumption 2. It is stated that 2 pieces of 600-litre demineralised water tanks are used for water mist extinguishing systems for the protection of turbine oil systems. Which is the suppression duration supposed to calculate this capacity? The same question applies to the capacity of water mist extinguishing systems to protect diesel generators. - Page 90 of pdf, section 3.2.2.2.1, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown or any similar provision? - Page 90 of pdf, section 3.2.2.2.1, assumption 1. The use of standpipe hoses inside the main buildings is not described. Please, describe the type of hoses, lengths, separation between them and other features. Are all SSC important to safety covered by the jet from at least one hose? - Page 90 of pdf, section 3.2.2.2.1, assumption 2. Fire water pump stations and the fire protection water supply system are not described. Please describe electrical pumps and diesel-driven pumps; including flow and pressure, electrical supply, seismic category, separation between them and other relevant features. Also describe water tanks or other sources of supply; including their inventory, connections and other relevant features. - Page 90 of pdf, section 3.2.2.2.1, assumption 2. Explain if the fire ring include a double supply to buildings containing safety related SSC’s; and if this ring have isolation valves, the aim being to be able to isolate part of the main ring for maintenance or repair. - Page 90 of pdf, section 3.2.2.2.1, assumption 2. Hydrants are not described. Please, describe their main features including isolation valves, distance between them, coverage and connections. - Page 90 of pdf, section 3.2.2.2.1, assumption 3. Explain in general the procedures established for the examination, inspection, maintenance and testing of extinguishing systems. - Page 92 of pdf, section 3.2.2.3.1, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain.
HU-E-924 | AFP | HU | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Paks NPP |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
HU-E-925 | AFP | HU | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Paks NPP | Page 98 Section 3.2.3 Topic 1 - No detail of the criteria for contacting the external fire brigade. Please could you provide clarification on this issue?
HU-E-926 | AFP | HU | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Paks NPP | Page 96 of pdf, section 3.2.3.1.1, assumption 1. Drills and exercises are described very briefly. Please explain their goal, type, frequency, minimum number of drills and exercises per year for each member of the fire brigade, content and main lessons learnt. - Page 99 of pdf, section 3.2.3.2.1, assumption 4. “In the event of a fire, the first responder is the Nuclear Power Plant's professional industrial Fire Brigade. 18 trained firefighters per shift are available for deployment all the time”. Explain the training, organisation, minimum knowledge and physical conditions of the fire brigade. - Page 99 of pdf, section 3.2.3.2.1, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 99 of pdf, section 3.2.3.2.1, assumption 2. Explain the written procedures in place defining responsibility and actions of staff in responding to any fire in the installation. - Page 99 of pdf, section 3.2.3.2.1, assumption 2. Explain the coordination between the onsite fire brigade and the offsite fire brigade.
HU-E-927 | AFP | HU | Active fire protection | Licensee and regulatory experience |  | NPP | Paks NPP |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
HU-E-928 | AFP | HU | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | Budapest Research Reactor |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
HU-E-929 | AFP | HU | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
HU-E-930 | AFP | HU | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | Budapest Research Reactor |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
HU-E-931 | AFP | HU | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
HU-E-932 | AFP | HU | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics | (p91) Clarify why there is no automatic fire suppression system within the BME OR facility, especially keeping in mind that there is operators’ presence only during weekdays working hours. Is there any prohibited (red) radiological area where a fire could occur and that could not be accessible to fire brigade?
HU-E-933 | AFP | HU | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Budapest Research Reactor |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
HU-E-934 | AFP | HU | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Budapest Research Reactor | • (NAR p.9) The license of the BKR expires in Dec 2023. Will the BKR will be decommissioned after that date, or is the license expected to be extended? • How far is the external fire brigade? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours (so-called “abandoned state” on p.76)? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for on-call escort, presence of RP escort (NAR p.98), access formalities, personal protection equipment for entering radiological controlled zone, etc.).
HU-E-935 | AFP | HU | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
HU-E-936 | AFP | HU | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics | • There seems to be only one entrance/exit to the reactor hall. Is this correct, or is there a second access/evacuation route (p81-82)? If there is indeed only one access point, how does this impact the fire protection strategy? • (p96) It seems on one hand that there is no internal fire brigade. On the other hand, the NAR states “Everyone is obliged to participate in extinguishing fires to the extent realistically expectable […]”. To be clarified. • How far is the external fire brigade? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours (so-called “abandoned state” on p.52)? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for on-call escort (p99: “operator on standby”), presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.).
HU-E-937 | AFP | HU | Active fire protection | Licensee and regulatory experience |  | Research reactor | Budapest Research Reactor |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
HU-E-938 | AFP | HU | Active fire protection | Licensee and regulatory experience |  | Research reactor | Training Reactor of the Budapest University of Technology and Economics |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
HU-E-939 | AFP | HU | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
HU-E-940 | AFP | HU | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
HU-E-941 | AFP | HU | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards.
HU-E-942 | AFP | HU | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
HU-E-943 | AFP | HU | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Spent Fuel Interim Storage Facility |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-944 | FSA | IT | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | Latina NPP Magnox | How was the hazard of graphite fire (and graphite dust explosion) taken into account?
IT-E-945 | FSA | IT | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | Latina NPP Magnox | To 1/ (pp. 161-165): a) Can you please give clarification on what are the required safety functions and SSC to be protected in case of fire?
IT-E-946 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Latina NPP Magnox | Are there criteria to perform specific analyses? Is there a guide to define fire scenarios and to explain the use of calculation codes?
IT-E-947 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Latina NPP Magnox |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-948 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Trino NPP PWR | Are there criteria to perform specific analyses? Is there a guide to define fire scenarios and to explain the use of calculation codes ?
IT-E-949 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Trino NPP PWR |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-950 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | EUREX FCF | Are there criteria to perform specific analyses? Is there a guide to define fire scenarios and to explain the use of calculation codes ?
IT-E-951 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | EUREX FCF |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-952 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | ESSOR RR | Are there criteria to perform specific analyses? Is there a guide to define fire scenarios and to explain the use of calculation codes ?
IT-E-953 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | ESSOR RR |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-954 | FSA | IT | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Tapiro Fast neutron | To p.19, ch.A.2.2.7.2: Is there a time table regarding the fire hazard analysis that has been only recently conducted? It needs some additional analyses and demonstrations to be provided that will be supervised by ISIN.
IT-E-955 | FSA | IT | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Tapiro Fast neutron | To p. 55-56, assumptions 2/3/: Could you clarify from the commissioning if there is no fire safety analysis performed? What is the reason of this, low potential risk from the facility? Can you clarify if it is correct that the Tapiro areas are currently zoned according to the potential radiological risk? There are no zones according to the fire risk.
IT-E-956 | FSA | IT | Fire safety analysis | PSR and modifications |  | Research reactor | Lena Triga Mark II | 1 - The report states that there is an ongoing evaluation of the fire detection and alarm system ageing, but can you clarify if the verification of the fire assessment is done systematically for every reactor modification, or if it is checked at fixed periodic intervals? [page 43][Section A.I.2.1.5.2] [Topic 3/]
IT-E-957 | FSA | IT | Fire safety analysis | PSR and modifications |  | Research reactor | Tapiro Fast neutron | To p. 18, topic 3/: The NAR mentioned that the Tapiro reactor is currently not operating, in view of an improvement program to be implemented. Could you describe the main improvements to be implemented? Are any improvements related to fire protection? Will these improvements be considered in the upcoming FHA? To topic 1/: Was Tapiro a subject of PSR? Is fire safety included in the scope of PSR?
IT-E-958 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Lena Triga Mark II |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-959 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Tapiro Fast neutron |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-960 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Tapiro Fast neutron | To p.19, topic 2/: In light of the information mentioned in section A.2.2.7.2, is it true that no inspection on fire safety was conducted at Tapiro?
IT-E-961 | FSA | IT | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | Avogadro AFR | Please provide the information in the degree of detail requested in the Section 02.4 of the Technical Specifications.
IT-E-962 | FSA | IT | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | ESSOR-plant | Please provide the information in the degree of detail requested in the Section 02.4 of the Technical Specifications.
IT-E-963 | FSA | IT | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | ITREC-plant | Please provide the information in the degree of detail requested in the Section 02.4 of the Technical Specifications.
IT-E-964 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | Avogadro AFR |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire safety analyses with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Inventory make-up: Please provide a higher level of detail on the systems used to make-up inventory. 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 5. Additional analyses: Please provide details about: a) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for spent fuel storage facilities in your country? b) Some countries mention that a periodic safety review is performed for spent fuel storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 6. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-965 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | Avogadro AFR | P. 20-21 (B.2.3.7.1 and B.2.3.7.3) Report says the water pool cooling system is not redundant; there is a large margin for decay heat removal performed by natural circulation; and heat removal function can be assured by the evaporation of the water in the pool. Additionally at p. 100 (B.III.1.1) is mentioned, that the storage facility contains only 64 fuel elements. What are possible consequences and recovery actions needed in case of fire affecting cooling system?
IT-E-966 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | ESSOR-plant |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire safety analyses with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Inventory make-up: Please provide a higher level of detail on the systems used to make-up inventory. 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 5. Additional analyses: Please provide details about: a) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for spent fuel storage facilities in your country? b) Some countries mention that a periodic safety review is performed for spent fuel storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 6. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-967 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | ESSOR-plant | P. 20-21 (B.2.3.7.1 and B.2.3.7.3) Report says there is no need for active heat removal and heat removal function can be assured by the evaporation of the water in the pool. What are possible consequences and recovery actions needed in case of fire affecting cooling system?
IT-E-968 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | ITREC-plant |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire safety analyses with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Inventory make-up: Please provide a higher level of detail on the systems used to make-up inventory. 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 5. Additional analyses: Please provide details about: a) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for spent fuel storage facilities in your country? b) Some countries mention that a periodic safety review is performed for spent fuel storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 6. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-969 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | ITREC-plant | P. 20-21 (B.2.3.7.1 and B.2.3.7.3) Report says there is no need for active heat removal and heat removal function can be assured by the evaporation of the water in the pool. What are possible consequences and recovery actions needed in case of fire affecting cooling system?
IT-E-970 | FSA | IT | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | /1/ P-117: The approach is described, but is ist possible to provide details provided on the underlying models, data etc? What is a qualitative FHA?
IT-E-971 | FSA | IT | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Facility 2300 (Eurex) | /1/ P-126: The approach is described, but is ist possible to provide details provided on the underlying models, data etc? What is a qualitative FHA?
IT-E-972 | FSA | IT | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | D2 storage facility (Eurex) | /1/ P- 134:The approach is described, but is it possible to provide details on the underlying models, data etc? What is a qualitative FHA?
IT-E-973 | FSA | IT | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Deposito OPEC2 | p152 : "The assumptions underlying the evaluation of the released source term are very conservative. It has been considered involved into the fire drums with maximum Plutonium content": Which kind or other assumptions? Which A considered? FDS calculations : How did you manage with Reliability on data, uncertainties, safety margins? "The ventilation system can be restarted in extraction once the temperature in the compartment has returned below 120°C without compromising the functionality of the filters". How smoke and soots taken into account for clogging of HEPA filters? Is the failure of fire dampers taken into account?
IT-E-974 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | /2/ Is there any regulatory experience documented?
IT-E-975 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Waste | D1-D2 waste storage facilities (Trino NPP site) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-976 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Waste | Facility 2300 (Eurex) | /2/ Is there any regulatory experience documented?
IT-E-977 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Waste | Facility 2300 (Eurex) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-978 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Waste | D2 storage facility (Eurex) | /2/ Is there any regulatory experience documented?
IT-E-979 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Waste | D2 storage facility (Eurex) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-980 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Waste | NPS New tank park (Eurex) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-981 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Waste | Area 800 (Eurex) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-982 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Waste | Deposito OPEC2 | /2/ Is there any regulatory experience documented?
IT-E-983 | FSA | IT | Fire safety analysis | Licensee and regulatory experience |  | Waste | Deposito OPEC2 |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
IT-E-984 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Latina NPP Magnox | *Page 8. Key parameters. - Please descibe the intended end state is of decommissioning. *Page 166. D.I.3.1.2. Section Overview of arrangements for management and control of fire load and ignition sources. Assumption 3/. REGARDING FIRE LOADS AND IGNITION SOURCES. The NAR provides little information about temporary or fixed fire load management, neather about ignition sources. Please, answer the following questions having into account the state of the facility (or indicate if it does not apply): -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) REGARDING HOT WORK "If the activity involves use of open flame, this use is done without combustible material and whit safety prescriptions." Please, answer the following questions having into account the state of the facility (or indicate if it does not apply): -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.)
IT-E-985 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Latina NPP Magnox |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-986 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Trino NPP PWR | *Page 175. Section D.II.3 Fire Protection Concept and Its Implementation; D.II.3.1 Fire prevention; D.II.3.1.1. Design considerations and prevention means. "Combustible materials are not allowed, especcially in the classified area, if not strictly needed." What are the processes by which the use of combustible materials is managed? What is the process to decide what combustible materials are strictly necessary? Valuation and permitting process?. REGARDING HOT WORKS. The NAR gives little information about this topic. Please, answer the following questions having into account the state of the facility (or indicate if it does not apply): -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) REGARDING FIRE LOADS AND IGNITION SOURCES. The NAR gives little information about this topic. Please, answer the following questions having into account the state of the facility (or indicate if it does not apply): -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.)
IT-E-987 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Trino NPP PWR |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-988 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | EUREX FCF | *Page 8. Key parameters. - Please descibe the intended end state of decommissioning. *Page 197. Section D.IV.3 Fire Protection Concept and Its Implementation; D.IV.3.1 Fire prevention; D.IV.3.1.1. Design considerations and prevention means. Assumtpion 3/. "Minimization of additional combustible materials present in storage areas." Are there permanent and temporal storages?; In that case, Are they checked to verify that they are as expected with a certain periodicity? Are the (fix and temporary) storage areas registered and clearly identified? Is it taken into account that the location of the storage is far from ignition sources? (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) *Page 197. Section D.IV.3.1.2. Overview of arrangements for management and control of fire load and ignition sources. Assumtpion 3/. "Whenever an ignition source shall be used (e.g. tools for mechanical cutting producing hot swarfs), combustible material are not allowed in the surrounding or, if possible, are segregated." REGARDING HOT WORKS. The NAR gives little information about this topic. Please, answer the following questions having into account the state of the facility (or indicate if it does not apply): -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.)
IT-E-989 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | EUREX FCF |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-990 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | ESSOR RR | *Page 8. Section 1.1.3. Key parameters per installation. - Please describe the intended end state o decommissioning. - In the table is indicated the year 1987 as Year of authorization for decommissioning. However in Page 184 the Licensee indicate "Nevertheless, the ESSOR plant and its related laboratories are currently in a SAFE STORAGE phase while the decommissioning authorization has not been granted yet since the application was submitted only in 2023". What is the correct date?. *Page 185. Section D.III.3.1 Fire prevention; D.III.3.1.1. Design considerations and prevention means. Assumtpion 3/. "The quantities of combustible materials present are reduced to the minimum necessary for the normal conduct of work." REGARDING FIRE LOADS AND IGNITION SOURCES.The NAR gives little information about this topic. Please, answer the following questions having into account the state of the facility (or indicate if it does not apply): -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) REGARDING HOT WORKS. "To date, the work activities within the controlled zones are limited to the scheduled maintenance of the facilities, performed by external companies, to environmental monitoring with radiation protection systems, to instrumental surveys of various types preparatory to the executive design of the decommissioning phases, to cleaning works of the rooms." Are hot work carried out at the facility? In that case: Please, answer the following questions having into account the state of the facility (or indicate if it does not apply): -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.)
IT-E-991 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | ESSOR RR |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-992 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Latina NPP Magnox | *Page 170. Section D.I.3.3.1 Prevention of fire spreading (barriers) ; D.I.3.3.1.1. Design approach. Assumption 3/. "Accordingly with the third level of defence in depth concept is assumed that fire extinguishing systems fail and that firefighters do not respond quickly enough which causes fire development. In this scenario the confinement of radioactive spread is guarantee by the fire compartment of each storage area designed to withstand the worst-case scenario" NAR indicates in page 163 that "New radioactive repository"with "electrical ignition probability"; and "Radioactive liquid treatment building" with fire dangers like "solid combustible, high heated machine", have a REI classification 0. So, How is it guaranteed that in the event of a fire in these areas, there will be no discharge of reactive contamination into the environment? In page 170 NAR sais "In the repository, wastes can be enclosed in fire resistant shell to avoid their participation in case of fire", what is the fire rate of theses shells?. *Page 170. Section D.I.3.3.1 Prevention of fire spreading (barriers) ; D.I.3.3.1.1. Design approach. Assumtpion 3/. "Compartimentation is designed following the recommendations of national guidances (UNI guidances on REI criteria), based upon the assessment of fire load for every activity (rif. DM 10/03/1998, Evaluation of fire load – LT MS 10891). The same criteria are used for every new decommissioning activity." Is the fire resistance of the compartments taken into account when allowing temporary and/or fixed storage during desmantling activities? (The question mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) *Page 170. Section D.I.3.3.1 Prevention of fire spreading (barriers) ; D.I.3.3.1.1. Design approach. Assumtpion 3/. "It is avoided that a possible fire spreads, or that the fumes spread through the ventilation systems. For this purpose, the ventilation ducts, at the crossings of walls that constitute fire compartmentalization, are equipped with fire dampers with fire classification completely identical of the wall crossed." Please provide a brief description of other elements that form the fire barriers (walls, ceilings, doors, penetrations, seals...). What fire-resistance do closures of openings have? Is it the same than the one for boundaries? Are periodic inspections of these elements carried out? REGARDING ACCESS ROUTES. Assumption 4/. Is not described how access routes for firefighting are maintained. Please, provide this information. *Page 171. Section D.I.3.3.1.3. Performance assurance through lifetime. Assumtpion 5/. "Functional conditions and performances of compartments are verified and tested through time by periodic checking (six month-based), carried out following the provisions of the Decommissiong Authorization or reference national legislation." Are all fire barrier elements (doors, seals, dampers, walls...) tested?
IT-E-993 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Latina NPP Magnox |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-994 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Trino NPP PWR | *Page 178. Section D.II.3.3 Passive fire protection; D.II.3.3.1 Prevention of fire spreading (barriers); D.II.3.3.1.1. Design approach. Assumption 1/. "In the fire hazard analysis, the fire barriers are evaluated. It is mainly considered that the thickness of the facility walls is sufficient to prevent the fire spreading. This is due minly to the fact that the thickness needed by the radiation protection point of view is normally bigger than the thickness needed for fire protection." In page 179 NAR sais: "The fire safety analysis is performed taking into account every area of the NPP. For each area the presence of combustible material and the characteristics of fire prevention are listed." Is the fire resistance of the compartments taken into account when allowing temporary and/or fixed storage? "The spreading of secondary fire is also avoided through the use of anti-fire-spreading cables, walls and doors." What is the fire rate for elements like doors, sealings, fire dampers...? Are periodic inspections carried out on these components? Are the seals installed by qualified personnel and using certified materials? REGARDING ACCESS ROUTES. Assumption 4/. Is not described how access routes for firefighting are maintained. Please, provide this information. *Page 179. Section D.II.3.3.1.3. Performance assurance through lifetime. Assumption 2/ and 5/. "Inspections on specific compartimentation (as waste storage facilities walls or Reactor Building walls and doors) are periodically performed. In case of malfunctioning or visible deterioration of their characteristics, maintenance is provided. […] The areas where SSC important to safety are located, are equipped with fire barriers (e.g. main control room, diesel generator area, DC battery area, etc.)" Are inspections carried out on barriers in all areas that contain SSC important to safety?
IT-E-995 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Trino NPP PWR |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-996 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | EUREX FCF | REGARDING ACCESS ROUTES. Assumption 4/. Is not described how access routes for firefighting are maintained. Please, provide this information.
IT-E-997 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | EUREX FCF |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-998 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | ESSOR RR | *Page 192. Section D.III.3.3.1.1. Design approach. Assumption 2/. "All building structures shall ensure fire resistance appropriate to the fire load provided therein. The compartments have a fire resistance class compatible with the expected fire loads and are calculated according to Italian regulations." Are the fire barriers rate taken into account before to introduce transient or fixed fire loads? REGARDING ACCESS ROUTES. Assumption 4/. Is not described how access routes for firefighting are maintained. Please, provide this information.
IT-E-999 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | ESSOR RR |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1000 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Latina NPP Magnox | *Oage 171. Section D.I.3.3.2.2. Performance and management requirements under fire conditions. Assumption 1/. "In case of fire, ventilation system is shut down by authomatically ventilators turning off. The ventilation shut down is controlled by the detection system starting (alarm signal);" How is smoke extraction guaranteed? Important in case of access and evacuation routes.
IT-E-1001 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Latina NPP Magnox |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1002 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Trino NPP PWR | *Page 180. Section D.II.3.3.2 Ventilation systems; D.II.3.3.2.1. Ventilation system design: segregation and isolation provisions (as applicable). Assumption 1/. "The ventilation system is designed to be automatically or manually closed in order to seal zones. Since it is located on vertical walls or ceiling, it does not interfere with firefighting routes. During fire events, the ventilation system in hazardous areas is designed to shut down automatically. In the other cases, it is shut down manually." Is there a program to check the proper functioning of fire dampers? How are these access and escape routes maintained as the plant changes as a result of decommissioning? and How is smoke extraction guaranteed? *Page 180. Section D.II.3.3.2 Ventilation systems; D.II.3.3.2.1. Ventilation system design: segregation and isolation provisions (as applicable). Assumption 4/. What is the fire resistance rate of ventilation system?
IT-E-1003 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Trino NPP PWR |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1004 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | EUREX FCF | * Page 200. Section D.IV.3.3.2 Ventilation systems; D.IV.3.3.2.1. Ventilation system design: segregation and isolation provisions (as applicable) "No segregation of ventilation or fire dampers are present, due to design and construction time (60’s); in any case the filtering unit is very far from eventual fire (long ventilation ducts)" What measures are applied to avoid the affectation of the filter units by a fire? REGARDING ACCESS ROUTES.Assumtpion 1/. How smoke is extracted in case of fire to maintain access routes for firefighting?
IT-E-1005 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | EUREX FCF |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1006 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | ESSOR RR | * Page 193. Section D.III.3.3.2.1. Ventilation system design: segregation and isolation provisions (as applicable). Assumtpion 1/. "Fire systems have the same REI class as wall compartments. The ventilation systems that pass through adjacent compartments are equipped with fire dampers controlled by a smoke detection system." Is there a program to check the proper functioning of fire dampers?
IT-E-1007 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | ESSOR RR |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1008 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Latina NPP Magnox |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1009 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Trino NPP PWR | *Page 180. Section D.II.3.4 Licensee’s experience of the implementation of fire protection concept. Assumption 1/. Lessons learnt are not mentioned in the NAR. Please provide that information.
IT-E-1010 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Trino NPP PWR |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1011 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | EUREX FCF | *Page 200. Section D.IV.3.4 Licensee’s experience of the implementation of fire protection concept. Assumtpion 1/. Strengths and weaknesses are not clearly mentioned in the NAR. Lessons learnt are not mentioned. Please provide that information.
IT-E-1012 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | EUREX FCF |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1013 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | ESSOR RR |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1014 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Lena Triga Mark II |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1015 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Tapiro Fast neutron | (P 19 Ch A.2.2.7.2) Timetable regarding the fire hazard analysis that has been only recently conducted? It needs some additional analyses and demonstrations to be provided, that will be supervised by ISIN. --- (Relevent to FIRE ANALYSES thematic)
IT-E-1016 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Tapiro Fast neutron |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1017 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Lena Triga Mark II | How are the fire classes for fire barriers defined?
IT-E-1018 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Lena Triga Mark II |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1019 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Tapiro Fast neutron | How are the fire classes for fire barriers defined?
IT-E-1020 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Tapiro Fast neutron |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1021 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Lena Triga Mark II | Please provide more comprehensive information on the ventilation systems.
IT-E-1022 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Lena Triga Mark II |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1023 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Tapiro Fast neutron |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1024 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Lena Triga Mark II | It is considered that A.I.3.4 Licensee's experience of the implementation of fire protection concept section should be specified in a more comprehensive manner for better understanding.
IT-E-1025 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Lena Triga Mark II |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1026 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Tapiro Fast neutron | A.II.3.4 Licensee’s experience of the implementation of fire protection concept section should be specified in a more comprehensive manner for better understanding. (page 63)
IT-E-1027 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Tapiro Fast neutron |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1028 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | ESSOR-plant dry |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1029 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | ITREC-plant dry |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1030 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | ESSOR-plant dry |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1031 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | ITREC-plant dry |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1032 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | ESSOR-plant dry |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1033 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | ITREC-plant dry |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1034 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | ESSOR-plant dry |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1035 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | ITREC-plant dry |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1036 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | Avogadro AFR | The following information is missing in the NAR: Fire prevention measures/approach implemented at this facility- any learning from regulatory activity and specific approach used. Actual removal date for spent fuel from the facility (stated to be in the near future) - page 100. Consideration of fire prevention and passive fire protection during fuel transfer operations (planned) Please provide the missing information from the above.
IT-E-1037 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | Avogadro AFR |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1038 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | ESSOR-plant | ESSOR spent fuel a program to remove no more usable combustible cables is ongoing (page 26) - Recognising the value of this in terms of fire load reduction, how is it considered for the other spent fuel storage facilities to being decommissioned in the near future?
IT-E-1039 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | ESSOR-plant |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1040 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | ITREC-plant |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1041 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | Avogadro AFR | Page 34 recognises that there are no passive fire protection barriers. Consideration of fire prevention and passive fire protection during fuel transfer operations (planned) - this is not described in the NAR. Please describe fire prevention and protection arrangements during the planned fuel transfer operations.
IT-E-1042 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | Avogadro AFR |  | [generic]: o Compartmentation (as applicable): How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1043 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | ESSOR-plant | As per Avogadro: Please describe fire prevention and protection arrangements during the planned fuel transfer operations.
IT-E-1044 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | ESSOR-plant |  | [generic]: o Compartmentation (as applicable): How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1045 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | ITREC-plant |  | [generic]: o Compartmentation (as applicable): How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1046 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | Avogadro AFR |  | [generic] o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1047 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | ESSOR-plant |  | [generic] o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1048 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | ITREC-plant |  | [generic] o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1049 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Avogadro AFR |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1050 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | ESSOR-plant |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1051 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | ITREC-plant |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1052 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | Section C.I.1.1.2; P.119. Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined? Section C.I.3.1.2; P. 119. How much resin is stored in D1-D2 waste storage facilities and what is their fire load density? What is the fire resistance of the packages in which the resin is stored?
IT-E-1053 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1054 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Facility 2300 (Eurex) | Section C.II.3.1.2; P.128. Please provide information about flammability characteristics of radioactive waste in the waste storage facility 2300. Section 4; P.33; What are the fire prevention measures during transfer of the radioactive waste from 2300 to D2 radioactive waste storage facility? Section C.I.3.1.2; P.128. Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined?
IT-E-1055 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Facility 2300 (Eurex) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of
IT-E-1056 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | D2 storage facility (Eurex) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1057 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | NPS New tank park (Eurex) | Section C.IV.3.1.2; P.143. Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined?
IT-E-1058 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | NPS New tank park (Eurex) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1059 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Area 800 (Eurex) | Section C.V. 2.1.1; P.148. What amount of combustible organic waste can be stored? What are the flammability characteristics of this waste? What fire prevention measures are applied to prevent organic combustible liquid waste from igniting? Section C.V.3.3.1.1; P.150. Please provide information, is the bituminised mineral velt used for tank waterproofing flammable?
IT-E-1060 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Area 800 (Eurex) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1061 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Deposito OPEC2 | Section C.VI.2.1.4 ; P.154; Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined?
IT-E-1062 | PFP | IT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Deposito OPEC2 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
IT-E-1063 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | Section C.I.3.1.2 ; P.119. What are the fire resistance and the fire safety requirements of the metal containers that store combustible waste? Section C.I.3.3.1.2; P.123. Please provide information about fire compartmentation of the D1-D2 waste storage facilities.
IT-E-1064 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1065 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Facility 2300 (Eurex) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1066 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | D2 storage facility (Eurex) | C.III.3.3.1.2; P. 138. Please provide information for the D2 storage facility about separation into fire compartments. Section C.III.3.3.1.2; P. 138. What is the fire resistance of the floors of the building?
IT-E-1067 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | D2 storage facility (Eurex) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1068 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | NPS New tank park (Eurex) | Section C.IV.3.3.1.2; P. 138. Please provide informatioan about thefire compartmentation of NPS new tank park building.
IT-E-1069 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | NPS New tank park (Eurex) | p146/C.IV.3.3.1.2. Could you provide the fire resitance rating of the fire compartments? How is it determined?
IT-E-1070 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | NPS New tank park (Eurex) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1071 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Area 800 (Eurex) | Section C.V.3.3.1.2; P.150. Please provide information for area 800 about its fire compartmentation.
IT-E-1072 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Area 800 (Eurex) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1073 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Deposito OPEC2 | Section C.VI. 3.3.1.; P.158. Please provide information about fire compartmentation of the Deposito OPEC2.
IT-E-1074 | PFP | IT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Deposito OPEC2 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
IT-E-1075 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | p123/C.I.3.3.2.1. "As reported in the fire safety analysis, the waste storage facilities are not provided with a ventilation system." There is no mention of this in the fire analysis section. How is the ventilation of the facility arranged?
IT-E-1076 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1077 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Facility 2300 (Eurex) | p129/C.II.3.3.2.1 No ventilation system is present. How is the ventilation of the facility arranged?
IT-E-1078 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Facility 2300 (Eurex) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1079 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | D2 storage facility (Eurex) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1080 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | NPS New tank park (Eurex) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1081 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Area 800 (Eurex) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1082 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Deposito OPEC2 | p123/C.I.3.3.2.1. "As reported in the fire safety analysis, the waste storage facilities are not provided with a ventilation system." There is no mention of this in the fire analysis section. Can you explain why a ventilation system is not needed?
IT-E-1083 | PFP | IT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Deposito OPEC2 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
IT-E-1084 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | Section C.I.3.4; P.123. Are passive fire protection measures included in the ongoing D2 refurbishing program?
IT-E-1085 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | D1-D2 waste storage facilities (Trino NPP site) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1086 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Facility 2300 (Eurex) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1087 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | D2 storage facility (Eurex) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1088 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | NPS New tank park (Eurex) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1089 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Area 800 (Eurex) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1090 | PFP | IT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Deposito OPEC2 |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
IT-E-1091 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Latina NPP Magnox |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1092 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Latina NPP Magnox | Page 168 of pdf, section D.I.3.2.1.2, assumption 4. Explain in general the procedures established for the examination, inspection, maintenance and testing of fire detection and alarm features. - Page 168 of pdf, section D.I.3.2.1.3, assumption 4. Explain more in depth the types of compensatory measures in case of impairment of fire detection systems.
IT-E-1093 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Trino NPP PWR |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1094 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Trino NPP PWR | Page 176 of pdf, section D.II.3.2.1.2, assumption 1. Are non-interruptible emergency power supplies available to feed the fire detection and alarm features? Explain these power supplies. - Page 176 of pdf, section D.II.3.2.1.2, assumption 1. Are failures of the cable connections announced to the main control room? - Page 176 of pdf, section D.II.3.2.1.2, assumption 4. Explain in general the procedures established for the examination, inspection, maintenance and testing of fire detection and alarm features.
IT-E-1095 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Trino NPP PWR | A description of the active fire safety of the facilities is in Appendix D. D.II.3.2 does not provide a detailed description of the types of fire detection sensors and the timing of fire detection. Please provide the relevant information.
IT-E-1096 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | EUREX FCF |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1097 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | EUREX FCF | Page 198 of pdf, section D.IV.3.2.1.1, assumption 1. “Alert the operator for any manual request for intervention of the CO2 fire suppression”, “remote transmission of alarm signals to predetermined area”. Where are the fire alarm signals transmitted to? Is there a control room or any similar location? Is there an operator present in this location? - Page 198 of pdf, section D.IV.3.2.1.2, assumption 1. Are non-interruptible emergency power supplies available to feed the fire detection and alarm features? Explain these power supplies. - Page 198 of pdf, section D.IV.3.2.1.2, assumption 1. Are failures of the cable connections announced to the control room?
IT-E-1098 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | ESSOR RR |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1099 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | ESSOR RR | Page 189 of pdf, section D.III.3.2.2, assumption 2. Regarding the fire pumps: describe their flow and pressure, electrical supply, seismic category, separation between them and other relevant features.
IT-E-1100 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | ESSOR RR | Section D.IV.3.2 contains only a general description of the active fire protection system. It is proposed to provide a more detailed description of this system.
IT-E-1101 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Latina NPP Magnox |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1102 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Latina NPP Magnox | Page 168 of pdf, section D.I.3.2.2.2, assumption 2. Regarding the main pump and the emergency pump: are they electrical pumps or diesel-driven pumps? Describe their flow and pressure, electrical supply, seismic category, separation between them and other relevant features. - Page 169 of pdf, section D.I.3.2.2.2, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to fire hoses/hydrants or any similar provision? - Page 169 of pdf, section D.I.3.2.2.2, assumption 3. Explain in general the procedures established for the examination, inspection, maintenance and testing of extinguishing systems. - Page 169 of pdf, section D.I.3.2.2.3, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain.
IT-E-1103 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Trino NPP PWR |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1104 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Trino NPP PWR | Page 177 of pdf, section D.II.3.2.2.2, assumption 1. The types of fire extinguishing systems is stated very briefly. Please, describe the key features and technology of the different types of systems (spray, sprinkler, hoses, gas, foam, hydrants or other types). - Page 177 of pdf, section D.II.3.2.2.2, assumption 2. Regarding the fire pumps: describe their flow and pressure, electrical supply, seismic category, separation between them and other relevant features. - Page 177 of pdf, section D.II.3.2.2.2, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to fire hoses/hydrants or any similar provision? - Page 177 of pdf, section D.II.3.2.2.2, assumption 3. Explain in general the procedures established for the examination, inspection, maintenance and testing of extinguishing systems. - Page 177 of pdf, section D.II.3.2.2.4, assumption 3. Explain in general the types of compensatory measures in case of impairment of fire suppression systems.
IT-E-1105 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | EUREX FCF |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1106 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | EUREX FCF | Page 199 of pdf, section D.IV.3.2.2.2, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to fire hoses/hydrants or any similar provision? - Page 199 of pdf, section D.IV.3.2.2.2, assumption 2. Regarding the fire pumps: describe their flow and pressure, electrical supply, seismic category, separation between them and other relevant features. - Page 199 of pdf, section D.IV.3.2.2.2, assumption 3. Explain in general the procedures established for the examination, inspection, maintenance and testing of extinguishing systems.
IT-E-1107 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | ESSOR RR |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1108 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Latina NPP Magnox |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
IT-E-1109 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Latina NPP Magnox | Page 170 of pdf, section D.I.3.2.3.2, assumption 4. “On site there is a firefighting of n.21 employees, trained according to the national law for the higher level of fire risk with final exam certification by the fire department”. “Firefighting team are available, in group of three, beyond worker’s hours”. Explain the training, organisation, minimum staffing, minimum knowledge and physical conditions of the onsite fire brigade. What is the difference between the internal fire-fighting staff and the onsite fire-fighting brigade? - Page 170 of pdf, section D.I.3.2.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content.
IT-E-1110 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Trino NPP PWR |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
IT-E-1111 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Trino NPP PWR | Page 177 of pdf, section D.II.3.2.3.2, assumption 4. Regarding the “fire fighting team”: what are the firefighter qualifications, organization, fitness requirements, skills, duties during normal operation and training? Is there a professional onsite fire brigade or only offsite fire brigade? How far from the plant is the offsite fire brigade located? - Page 177 of pdf, section D.II.3.2.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content.
IT-E-1112 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | EUREX FCF |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
IT-E-1113 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | EUREX FCF | Page 199 of pdf, section D.IV.3.2.3.2, assumption 4. Regarding the “on site Fire-Fighting Brigade”: what are the firefighter qualifications, minimum staffing, minimum knowledge, organization, fitness requirements, skills, duties during normal operation and training? - Page 199 of pdf, section D.IV.3.2.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content.
IT-E-1114 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | ESSOR RR |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
IT-E-1115 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | ESSOR RR | Page 192 of pdf, section D.III.3.2.3.2, assumption 4. “The teams of the Fire Brigades operating 24 hrs/day, based within the JRC Ispra site, have intervention times of about 5 minutes, in case of detection of anomalies and alarms by the INE detection systems. They are perfectly trained for any type of intervention”. Explain the training, organisation, minimum staffing, minimum knowledge, physical conditions and other features of the onsite fire brigade. - Page 192 of pdf, section D.III.3.2.3.2, assumption 4. Regarding drills and exercises of the onsite fire brigade: explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade and content. - Page 192 of pdf, section D.III.3.2.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content.
IT-E-1116 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Latina NPP Magnox |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1117 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Latina NPP Magnox | Page 171 of pdf, section D.I.3.4, and all the assumptions. Strengths and weaknesses are not clearly mentioned in the NAR, can you confirm that there are no strengths/weaknesses or otherwise mention them if there are any?
IT-E-1118 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Trino NPP PWR |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1119 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Trino NPP PWR | Page 180 of pdf, section D.II.3.4, and all the assumptions. Strengths and weaknesses are not clearly mentioned in the NAR, can you confirm that there are no strengths/weaknesses or otherwise mention them if there are any?
IT-E-1120 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Decommissioning | EUREX FCF |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1121 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Decommissioning | ESSOR RR |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1122 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | Lena Triga Mark II |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1123 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | Tapiro Fast neutron |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1124 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | Lena Triga Mark II |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1125 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | Tapiro Fast neutron |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1126 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Lena Triga Mark II |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
IT-E-1127 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Tapiro Fast neutron |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
IT-E-1128 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Research reactor | Lena Triga Mark II |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
IT-E-1129 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Research reactor | Tapiro Fast neutron |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
IT-E-1130 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | ESSOR-plant dry |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1131 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | ESSOR-plant dry | No further information given for /2/, /3/, /4/ sections. Please provide the further information for fire suppression.
IT-E-1132 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | ITREC-plant dry |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1133 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | ITREC-plant dry | No further information given for /2/, /3/, /4/ sections. Please provide the further information for fire suppression.
IT-E-1134 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | ESSOR-plant dry |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1135 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | ESSOR-plant dry | It needs to be clarified how access to the building is ensured in case of manual ff/ more than one access?
IT-E-1136 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | ESSOR-plant dry | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards.
IT-E-1137 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | ITREC-plant dry |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1138 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | ITREC-plant dry | /1/ it needs to be claryfied what is meant wit "mainly complies with the national standards.." -> what are the differences and why? /2/ p.65 it needs to be claryfied how the adequate capacity of water is ensured e.g. for high ambient temperatures, with regard to supply from Sinni River /2/no further information for seismic resistance Please provide the relevant information.
IT-E-1139 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | ITREC-plant dry | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards.
IT-E-1140 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | ESSOR-plant dry |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
IT-E-1141 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | ITREC-plant dry |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
IT-E-1142 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | ITREC-plant dry | p.65, 1 equipped vehicle on site for fire fighters. What is the replacement or how to deal with maintenance of this vehicle?
IT-E-1143 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | ESSOR-plant dry |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1144 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | ESSOR-plant dry | What are the main outcomes from the last inspections with attention on fire safety from 10/2022?
IT-E-1145 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | ITREC-plant dry |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1146 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | ITREC-plant dry | What are the main outcomes from the last inspections with attention on fire safety from 07/2023? B.I.2.1.5, p.73, It should be claryfied how necessary documents are kept up to date and how the information exchange between operator and egulator is ensured.
IT-E-1147 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | Avogadro AFR |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1148 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | Avogadro AFR | • When is the last spent fuel assembly planned to be transferred to France? • Clarify fire alarming system (where and how are fire alarms visible? How robust is the system? What technology is used?) As the actual fire prevention measures present at the facility are not described in the NAR, there is the need to provide linkage to detection and alarm systems situation (noting that the NAR acknowledges that they are ageing) and that a general review is recommended to verify the need for replacement is referred to (in page 27).
IT-E-1149 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | ESSOR-plant |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1150 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | ESSOR-plant | As the actual fire prevention measures present at the facility are not described in the NAR, there is the need to provide linkage to detection and alarm systems situation (noting that the NAR acknowledges that they are ageing) and that a general review is recommended to verify the need for replacement is referred to (in page 27).
IT-E-1151 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | ITREC-plant |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1152 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | ITREC-plant | • When is the new dry storage facility planned to be operational? When is the last spent fuel assembly planned to be transferred to the new dry storage under construction? • Clarify fire alarming system (where and how are fire alarms visible? How robust is the system? What technology is used?)
IT-E-1153 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | Avogadro AFR |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1154 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | ESSOR-plant |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1155 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | ESSOR-plant | p.97, B.II.3.2.2 Fire suppression, "no manual or automatic fire extinguishing systems" -> Are there not even fire extinguishers for manual firefighting?
IT-E-1156 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | ITREC-plant |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1157 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | Avogadro AFR |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
IT-E-1158 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | Avogadro AFR | Clarify whether there is an internal professional fire brigade or if it is a local but external fire brigade.
IT-E-1159 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | ESSOR-plant |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
IT-E-1160 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | ESSOR-plant | p.97, B.II.3.2.3.1., please explain how the national fire brigades (VVF) are involved in drills and describe how they are equipped with necessary material and vehicles? Please explain the "continous updating" in more details. How it is ensured that all stakeholders e.g. national fire brigades are kept to date?
IT-E-1161 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | ITREC-plant |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
IT-E-1162 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | ITREC-plant | Clarify whether there is an internal professional fire brigade or if it is a local but external fire brigade.
IT-E-1163 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - wet | Avogadro AFR |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1164 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - wet | ESSOR-plant |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1165 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - wet | ITREC-plant |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1166 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1167 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | Page 120 Section C.I.3.2.1 Topic 1 The NAR does not mention the Nuclear Safety Classification of the new fire detection system required in D2 -is there one? There is no detail provided for this new system regarding design standards (what is it designed against?) or will the system initiate any protective measures?
IT-E-1168 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | Page 120 Section C.I.3.2.1 Topic 2 There is also no detail regarding the emergency power arrangements (is there emergency power back up?), fire resistance of cables (are they fire resistant?), is the sytem hazard tolerant and what are the EMIT arrangements?
IT-E-1169 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Facility 2300 (Eurex) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1170 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Facility 2300 (Eurex) | Pages 128, 131 and 144 Sections C.II - IV.3.2.1 Topic 1 The NAR does not mention the Nuclear Safety Classification of the fire detection system -is there one? There is no detail provided for this system regarding design standards (what is it designed against?) or will the system initiate any protective measures?
IT-E-1171 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Facility 2300 (Eurex) | Pages 128, 131 and 144 Sections C.II - IV.3.2.1 Topic 2 There is also no detail regarding the emergency power arrangements (is there emergency power back up?), fire resistance of cables (are they fire resistant?), is the sytem hazard tolerant and what are the EMIT arrangements?
IT-E-1172 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | D2 storage facility (Eurex) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1173 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | NPS New tank park (Eurex) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1174 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Area 800 (Eurex) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1175 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Deposito OPEC2 |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
IT-E-1176 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Deposito OPEC2 | Page 155 Section C.VI.3.2.1 Topic 1 The NAR does not mention the Nuclear Safety Classification of the new fire detection system required in D2 -is there one? There is no detail provided for this new system regarding design standards (what is it designed against?) or will the system initiate any protective measures?
IT-E-1177 | AFP | IT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Deposito OPEC2 | Page Page 155 Section C.VI.3.2.1 Topic 2 There is also no detail regarding the emergency power arrangements (is there emergency power back up?), fire resistance of cables (are they fire resistant?), is the sytem hazard tolerant and what are the EMIT arrangements?
IT-E-1178 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1179 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | Page 120 Section C.I.3.2.2 Topic 2 The NAR does not explain why the fire suppression provisions are deemed adequate for the size of the potential fire (has this been determined?) or whether the suppression provisions are hazard tolerant e.g. against seismic events or combined hazards (has the system design considered the potential effects of hazards?).
IT-E-1180 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
IT-E-1181 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Facility 2300 (Eurex) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1182 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Facility 2300 (Eurex) | Pages 129 and 136 Sections C.II - III.3.2.2 Topic 2 The NAR does not explain why the fire suppression provisions are deemed adequate for the size of the potential fire (has this been determined?) or whether the suppression provisions are hazard tolerant e.g. against seismic events or combined hazards (has the system design considered the potential effects of hazards?).
IT-E-1183 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Facility 2300 (Eurex) | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
IT-E-1184 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | D2 storage facility (Eurex) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1185 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | D2 storage facility (Eurex) | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
IT-E-1186 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | NPS New tank park (Eurex) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1187 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Area 800 (Eurex) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1188 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Area 800 (Eurex) | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
IT-E-1189 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Deposito OPEC2 |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
IT-E-1190 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Deposito OPEC2 | Page 156 Section C.VI.3.2.2 Topic 2 The NAR does not explain whether the suppression provisions are hazard tolerant e.g. against seismic events or combined hazards (has the system design considered the potential effects of hazards?).
IT-E-1191 | AFP | IT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Deposito OPEC2 | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
IT-E-1192 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
IT-E-1193 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | D1-D2 waste storage facilities (Trino NPP site) | Page 121 Section C.I.3.2.3 Topic 3 The NAR does not discuss the EMIT arrangements for fire protection measures or how these are tracked. Also this section does not explain what measures are in place to ensure the operability of the fire protection measures. Please provide the relevant information.
IT-E-1194 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Facility 2300 (Eurex) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
IT-E-1195 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Facility 2300 (Eurex) | Page 199 - Section D.IV.3.2.3 Topic 3 The NAR does not discuss the EMIT arrangements for fire protection measures or how these are tracked. Also this section does not explain what measures are in place to ensure the operability of the fire protection measures. Little detail is provided with regard to emergency exercises and the training provided to the off-site fire brigade. Please provide the relevant information.
IT-E-1196 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | D2 storage facility (Eurex) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
IT-E-1197 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | NPS New tank park (Eurex) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
IT-E-1198 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Area 800 (Eurex) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
IT-E-1199 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Deposito OPEC2 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
IT-E-1200 | AFP | IT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Deposito OPEC2 | Page 157 Section C.VI.3.2.3 Topic 3 The NAR does not discuss the EMIT arrangements for fire protection measures or how these are tracked. Also this section does not explain what measures are in place to ensure the operability of the fire protection measures. Little detail is provided with regard to emergency exercises and the training provided to the off-site fire brigade. Please provide the relevant information.
IT-E-1201 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Waste | D1-D2 waste storage facilities (Trino NPP site) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1202 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Waste | Facility 2300 (Eurex) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1203 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Waste | D2 storage facility (Eurex) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1204 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Waste | NPS New tank park (Eurex) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1205 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Waste | Area 800 (Eurex) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
IT-E-1206 | AFP | IT | Active fire protection | Licensee and regulatory experience |  | Waste | Deposito OPEC2 |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
LT-E-1207 | FSA | LT | Fire safety analysis | Assumptions (TS 02.6) |  | Decommissioning | Ignalina RMBK | Which kind of improved methods proposed by western experts have been used for the not screened out rooms of IgnalinaNPP unit 2?
LT-E-1208 | FSA | LT | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Ignalina RMBK |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
LT-E-1209 | FSA | LT | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) | /2/ p.57: What is the final conclusion regarding crane fire (difficult to reach)? /2/ p.59: What is the accident liquidation plan?
LT-E-1210 | FSA | LT | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) | "It is mentined that cables in RU have flame retardant insulation so fire not able to spread ": How cables are considered in fire analysisi? Are there taken into account as a fire source?
LT-E-1211 | FSA | LT | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) | /2/ : p. 85 - Could you elaborate a bit more on (detailed) recommendations and safety improvement measures, e.g. in form of a list. Has a PSR been performed in 2020 and what was the outcome of it regarding the Fire safety analyses.
LT-E-1212 | FSA | LT | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Liquid Waste Storage Facilities (Building 151) | /2/ : p. 95: As stated in case of fire in Room 007, the smoke will lower the visbility, how do you ensure that the person using the fire extinguisher will see the fire and properly fight it. P. 98: A a PSR been performed in 2018 - what was the outcome of it regarding the Fire safety analyses.
LT-E-1213 | FSA | LT | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Bituminized waste Storage facility (Building 158) | /2/ : P. 118: A a PSR been performed in 2021 - what was the outcome of it regarding the Fire safety analyses.?
LT-E-1214 | FSA | LT | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Cemented waste Storage facility (Building 158/2) | P. 129: A a PSR been performed in 2018 - what was the outcome of it regarding the Fire safety analyses?
LT-E-1215 | FSA | LT | Fire safety analysis | Licensee and regulatory experience |  | Waste | Solid Waste Retrieval Facility (B2-2 project) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
LT-E-1216 | FSA | LT | Fire safety analysis | Licensee and regulatory experience |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
LT-E-1217 | FSA | LT | Fire safety analysis | Licensee and regulatory experience |  | Waste | Liquid Waste Storage Facilities (Building 151) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
LT-E-1218 | FSA | LT | Fire safety analysis | Licensee and regulatory experience |  | Waste | Bituminized waste Storage facility (Building 158) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
LT-E-1219 | FSA | LT | Fire safety analysis | Licensee and regulatory experience |  | Waste | Cemented waste Storage facility (Building 158/2) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
LT-E-1220 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Ignalina RMBK | *Page 145. Section 3.1.2. Overview of arrangements for management and control of fire load and ignition sources. Assumtpion 3/. REGARDING HOT WORK. The NAR gives little information about this topic. Due to the dismantlig activities It is understood that hot works are carried out (or will be). Please, answer the following questions having into account the state of the facility (or indicate if it does not apply): -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) REGARDING FIRE LOADS. Please, answer the following questions having into account the state of the facility (or indicate if it does not apply): -> generic question. (The questions mainly refer to those areas where a possible fire could cause the release of radiation to the outside.) *Page 145. Section 3.1.3. Licensee’s experience of the implementation of the fire prevention. Assumption 4/. This section is not divided on the subsections indicated by TS (all this information is missing): 3.1.3.1 Overview of strengths and weaknesses. 3.1.3.2 Lessons learned from events, reviews fire safety related missions, etc. 3.1.3.3 Overview of actions and implementation status. Please provide information about the above. *Page 145. Section 3.1.4. Regulator’s assessment of the fire prevention. Assumption 5/. This section is not divided on the subsections indicated by TS (all this information is missing): 3.1.4.1 Overview of strengths and weaknesses. 3.1.4.2 Lessons learned from inspection and assesment on the fire prevention as part of its regulatory oversight. Please provide information about the above.
LT-E-1221 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Ignalina RMBK |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
LT-E-1222 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Ignalina RMBK | *Page 155. Section 3.3. Passive fire protection; 3.3.1. Prevention of fire spreading (barriers). Assumptions 1/ to 7/. This section is not divided into subsections like TS indicate: 3.3.1.1 Design approach. 3.3.1.2 Description of fire compartements and/or cells design and key features. 3.3.1.3 Performance assurance through lifetime. Very little information is given related to these sections. Please provide additional information on the above. Some specific questions are the following: Please provide a brief description of characteristics of fire barriers forming fire compartments (walls, ceilings, doors, penetrations...). What is the fire rate of boundaries? What is the fire-resistance of closures of openings? Are they the same as the ones for boundaries? (This questions mainly refer to those areas that contain SSCs important for safety) Are checks carried out on these elements to guarantee their proper functioning? Are the seals installed by qualified personnel and using certified materials? Are there currently fire-resistant barriers that are still necessary to prevent the release of radioactive material into the environment?, in that case: How is guaranteed that in the event of a fire there is no emission of smoke and contamination of radioactive material due to the remaining activity?. REGARDING ACCESS ROUTES Assumption 4/. Is not described how access routes for firefighting are maintained. Please, provide this information.
LT-E-1223 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Ignalina RMBK |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
LT-E-1224 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Ignalina RMBK | *Page 156. Section 3.3.2. Ventilation systems . The section is not divided into the following sections as indicated in the TS: 3.3.1.1 Desingn approach 3.3.1.2 Description of fire ocmpartments and/or cessa design and key features. 3.3.1.3 Performance assurance through lifetime. Some information about points 3.3.1.1 and 3.3.1.2 is given. But there is no information about 3.3.1.3 in the NAR. Please provide the missing information. *Page 156. Section 3.3.2. Ventilation systems .Assumption 1/. "Electrically operated dampers are installed on the collectors. The ventilation shutdown systems aim to reduce the consequences of a fire by automatically disconnecting the supply and exhaust fans to stop the air supply to the fire source." "removal of combustion products from protected areas (smoke removal)" How is smoke extraction guaranteed? Important in case of access and evacuation routes.
LT-E-1225 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Ignalina RMBK |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
LT-E-1226 | PFP | LT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Ignalina RMBK | *Page 157. Section 3.4. Licensee’s experience of the implementation of the fire protection concept. Assumtpion 1/. Strengths and weaknesses are not mentioned in the NAR. Please provide that information. *Page 158. Section 3.5. Regulator’s assessment of the fire protection concept and conclusions . Assumtpio 2/. Strengths and weaknesses are not clearly identified in the NAR. Please provide additional information and/or clarify this.
LT-E-1227 | PFP | LT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Ignalina RMBK |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
LT-E-1228 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | SNFSF - 1 | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: NAR section 3.1.1 Design considerations and prevention means" (and related subparagraphs): NAR section 3.1.2 Overview of arrangements for management and control of fire load and ignition sources" (and related subparagraphs) NAR section 3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) NAR section 3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) and relative subparaghraph. Please provide missing information on the above.
LT-E-1229 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | SNFSF - 1 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
LT-E-1230 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | SNFSF - 2 | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: NAR section 3.1.1 Design considerations and prevention means" (and related subparagraphs): NAR section 3.1.2 Overview of arrangements for management and control of fire load and ignition sources" (and related subparagraphs) NAR section 3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) NAR section 3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) and relative subparaghraph. Please provide missing information on the above (same as for SNFSF-1).
LT-E-1231 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | SNFSF - 2 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
LT-E-1232 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | SNFSF - 1 | Prevenction of fire spreading should be described as reported in the TS List of Detailed Contents - Annex 2. Some information is missing in the NAR. In particular related to: NAR section 3.3.1 Prevention of fire spreading" (and related subparagraphs) NAR section 3.3.2 Ventilation systems" (and related subparagraphs) NAR section 3.3.3 Licensee's experience of the implementation of passive fire protection" (and related subparagraphs) NAR section3.3.4 Regulator's assessment of passive fire protection" (and related subparagraphs) and almost all subparaghraph Please provide the missing information on the above.
LT-E-1233 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | SNFSF - 1 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
LT-E-1234 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | SNFSF - 2 | Prevenction of fire spreading should be described as reported in the TS List of Detailed Contents - Annex 2. Some information is missing in the NAR. In particular related to: NAR section 3.3.1 Prevention of fire spreading" (and related subparagraphs) NAR section 3.3.2 Ventilation systems" (and related subparagraphs) NAR section 3.3.3 Licensee's experience of the implementation of passive fire protection" (and related subparagraphs) NAR section3.3.4 Regulator's assessment of passive fire protection" (and related subparagraphs) and almost all subparaghraph Please provide the missing information on the above (same as for SNFSF-1).
LT-E-1235 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | SNFSF - 2 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
LT-E-1236 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | SNFSF - 1 | NAR section 3.3.2. (Ventilation system) pag. 156 --> Please clarify when the smoke removal is utilized? Why is it necessary to force air into the personell evacuation route? How does the ventilation system produce "forced air supply" and what is the logical application? Please provide more informations on the HEPA filter fire resistance.
LT-E-1237 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | SNFSF - 2 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
LT-E-1238 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | SNFSF - 2 | NAR section 3.3.2. (Ventilation system) pag. 156 --> Please clarify when the smoke removal is utilized? Why is it necessary to force air into the personell evacuation route? How does the ventilation system produce "forced air supply" and what is the logical application? Please provide more informations on the HEPA filter fire resistance.
LT-E-1239 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | SNFSF - 2 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
LT-E-1240 | PFP | LT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | SNFSF - 1 |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
LT-E-1241 | PFP | LT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | SNFSF - 2 |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
LT-E-1242 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) | -The prevention chapter is common for all type of nuclear installations. Please provide specific information for this waste installation. - section 3.1 for this installation is very sparse Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined? Also, please provide information on how fire prevention is ensured during the transportation and handling of radioactive waste and maintenance work
LT-E-1243 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
LT-E-1244 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) | Section 3.1 for this installation is very sparse Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined? Also, please provide information on how fire prevention is ensured during the transportation and handling of radioactive waste and maintenance work
LT-E-1245 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
LT-E-1246 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Liquid Waste Storage Facilities (Building 151) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
LT-E-1247 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Liquid Waste Storage Facilities (Building 151) | Section 3.1 for this installation is very sparse Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined? Also, please provide information on how fire prevention is ensured during the transportation and handling of radioactive waste and maintenance work
LT-E-1248 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Bituminized waste Storage facility (Building 158) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
LT-E-1249 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Bituminized waste Storage facility (Building 158) | Section 3.1 for this installation is very sparse Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined? Also, please provide information on how fire prevention is ensured during the transportation and handling of radioactive waste and maintenance work
LT-E-1250 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Cemented waste Storage facility (Building 158/2) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
LT-E-1251 | PFP | LT | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Cemented waste Storage facility (Building 158/2) | Section 3.1 for this installation is very sparse Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined? Also, please provide information on how fire prevention is ensured during the transportation and handling of radioactive waste and maintenance work
LT-E-1252 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) | the passive fire protection chapter is common for all type of nuclear installations. A specific chapter for this waste installation would be appreciated.
LT-E-1253 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) | Section 3.3 for this installation is very sparse Please provide information about compartmentatuion and other means of preventing fire spread. What are the fire ratings of said compartments?
LT-E-1254 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
LT-E-1255 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) | the passive fire protection chapter is common for all type of nuclear installations. A specific chapter for this waste installation would be appreciated.
LT-E-1256 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) | Section 3.3 for this installation is very sparse Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined?
LT-E-1257 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
LT-E-1258 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Liquid Waste Storage Facilities (Building 151) | the passive fire protection chapter is common for all type of nuclear installations. A specific chapter for this waste installation would be appreciated.
LT-E-1259 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Liquid Waste Storage Facilities (Building 151) | Section 3.3 for this installation is very sparse Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined?
LT-E-1260 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Liquid Waste Storage Facilities (Building 151) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
LT-E-1261 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Bituminized waste Storage facility (Building 158) | the passive fire protection chapter is common for all type of nuclear installations. A specific chapter for this waste installation would be appreciated.
LT-E-1262 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Bituminized waste Storage facility (Building 158) | Section 3.3 for this installation is very sparse Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined?
LT-E-1263 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Bituminized waste Storage facility (Building 158) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
LT-E-1264 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Cemented waste Storage facility (Building 158/2) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
LT-E-1265 | PFP | LT | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Cemented waste Storage facility (Building 158/2) | section 3.1 for this installation is very sparse Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined?
LT-E-1266 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) | Section 3.3 for this installation is very sparse Please provide information about the passive means of fire protection in a structured manner
LT-E-1267 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
LT-E-1268 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) | the passive fire protection chapter is common for all type of nuclear installations. A specific chapter for this waste installation would be appreciated.
LT-E-1269 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) | section 3.3 for this installation is very sparse Please provide information about the passive means of fire protection in a structured manner
LT-E-1270 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
LT-E-1271 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Liquid Waste Storage Facilities (Building 151) | the passive fire protection chapter is common for all type of nuclear installations. A specific chapter for this waste installation would be appreciated.
LT-E-1272 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Liquid Waste Storage Facilities (Building 151) | section 3.3 for this installation is very sparse Please provide information about the passive means of fire protection in a structured manner
LT-E-1273 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Liquid Waste Storage Facilities (Building 151) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
LT-E-1274 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Bituminized waste Storage facility (Building 158) | the passive fire protection chapter is common for all type of nuclear installations. A specific chapter for this waste installation would be appreciated.
LT-E-1275 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Bituminized waste Storage facility (Building 158) | section 3.3 for this installation is very sparse Please provide information about the passive means of fire protection in a structured manner
LT-E-1276 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Bituminized waste Storage facility (Building 158) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
LT-E-1277 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Cemented waste Storage facility (Building 158/2) | the passive fire protection chapter is common for all type of nuclear installations. A specific chapter for this waste installation would be appreciated.
LT-E-1278 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Cemented waste Storage facility (Building 158/2) | section 3.3 for this installation is very sparse Please provide information about the passive means of fire protection in a structured manner
LT-E-1279 | PFP | LT | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Cemented waste Storage facility (Building 158/2) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
LT-E-1280 | PFP | LT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Solid Waste Retrieval Facility (B2-2 project) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
LT-E-1281 | PFP | LT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
LT-E-1282 | PFP | LT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Liquid Waste Storage Facilities (Building 151) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
LT-E-1283 | PFP | LT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Bituminized waste Storage facility (Building 158) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
LT-E-1284 | PFP | LT | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Cemented waste Storage facility (Building 158/2) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
LT-E-1285 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Ignalina RMBK |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
LT-E-1286 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Ignalina RMBK | Page 146 of pdf, section 3.2.1, assumption 1. Are non-interruptible emergency power supplies available to feed the fire detection and alarm features? Explain these power supplies. - Page 146 of pdf, section 3.2.1, assumption 4. Explain the types of compensatory measures in case of impairment of fire detection systems.
LT-E-1287 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Ignalina RMBK |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
LT-E-1288 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Ignalina RMBK | Page 146 of pdf, section 3.2.2, assumption 2. Fire water pump stations and the fire protection water supply system are not described. Please describe electrical pumps and diesel-driven pumps; including flow and pressure, electrical supply, seismic category, separation between them and other relevant features. Also describe water tanks or other sources of supply; including their inventory, connections and other relevant features. - Page 146 of pdf, section 3.2.2, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain. - Page 146 of pdf, section 3.2.2, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to fire hoses/hydrants or any similar provision? - Page 146 of pdf, section 3.2.2, assumption 3. Explain in general the types of compensatory measures in case of impairment of fire suppression systems.
LT-E-1289 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Ignalina RMBK |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
LT-E-1290 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Ignalina RMBK |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
LT-E-1291 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Ignalina RMBK | Page 155 of pdf, section 3.2.4, and all the assumptions. Strengths and weaknesses are not clearly mentioned in the NAR, can you confirm that there are no strengths/weaknesses or otherwise mention them if there are any?
LT-E-1292 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | SNFSF - 1 |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
LT-E-1293 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | SNFSF - 1 | The Active fire protection part is not explicit for Spent fuel storage facilities. There are no dedicated paragaphs for these facilities. ---> Clarify whether the fire detection and suppression provisions in Chapter 3.2 also apply to SNFSF-1/2 installations. - Clarification is needed for: - Types, main characteristics and performance expectations (TS 3.2.1.2. - 3.2.2.2.) - Alternative/temporary provisions (TS 3.2.1.3. - 3.2.2.4.) Please provide the requested information.
LT-E-1294 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | SNFSF - 2 |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
LT-E-1295 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | SNFSF - 2 | The Active fire protection part is not explicit for Spent fuel storage facilities. There are no dedicated paragaphs for these facilities. ---> Clarify whether the fire detection and suppression provisions in Chapter 3.2 also apply to SNFSF-1/2 installations. - Clarification is needed for: - Types, main characteristics and performance expectations (TS 3.2.1.2. - 3.2.2.2.) - Alternative/temporary provisions (TS 3.2.1.3. - 3.2.2.4.) Please provide the requested information.
LT-E-1296 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | SNFSF - 1 |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
LT-E-1297 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | SNFSF - 1 | - The Active fire protection part is not explicit for Spent fuel storage facilities. There are no dedicated paragaphs for these facilities. ---> Clarify whether the fire detection and suppression provisions in Chapter 3.2 also apply to SNFSF-1/2 installations. - Clarification is needed for: - Types, main characteristics and performance expectations (TS 3.2.1.2. - 3.2.2.2.) - Management of harmful effects and consequential hazards (TS 3.2.2.3.) - Alternative/temporary provisions (TS 3.2.1.3. - 3.2.2.4.) Please provide the relevant information
LT-E-1298 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | SNFSF - 2 |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
LT-E-1299 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | SNFSF - 2 | The Active fire protection part is not explicit for Spent fuel storage facilities. There are no dedicated paragaphs for these facilities. ---> Clarify whether the fire detection and suppression provisions in Chapter 3.2 also apply to SNFSF-1/2 installations. Please provide the relevant information. - Clarification is needed for: - Types, main characteristics and performance expectations (TS 3.2.1.2. - 3.2.2.2.) - Management of harmful effects and consequential hazards (TS 3.2.2.3.) - Alternative/temporary provisions (TS 3.2.1.3. - 3.2.2.4.)
LT-E-1300 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | SNFSF - 1 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
LT-E-1301 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | SNFSF - 1 | The Active fire protection part is not explicit for Spent fuel storage facilities. There are no dedicated paragaphs for these facilities. ---> Clarification is needed for Administrative and organisational fire protection issues for the specific installation.
LT-E-1302 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | SNFSF - 2 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
LT-E-1303 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | SNFSF - 2 | The Active fire protection part is not explicit for Spent fuel storage facilities. There are no dedicated paragaphs for these facilities. ---> Clarification is needed for Administrative and organisational fire protection issues for the specific installation.
LT-E-1304 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | SNFSF - 1 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
LT-E-1305 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | SNFSF - 1 | Please clarify which is the 'Regulatory Authority Assessment of Active Fire Protection' for the facility. - Several events are mentioned in Chapter 3.4 ---> Please clarify which of these events concern facilities SNFSF-1/2
LT-E-1306 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | SNFSF - 2 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
LT-E-1307 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | SNFSF - 2 | Please clarify which is the 'Regulatory Authority Assessment of Active Fire Protection' for the facility. - Several events are mentioned in Chapter 3.4 ---> Please clarify which of these events concern facilities SNFSF-1/2
LT-E-1308 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
LT-E-1309 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
LT-E-1310 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Liquid Waste Storage Facilities (Building 151) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
LT-E-1311 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Bituminized waste Storage facility (Building 158) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
LT-E-1312 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Bituminized waste Storage facility (Building 158) | In bullet 2.2.4.3, it is not entirely clear which elements are responsible for detecting a fire in different rooms. Whether smoke detectors and visual control. It is not specified whether the fire safety system is safety-critical (its classification) and whether it can operate in conditions without electricity. It is also not clear whether Building 158/2 has an automatic fire extinguishing system. Please provide the relevant information.
LT-E-1313 | AFP | LT | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Cemented waste Storage facility (Building 158/2) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
LT-E-1314 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
LT-E-1315 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
LT-E-1316 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
LT-E-1317 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) | Paragraph 2.2.2.1 states that the SWMSF provides for the incineration of radioactive waste. In this regard, do you also consider the ignition of flammable radioactive waste as a fire scenario?
LT-E-1318 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
LT-E-1319 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Liquid Waste Storage Facilities (Building 151) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
LT-E-1320 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Liquid Waste Storage Facilities (Building 151) | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
LT-E-1321 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Bituminized waste Storage facility (Building 158) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
LT-E-1322 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Bituminized waste Storage facility (Building 158) | There is no data to substantiate the number of forces and means in the fire fighting part of the site. The amount and type of fire service forces and means should be justified depending on the type and scale of the hazards. Please provide the relevant information.
LT-E-1323 | AFP | LT | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Cemented waste Storage facility (Building 158/2) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
LT-E-1324 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
LT-E-1325 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Solid Waste Retrieval Facility (B2-2 project) | The names and legends of some of the figures have not been translated
LT-E-1326 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
LT-E-1327 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) | The names and legends of some of the figures have not been translated
LT-E-1328 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Liquid Waste Storage Facilities (Building 151) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
LT-E-1329 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Liquid Waste Storage Facilities (Building 151) | The names and legends of some of the figures have not been translated
LT-E-1330 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Bituminized waste Storage facility (Building 158) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
LT-E-1331 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Bituminized waste Storage facility (Building 158) | For the Cemented waste Storage facility (Building 158/2), various fire scenarios with source outside the building were considered, which was not done for Bituminized waste Storage facility (Building 158). Could you explain why different approaches are applied?
LT-E-1332 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Bituminized waste Storage facility (Building 158) | The names and legends of some of the figures have not been translated
LT-E-1333 | AFP | LT | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Cemented waste Storage facility (Building 158/2) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
LT-E-1334 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Waste | Solid Waste Retrieval Facility (B2-2 project) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
LT-E-1335 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
LT-E-1336 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Waste | Solid Waste Management and Storage Facilities (B3/4 project) | 2.2.2.3 in "Recommendations and safety improvement measures " is stated "After performing FHA for SWTSF some recommendations were proposed" and provided one example of recommendations. Could you provide other recomendations?
LT-E-1337 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Waste | Liquid Waste Storage Facilities (Building 151) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
LT-E-1338 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Waste | Bituminized waste Storage facility (Building 158) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
LT-E-1339 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Waste | Bituminized waste Storage facility (Building 158) | In bullet 2.2.4.5 it is noted that "VATESI reviewed the FHA report of the BWSF provided by SE Ignalina NPP in 2015. The FHA report provided recommendations for improving the fire safety of BWSF. VATESI constantly supervised the implementation of these recommendations until they were implemented." It may be useful to present key recommendations in this report.
LT-E-1340 | AFP | LT | Active fire protection | Licensee and regulatory experience |  | Waste | Cemented waste Storage facility (Building 158/2) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
NL-E-1341 | FSA | NL | Fire safety analysis | Licensee and regulatory experience |  | NPP | Borssele |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
NL-E-1342 | FSA | NL | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | High Flux Reactor (HFR) | to ch. 2.2.4, p. 55: The total contribution of fire events to the CDF is 1.2 10-8/year. In comparison, the total core damage frequency (TCDF) of the HFR is 4.7 10-7/year. The contribution of plant internal fires to the total core damage frequency of HFR is 2.5 %. Do you consider your Fire PSA to be conservative/realistic on a scale from 1-3 with 1 conservative, 3 realistic and 2 in between? In your Fire PSA, do you use failure probabilities for SSC being part of the fire protection, or do you merely use general assumptions, e.g. a complete burnout of the fire compatment and the failure of all SSC in that compartment, or assumptions that fire doors/dampers remain always functional?
NL-E-1343 | FSA | NL | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Hoger Onderwijs Reactor (HOR) |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
NL-E-1344 | FSA | NL | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | High Flux Reactor (HFR) |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
NL-E-1345 | FSA | NL | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) | A probabilistic fire analysis was performed for the Waste Storage Facility (WSF) but it is not clear if some general recommandations have conduced to modifications on WSF. Coul you clarify? No specific Fire Hazard Analysis has been done. Is it correct?
NL-E-1346 | FSA | NL | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) | p. 83: Why is it considered that "Fire ignition or fire propagation to the fire cell containing radioactive sources will directly lead to a full radioactive release om the building to the atmosphere. This is applicable when the fire cell containing the radioactive sources, does not have a complete barrier or.." if the cells are plugged or sealed. p. 88 ff: How are changes and modifications adressed, are PSRs perfomed?
NL-E-1347 | FSA | NL | Fire safety analysis | Licensee and regulatory experience |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
NL-E-1348 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel enrichment facilities | Uranium Enrichment Company | page 137 /Section 3.4.1.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
NL-E-1349 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel enrichment facilities | Uranium Enrichment Company | page137: Describe how hot work are performed under the work permit procedure?
NL-E-1350 | PFP | NL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel enrichment facilities | Uranium Enrichment Company | page 143/Section 3.4.3.1/1,2/What are fire-resistances for fire barriers (walls, fire doors, fire dampers...)? page 145/Section 3.4.3.2/3/ It is written the following sentence "Room ventilation systems are present in all buildings with radiological risks". Please provide more information about the ventilation system (dampers). Did you identified any deficiencies regarding ventilation systems? Describe improvements or modifications regarding ventilation systems. page 143/Section 3.4.3.1.2/1,2/Describe deficiencies regarding prevention of fire spreading (fire barriers)? Describe improvements or modifications regarding prevention of fire spreading (fire barriers).
NL-E-1351 | PFP | NL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel enrichment facilities | Uranium Enrichment Company |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
NL-E-1352 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Borssele |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
NL-E-1353 | PFP | NL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Borssele |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
NL-E-1354 | PFP | NL | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Borssele |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
NL-E-1355 | PFP | NL | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Borssele |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
NL-E-1356 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Hoger Onderwijs Reactor (HOR) | Please provide more information on the practise of temporary fire load management.
NL-E-1357 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Hoger Onderwijs Reactor (HOR) |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
NL-E-1358 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | High Flux Reactor (HFR) | Please provide more information on the practise of temporary fire load management.
NL-E-1359 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | High Flux Reactor (HFR) |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
NL-E-1360 | PFP | NL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Hoger Onderwijs Reactor (HOR) | How are the fire classes for fire barriers defined?
NL-E-1361 | PFP | NL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Hoger Onderwijs Reactor (HOR) |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
NL-E-1362 | PFP | NL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | High Flux Reactor (HFR) | How are the fire classes for fire barriers defined?
NL-E-1363 | PFP | NL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | High Flux Reactor (HFR) |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
NL-E-1364 | PFP | NL | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Hoger Onderwijs Reactor (HOR) | Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers? (p130: The ventilation system has two isolation valves (no separate fire-dampers are installed) in series in the inlet duct and two isolation valves in series in the outlet duct.).
NL-E-1365 | PFP | NL | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Hoger Onderwijs Reactor (HOR) |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
NL-E-1366 | PFP | NL | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | High Flux Reactor (HFR) | Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers? (p116: "In case of fire in a charcoal filter of the nuclear ventilation system the high pressure extinguishing system can be manually coupled to the filter for extinguishing the fire.)
NL-E-1367 | PFP | NL | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | High Flux Reactor (HFR) |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
NL-E-1368 | PFP | NL | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Hoger Onderwijs Reactor (HOR) |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
NL-E-1369 | PFP | NL | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | High Flux Reactor (HFR) |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
NL-E-1370 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | HABOG | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: NAR section 3.1.1 Design considerations and prevention means" (and related subparagraphs): NAR section 3.1.2 Overview of arrangements for management and control of fire load and ignition sources" (and related subparagraphs) NAR section 3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) NAR section 3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) and relative subparaghraph. Please provide missing information on the above.
NL-E-1371 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | HABOG |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
NL-E-1372 | PFP | NL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | HABOG | Prevenction of fire spreading should be described as reported in the TS List of Detailed Contents - Annex 2. Some information is missing in the NAR. In particular related to: NAR section 3.3.1 Prevention of fire spreading" (and related subparagraphs) NAR section 3.3.2 Ventilation systems" (and related subparagraphs) NAR section 3.3.3 Licensee's experience of the implementation of passive fire protection" (and related subparagraphs) NAR section3.3.4 Regulator's assessment of passive fire protection" (and related subparagraphs) and almost all subparaghraph Please provide the missing information on the above.
NL-E-1373 | PFP | NL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | HABOG |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
NL-E-1374 | PFP | NL | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | HABOG | Please describe the oxigen (if present) is reduced and the fire estinguishing systems. Could you clarify if the ventilation is partially independent, so to surround the fire zone? Could you give more informations on the HEPA filter fire resistance?
NL-E-1375 | PFP | NL | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | HABOG |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
NL-E-1376 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
NL-E-1377 | PFP | NL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) | Fire prevention and passive fire protection does not appear explicitly covered for WSF in the Fire protection concept section - considerations in section 3.6.2 page 159 largely relate to fire detection and alarm and extinguishing systems. Please provide the fire prevention and passive fire protection considerations, or confirm if considerations in section 3.2.1.1 and 3.2.1.1 apply to WSF. Section 3.2.3.1.2 does not appear to include WSFs - Please confirm if/ how this is covered.
NL-E-1378 | PFP | NL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
NL-E-1379 | PFP | NL | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
NL-E-1380 | PFP | NL | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
NL-E-1381 | AFP | NL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Borssele |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
NL-E-1382 | AFP | NL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Borssele | Page 87-89 Section 3.1.2.1 Topic 1 - no detail of nuclear safety class of the fire detection and alarm system is provided. Please clarify if the system has a nuclear safety class.
NL-E-1383 | AFP | NL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Borssele | Page 88 of pdf, section 3.1.2.1.1, assumption 1. In general, are SSC important to safety covered by fire detectors? If not, please explain. - Page 89 of pdf, section 3.1.2.1.2, assumption 4. Explain in general the procedures established for the examination, inspection, maintenance and testing of fire detection and alarm features.
NL-E-1384 | AFP | NL | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Borssele |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
NL-E-1385 | AFP | NL | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Borssele | Page 89-92 Section 3.1.2.2 Topic 1 - no detail of nuclear safety class of the fire suppression systems or the standards against which they were designed. What capacity is required of the suppression systems? Has consideration been given to the accessibility of the plant for manual fire fighting? Please could you provide clarification on these issues?
NL-E-1386 | AFP | NL | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Borssele | Page 91 of pdf, section 3.1.2.2.2, assumption 2. Explain if the fire ring include a double supply to buildings containing safety related SSC’s; and if this ring have isolation valves, the aim being to be able to isolate part of the main ring for maintenance or repair. - Page 91 of pdf, section 3.1.2.2.2, assumption 2. It is stated that the high pressure extinguishing system uses 1 water tank. Is there any redundancy (another tank or source of water) for this tank? - Page 91 of pdf, section 3.1.2.2.2, assumption 2. Seismic qualification of fire extinguishing systems. Is the low pressure extinguishing system (tank, pumps, pipes, suppression systems) seismically qualified for SSE? For the high pressure extinguishing system it is said: “The part of the high pressure system in the nuclear area is seismically qualified. The pumps however (built in in the electric building) are not seismically qualified. Therefore, in case of a seismic incident, a fire truck or a mobile pump can supply water into the high pressure system of the reactor building”. Which tank or source of water (seismically qualified) can be used for this arrangement? For fire hoses: in the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown? In general: how does the fire brigade suppress fires in the event of a SSE? Are there other fire extinguishing provisions qualified against seismic events? - Page 92 of pdf, section 3.1.2.2.3, assumption 4. Clarify if flooding is considered regarding management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems. - Page 92 of pdf, section 3.1.2.2.4, assumption 3. Explain in general the types of compensatory measures in case of impairment of fire suppression systems (additional to pumps’ impairment).
NL-E-1387 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Borssele |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
NL-E-1388 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Borssele | Page 93-100 Section 3.1.2.3 Topic 5 - Are on-plant personnel trained to use fire extinguishers? Should the need arise to call on the government fire brigade, what are the criteria for calling them, will they be familiar with the site, have they been involved in exercises on the site? Please could you provide clarification on these issues?
NL-E-1389 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Borssele | Page 95 of pdf, section 3.1.2.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. The six normative fire scenarios are very well described, but it is not clear for other fire areas. - Page 94 of pdf, section 3.1.2.3.2, assumption 4. “The Kew-licence states that an adequately trained, equipped, and thus a skilled firefighting team must be permanently available for the KCB”. Explain the training, organisation, minimum knowledge and physical conditions of the fire brigade.
NL-E-1390 | AFP | NL | Active fire protection | Licensee and regulatory experience |  | NPP | Borssele |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
NL-E-1391 | AFP | NL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | Hoger Onderwijs Reactor (HOR) |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
NL-E-1392 | AFP | NL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | Hoger Onderwijs Reactor (HOR) | What are the key features / technology of the fire detection alarm system? Fire detection cable failure arrangements? How independence between fire detection systems in adjacent compartments is achieved?
NL-E-1393 | AFP | NL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | High Flux Reactor (HFR) |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
NL-E-1394 | AFP | NL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | High Flux Reactor (HFR) | Detection system: adressable or not ? Same question about the system in place. Please describe the detection system in more details.
NL-E-1395 | AFP | NL | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | Hoger Onderwijs Reactor (HOR) |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
NL-E-1396 | AFP | NL | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | Hoger Onderwijs Reactor (HOR) | NAR p124: “For experimental assemblies (used by research reactors), no specific extinguisher equipment would be needed due to the type and design of the installations. The design of these experiments are within the scope of the present provisions installed in the fire compartments/cells.” To be clarified. No radioactivity contained in any experiment (fission products, …)? Experiments never increase fire risks? •How secondary hazards from actuation or rupture of fire extinguishing systems have been considered? •Please clarify why, for fire suppression in Main Control Room (MCR), only manual powder extinguishers are used… This could damage the I&C due to the corrosion by the powder.
NL-E-1397 | AFP | NL | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | High Flux Reactor (HFR) |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
NL-E-1398 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Hoger Onderwijs Reactor (HOR) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
NL-E-1399 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Hoger Onderwijs Reactor (HOR) | • Staffing of first responders and of the internal emergency response fire service (BHV-b)? Around the clock arrangements? • criteria for deploying onsite and offsite firefighting resources? • how coordination is achieved between the plant personnel and the offsite fire brigades? • how it is ensured that the firefighting resources (including the external fire brigades) are familiar with the hazards of the plant, and adequate time for security control is provided?
NL-E-1400 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | High Flux Reactor (HFR) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
NL-E-1401 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | High Flux Reactor (HFR) | Section 3.2.2.2.3 It would be appropriate to specify which types of fire extinguishers are used to extinguish various types of equipment.
NL-E-1402 | AFP | NL | Active fire protection | Licensee and regulatory experience |  | Research reactor | Hoger Onderwijs Reactor (HOR) |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
NL-E-1403 | AFP | NL | Active fire protection | Licensee and regulatory experience |  | Research reactor | High Flux Reactor (HFR) |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
NL-E-1404 | AFP | NL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | HABOG |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
NL-E-1405 | AFP | NL | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | HABOG |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
NL-E-1406 | AFP | NL | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | HABOG | (TS 3.2.1.3. and 3.2..2.4 Alternative/temporary provisions) pag. 151 ---> Please highlight weaknesses and any related improvement measures.
NL-E-1407 | AFP | NL | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | HABOG | TS 3.2.2, p.151, /3/ 3.5.2.2.3 The electrical cabinet is mentioned as a point of interest after extinguish activation. Needs to be claryfied for planned operation and for inadvertent operation. /5/ p.152, it needs to be claryfied how the access into the building is ensured, not only the building itself.
NL-E-1408 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | HABOG |  | p.152 3.5.2.3.2 how often are the periodic excercises and how are they organised?
NL-E-1409 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | HABOG | TS 3.2.3.1. Overview of firefighting strategies, administrative arrangements and assurance ---> para. 3.5.2..3.1 pag. 152 - Considering that "...is also not required to have an internal fie brigade…." ---> Please clarify how the external command is contacted and its ability to intervene. ---> Please highlight weaknesses and any related improvement measures.
NL-E-1410 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | HABOG |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
NL-E-1411 | AFP | NL | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | HABOG |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
NL-E-1412 | AFP | NL | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | HABOG | Active Fire Protection /1/ p.155, 3.5.4.2 what is the timeline for improvement of the suggestions from insurance company?
NL-E-1413 | AFP | NL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
NL-E-1414 | AFP | NL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) | /1/ (p. 158): "In the WSF, fire detectors are installed in four places and connected to the central alarm station." What is meant by "four places"?
NL-E-1415 | AFP | NL | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
NL-E-1416 | AFP | NL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
NL-E-1417 | AFP | NL | Active fire protection | Licensee and regulatory experience |  | Waste | High Flux Reactor (HFR) Waste Storage Facility (WSF) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
PL-E-1418 | FSA | PL | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Maria, Świerk | 2.3, p19 It is stated in the NAR that a PSA is performed. What is the fire contribution ? Do you consider your Fire PSA to be conservative/realistic on a scale from 1-3 with 1 conservative, 3 realistic and 2 in between? Do you consider spurious actuation due to fire? In your Fire PSA, do you use failure probabilities for SSCs being part of the fire protection features, or do you merely use general assumptions, e.g a complete burnout of the fire compatment and the failure of all SSC in that compartment, or assumptions that fire doors / fire dampers remain always functional?
PL-E-1419 | FSA | PL | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | Maria, Świerk | 1 - It is stated that "comprehensive probabilistic fire safety analyses were not conducted due to the low risk to nuclear safety and radiological protection posed by fires in the MARIA reactor". Does in mean that a Level 1 PSA has been performed or just risk assessment for compatibility or something else? How was the "low risk for nuclear safety" from fires defined? [page 19][Section 2.2][Assumption 5/]
PL-E-1420 | FSA | PL | Fire safety analysis | PSR and modifications |  | Research reactor | Maria, Świerk | 1 - Could you please give an overview of corrective actions in organisational aspects of fire protection identified in the PSR in 2019? [page 20]Section 2.5.1][topic 1/ 2/] 2 - The information on fire upgrades and fire safety analysis upgrades before the establishment of NCBJ have not been provided. Were any upgrades of fire protection implemented in the period from commissioning to 2011 and how were they managed in the safety analysis? [page 20][Section 2.6.1][topic 1/]
PL-E-1421 | FSA | PL | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Maria, Świerk | 1 - How often is the periodic inspection related to fire protection in the scope conducted? [page 22][Section 2.7.2] [topic 2/]
PL-E-1422 | FSA | PL | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | Maria, Świerk |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
PL-E-1423 | PFP | PL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Maria, Świerk | Please provide more information on the practise of temporary fire load management.
PL-E-1424 | PFP | PL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Maria, Świerk | It is mentioned buildings and reactor installations were designed according to old standards. (page 41) Which old standarts were used and what is the improvement plan in the short term?
PL-E-1425 | PFP | PL | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | Maria, Świerk |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
PL-E-1426 | PFP | PL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Maria, Świerk | How are the fire classes for fire barriers defined?
PL-E-1427 | PFP | PL | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | Maria, Świerk |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
PL-E-1428 | PFP | PL | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Maria, Świerk | Specify the dispositions implemented for iodine filter protection in case of fire?
PL-E-1429 | PFP | PL | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | Maria, Świerk |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
PL-E-1430 | PFP | PL | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | Maria, Świerk |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
PL-E-1431 | AFP | PL | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | Maria, Świerk |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
PL-E-1432 | AFP | PL | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | Maria, Świerk |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
PL-E-1433 | AFP | PL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Maria, Świerk |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
PL-E-1434 | AFP | PL | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | Maria, Świerk | Sections 3.2.2.1, 3.2.2.2 Characteristics of the fire water supply piping (water consumption, which provides the water supply), information on fire extinguishers and their types are missing. Please provide the related information.
PL-E-1435 | AFP | PL | Active fire protection | Licensee and regulatory experience |  | Research reactor | Maria, Świerk |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
RO-E-1436 | FSA | RO | Fire safety analysis | Assumptions (TS 02.3) |  | Fuel fabrication facilities | Pitesti Plant | P29, why the deterministic analysis § addresses probabilistic aspects?
RO-E-1437 | FSA | RO | Fire safety analysis | Licensee and regulatory experience |  | Fuel fabrication facilities | Pitesti Plant |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Radiological/criticality consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. c) Criticality: How has the criticality aspect been taken into account in the analysis and the impact on the fire protection features. d) How have the radiological hazards (radiological, criticality) been taken into account in the development of the fire brigade procedures (onsite, offsite brigades)? 5. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 6. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 7. Results and revisions of the Fire Safety Analyses, additional analyses: Please provide details about: a) Treatment of modifications and changes in the installations as well as updates of the analysis should be addressed. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for fuel fabrication facilities in your country? 8. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
RO-E-1438 | FSA | RO | Fire safety analysis | Assumptions (TS 02.3) |  | Fuel fabrication facilities | Pitesti Plant | • §2.3.4 (p.27): indicates that the legal limits for operating personnel and population are not exceeded. For workers a limit of 20-100 mSv is mentioned for emergency situations, but for the public no values are given (only indicated that dose is below max for DBAs and AOOs without specifying these max values). It would be good to indicate the values for these limits.
RO-E-1439 | FSA | RO | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Cernavoda NPP Unit 1 | (p 19, ch 2.1.6.1.) Time schedule for the gap analysis and the resulting measures? Update of the FHA and the FSSA?
RO-E-1440 | FSA | RO | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Cernavoda NPP Unit 1 | (p 19, ch 2.1.6.1.) What is the time schedule for the gap analysis and the resulting measures and for the updates of the FHA and the FSSA?
RO-E-1441 | FSA | RO | Fire safety analysis | Licensee and regulatory experience |  | NPP | Cernavoda NPP Unit 1 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
RO-E-1442 | FSA | RO | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | TRIGA Research Reactor in Pitesti | Are there any plans for probabilistic fire safety analysis?
RO-E-1443 | FSA | RO | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | TRIGA Research Reactor in Pitesti | 1 - Can you please provide information on the plant operating states considered in fire safety analysis? [page 20][Section 2.2][assumption 2/] 2 - The NAR states that "Minor fires that may occur in the area of safety related equipment will be extinguished with portable extinguishers". Have these actions been comfirmed by exercise or training? [page 21][Section 2.2.2][assumption 2/]
RO-E-1444 | FSA | RO | Fire safety analysis | PSR and modifications |  | Research reactor | TRIGA Research Reactor in Pitesti | to ch. 2.2.5, p. 22: Any there any plans for updating the FHA from 2013?
RO-E-1445 | FSA | RO | Fire safety analysis | PSR and modifications |  | Research reactor | TRIGA Research Reactor in Pitesti | To p. 22, Section 2.2.7, topic 3/: How often is a PSR required by the Romanian regulation? To p. 20, Section 2.2.5, topic 1/: Can you provide information on fire safety improvements based on the results from the PSR in 2013?
RO-E-1446 | FSA | RO | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | TRIGA Research Reactor in Pitesti | 1 - How often is the periodic inspection related to fire protection in the scope conducted? Please outline the insights from the oversight activities if any [page 22][Section 2.2.7] [topic 2/]
RO-E-1447 | FSA | RO | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | TRIGA Research Reactor in Pitesti |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
RO-E-1448 | FSA | RO | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Radioactive waste storage related to Cernavoda Units 1 | p.31: What is considered the minor offsite impact? p.31: Which fire resistance tests of the waste drums are you relying on. Have 6h fire tests been performed with the drums?
RO-E-1449 | FSA | RO | Fire safety analysis | Licensee and regulatory experience |  | Waste | Radioactive waste storage related to Cernavoda Units 1 |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
RO-E-1450 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Pitesti Plant | consolidating with p.64, §3.1.2.C: Please clarify how the maximum allowed load was determined, how this compares with the actual load, and the practice for the management of temporary fire loads.
RO-E-1451 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Pitesti Plant |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
RO-E-1452 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | Pitesti Plant | p..70, §3.3.1.2.C : Fire resistance of walls and doors is not the same (doors always less than the walls), nothing is said about fire resistance of penetration seals. And in §3.3.2.C pipes of ventilation systems are 90 min fire resistant (thus also less than the walls they pass through). To clarify, what is the minimal required fire resistance based on and why is the fire resistance of doors or penetrations (compared to walls) not identified as a weakness?
RO-E-1453 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | Pitesti Plant | How are the fire classes for fire barriers defined? Are air damper as resistant as the wall/door of the fire compartment in which they are included?
RO-E-1454 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | Pitesti Plant |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
RO-E-1455 | PFP | RO | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Pitesti Plant | p.70 §3.3.2.C : The confinement strategy should be clarified. How is the remote shutdown of the ventilation system initiated in case of fire (automatically/manually, via fire detection system, alarm to control room, ..)? It is not clear what is to be understood by 'shutdown of the ventilation system': the whole ventilation system of the building or just the part in the concerned zone with fire? Shutdown of the air inlet, the extraction or both sides? It seems that fire dampers are only triggered by fuses, which would mean that air inlet/extraction to/from the fire zone would only be isolated if enough heat reached this fire dampers.
RO-E-1456 | PFP | RO | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Pitesti Plant |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
RO-E-1457 | PFP | RO | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Fuel fabrication facilities | Pitesti Plant |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
RO-E-1458 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Cernavoda NPP Unit 1 | page 34/Section 3.1.2.A/3/How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
RO-E-1459 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Cernavoda NPP Unit 2 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
RO-E-1460 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Cernavoda NPP Unit 1 | page 42/Section 3.3.1.2A/1,2,4/ It is written the following sentence "The fire protection barriers must fulfill their function in the event of a fire, maintaining their stability, tightness and thermal insulation capacity for the prescribed time, depending on the density of the thermal load. Therefore, any penetration of the barriers must not affect their fire resistance. The penetrations of the barriers for the passage of cables and pipes must be sealed". Were there any non-compliances regarding design of fire barriers, stability, access routes for firefighting identified?
RO-E-1461 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Cernavoda NPP Unit 1 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
RO-E-1462 | PFP | RO | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Cernavoda NPP Unit 1 | page 46/Section 3.3.2.1.A/1/ In next sentence is written "Ventilation systems are provided for all buildings where safety-related SSC are located". Which buildings and SSCs are without ventilation systems"? /Section 3.3.2.1.A/2/ How are the ventilation systems in fire compartments separating redundant trains? /Section 3.3.2.1.A/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences? /Section 3.3.2.1.A/3/ Describe the case where a ventilation system serves more than one fire compartments to prevent the spread of fire?
RO-E-1463 | PFP | RO | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Cernavoda NPP Unit 1 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
RO-E-1464 | PFP | RO | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Cernavoda NPP Unit 1 | page 43/Section 3.4.A/1/ Did you have OSART and WANO missions?...What were lessons learnt from OSART and WANO missions? Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
RO-E-1465 | PFP | RO | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Cernavoda NPP Unit 1 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
RO-E-1466 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | TRIGA Research Reactor in Pitesti | Please provide more information on the practise of temporary fire load management.
RO-E-1467 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | TRIGA Research Reactor in Pitesti | It is mentioned that procedures are in place to prevent the accumulation of combustible materials in areas where SSC important to safety are located. Also, procedures are enforced for the control of work and equipment that could constitute ignition sources. Are there specific criteria to implement those procedures?
RO-E-1468 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | TRIGA Research Reactor in Pitesti |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
RO-E-1469 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | TRIGA Research Reactor in Pitesti | How are the fire classes for fire barriers defined?
RO-E-1470 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | TRIGA Research Reactor in Pitesti |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
RO-E-1471 | PFP | RO | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | TRIGA Research Reactor in Pitesti | Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers? How is the ventilation stopped if a fire occurs? (manual or automatic closure) : P62: "The ventilation system related to the main building of the reactor stops in case of fire, to prevent the spread of smoke and fire and to increase passive fire protection
RO-E-1472 | PFP | RO | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | TRIGA Research Reactor in Pitesti |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
RO-E-1473 | PFP | RO | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | TRIGA Research Reactor in Pitesti |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
RO-E-1474 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage | Some topics for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: NAR section 3.1.3.1 Overview of strengths and weaknesses" NAR section 3.1.3.2 Lesson learned from events, reviews fire safety related missions etc." NAR section "3.1.3.3 Overview of actions and implementation status" NAR section 3.1.4.1 Overview of strengths and weaknesses in the fire prevention" NAR section "3.1.4.2 Lessons learned from inspection and assessment on the fire prevention as part of its regulatory oversight" Please provide missing information on the above. NAR Section 3.1D pag. 73-->How the following topics have been taken into consideration, in relation to fire prevention: the combustible material (fire load), ignition source (ignition temperature) and oxygen (concentration)? NAR section 3.1.1.D pag.73 -> Could you provide more information on design considerations and means of intervention? NAR Section 3.1.2.D pag.73 -> Are there hydrogen detectors in the system?
RO-E-1475 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
RO-E-1476 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage | Some topics for the "Passive fire Protection" are not present (see List of detailed contents for the TS - annex 2), in particular: fire spreading (barriers)" (and related subparagraphs) Please provide the missing information on the above.
RO-E-1477 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
RO-E-1478 | PFP | RO | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage | Some topics for the "Passive fire Protection" are not present (see List of detailed contents for the TS - annex 2), in particular: NAR section 3.3.2 Ventilation system" (and related subparagraphs) Please provide the missing information.
RO-E-1479 | PFP | RO | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
RO-E-1480 | PFP | RO | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
RO-E-1481 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Radioactive waste storage related to Cernavoda Units 1 | Section 1.1.3.3; P.3-4. Please explain whether solid radioactive waste interim storage facility is designed only for storage of low and intermediate radioactive waste or also to high radioactive waste, as it is stated that structure no. 3 (Quadricell) is a concrete structure for highly contaminated pieces of equipment. Section 3.1.2.E; P.75. Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined? Section 3.1.3.2.E; P.76. Please provide more detailed information about several improvements implemented in the area of hot works preparation and authorization.
RO-E-1482 | PFP | RO | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Radioactive waste storage related to Cernavoda Units 1 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
RO-E-1483 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Radioactive waste storage related to Cernavoda Units 1 | Section 3.3.1.E; P.77. Please provide information how access routes for firefighting are maintained. Section 3.3.1.E; P.77. Please provide information about fire compartmentation of radioactive waste storage.
RO-E-1484 | PFP | RO | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Radioactive waste storage related to Cernavoda Units 2 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
RO-E-1485 | PFP | RO | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Radioactive waste storage related to Cernavoda Units 1 | Section 3.3.2.E; P.77; (5). Since there is natural ventilation, please indicate what measures are planned to prevent the spread of fire through it.
RO-E-1486 | PFP | RO | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Radioactive waste storage related to Cernavoda Units 2 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
RO-E-1487 | PFP | RO | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Radioactive waste storage related to Cernavoda Units 1 |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
RO-E-1488 | AFP | RO | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Cernavoda NPP Unit 1 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
RO-E-1489 | AFP | RO | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Cernavoda NPP Unit 1 | • Please provide more details on the fire detection systems key features / technology used and their cable failure arrangements. • Please clarify the approaches to assure that the fire detection and alarm systems are capable to withstand the relevant hazard conditions, in particular their resistance level against earthquake (considering the relatively high regional seismicity). • Please provide more details on how independence between fire detection systems in adjacent compartments is achieved • (p.18) Chapter 2.1.5.2 of the NAR provides a long list of decided improvements to fire detection and suppression. To be clarified which are already implemented and which not .
RO-E-1490 | AFP | RO | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Cernavoda NPP Unit 1 | Page 37-38 Section 3.2.1A Topic 1 - Please provide detail of the safety class of the fire detection systems.
RO-E-1491 | AFP | RO | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Cernavoda NPP Unit 1 | Section 3.2.1.2 Absence of requirements for seismic resistance of the fire alarm system.
RO-E-1492 | AFP | RO | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Cernavoda NPP Unit 1 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
RO-E-1493 | AFP | RO | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Cernavoda NPP Unit 1 | (p.39) “Fire extinguishing systems with sprayed water and automatic sprinkler systems are provided in plant areas and compartments where there is a substantial risk of fire.” Where is this exactly? Is the reactor building equipped with fixed automatic or distance-operable extinguishing system? • (p.39) “Fire extinguishing systems with INERGEN are used for computer rooms and other areas where water extinguishing systems are not suitable for use.” Clarify whether all safety-class I&C rooms are protected by this or something else? Are the main control room and the SCA protected by this? How are electrical equipment protected more broadly? • Please clarify key design characteristics of the fire extinguishing provisions including seismic resistance. • (p.18) Chapter 2.1.5.2 of the NAR provides a long list of decided improvements to fire detection and suppression. To be clarified which are already implemented and which not •(p.39) No fire hydrants yet installed in the Reactor Building of Unit 1. “Internal fire hydrants and piping will be installed during refurbishment”. When is this planned exactly? " "• (p.8) “As regards the consideration of combinations of fire events and earthquake events, such combinations have not been considered in the analysis, because the design of the plant is such that systems or components containing large quantities of flammable liquids or gases are seismically qualified or have been separated from essential safety related systems by a qualified barrier.” This does not seem to be a very robust approach, as demonstrated by international operating experience feedback. The fire detection and fire suppression functions would still need to be ensured in this scenario. • (p.39) No fire hydrants yet installed in the Reactor Building of Unit 1. “Internal fire hydrants and piping will be installed during refurbishment”. (When is this planned exactly?) As indicate on p.18, a large number of other significant improvements to fire detection and suppression are also still pending implementation. " • (p.38) The site has a high-capacity backup diesel-driven pump to supply (filtered) water from the Danube to the site fire water ring network. • (p.39) “Fire extinguishing systems with sprayed water and automatic sprinkler systems are provided in plant areas and compartments where there is a substantial risk of fire.” Where is this exactly? Is the reactor building equipped with fixed automatic or distance-operable extinguishing system? • (p.39) “Fire extinguishing systems with INERGEN are used for computer rooms and other areas where water extinguishing systems are not suitable for use.” Clarify whether all safety-class I&C rooms are protected by this or something else? Are the main control room and the SCA protected by this? How are electrical equipment protected more broadly? • Please clarify key design characteristics of the fire extinguishing provisions including seismic resistance. • (p.18) Chapter 2.1.5.2 of the NAR provides a long list of decided improvements to fire detection and suppression. To be clarified which are already implemented and which not •(p.39) No fire hydrants yet installed in the Reactor Building of Unit 1. “Internal fire hydrants and piping will be installed during refurbishment”. When is this planned exactly? " "• (p.8) “As regards the consideration of combinations of fire events and earthquake events, such combinations have not been considered in the analysis, because the design of the plant is such that systems or components containing large quantities of flammable liquids or gases are seismically qualified or have been separated from essential safety related systems by a qualified barrier.” This does not seem to be a very robust approach, as demonstrated by international operating experience feedback. The fire detection and fire suppression functions would still need to be ensured in this scenario. • (p.39) No fire hydrants yet installed in the Reactor Building of Unit 1. “Internal fire hydrants and piping will be installed during refurbishment”. (When is this planned exactly?) As indicate on p.18, a large number of other significant improvements to fire detection and suppression are also still pending implementation. " • (p.38) The site has a high-capacity backup diesel-driven pump to supply (filtered) water from the Danube to the site fire water ring network. • (p.39) “Fire extinguishing systems with sprayed water and automatic sprinkler systems are provided in plant areas and compartments where there is a substantial risk of fire.” Where is this exactly? Is the reactor building equipped with fixed automatic or distance-operable extinguishing system? • (p.39) “Fire extinguishing systems with INERGEN are used for computer rooms and other areas where water extinguishing systems are not suitable for use.” Clarify whether all safety-class I&C rooms are protected by this or something else? Are the main control room and the SCA protected by this? How are electrical equipment protected more broadly? • Please clarify key design characteristics of the fire extinguishing provisions including seismic resistance. • (p.18) Chapter 2.1.5.2 of the NAR provides a long list of decided improvements to fire detection and suppression. To be clarified which are already implemented and which not •(p.39) No fire hydrants yet installed in the Reactor Building of Unit 1. “Internal fire hydrants and piping will be installed during refurbishment”. When is this planned exactly?
RO-E-1494 | AFP | RO | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Cernavoda NPP Unit 1 | Page 38-39 Section 3.2.2A Topic 1 - no detail of the safety class of the fire suppression systems or the standards to which they were designed. There is not much detail on the suppression system characteristics such as the layout or coverage of the systems. Has consideration been given to the accessibility of the facilities for manual fire fighting? Please could more detail or clarification be provided in these areas?
RO-E-1495 | AFP | RO | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Cernavoda NPP Unit 1 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
RO-E-1496 | AFP | RO | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Cernavoda NPP Unit 1 | • Clarify balance between fixed fire extinguishing and manual firefighting (there is almost no info about manual or portable fire extinguishers). Please also clarify how accessibility is ensured during manual firefighting (ventilation strategy, …). • Clarify firefighting capabilities, responsibilities and organisation, including criteria for deploying onsite and offsite firefighting resources, how coordination is achieved between the plant personnel and the offsite resources, where are the external brigades located and what is their capacity, how much time is needed for the external brigades to reach the place of fighting on site, etc. The NAR mentions that there is a professional firefighting brigade onsite but with few details, and no info about whether the onsite brigade is big enough for all scenarios or not. • Clarify how the firefighting strategy takes into account possible damaged offsite and onsite roads and infrastructure (earthquake, ...), making access difficult.
RO-E-1497 | AFP | RO | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Cernavoda NPP Unit 1 | Page 39-41 Section 3.2.3A Topic 1 and 5 - Do the on-site fire brigde require support from an off-site fire brigade and, if so, what are the criteria for contacting them and what training do they receive regarding the plant layout etc.? With what frequency are exercises and drills held?
RO-E-1498 | AFP | RO | Active fire protection | Licensee and regulatory experience |  | NPP | Cernavoda NPP Unit 1 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
RO-E-1499 | AFP | RO | Active fire protection | Licensee and regulatory experience |  | NPP | Cernavoda NPP Unit 1 | For a site with a relatively high regional seismicity, how are the lessons learned in the field of fire safety from past international events (such as the Kashiwazaki-Kariwa earthquake) taken into account?
RO-E-1500 | AFP | RO | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | TRIGA Research Reactor in Pitesti |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
RO-E-1501 | AFP | RO | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | TRIGA Research Reactor in Pitesti |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
RO-E-1502 | AFP | RO | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | TRIGA Research Reactor in Pitesti |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
RO-E-1503 | AFP | RO | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | TRIGA Research Reactor in Pitesti | Please could you elaborate on the organisation of the fire brigade
RO-E-1504 | AFP | RO | Active fire protection | Licensee and regulatory experience |  | Research reactor | TRIGA Research Reactor in Pitesti |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
RO-E-1505 | AFP | RO | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
RO-E-1506 | AFP | RO | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
RO-E-1507 | AFP | RO | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage | (TS 3.2.1.2.) Types, main characteristics and performance expectations , Pag. 73 ---> Considering that no automatic suppression systems are in place, please clarify whether other extinguishing systems are in place (e.g. manual/portable fire extinguishers). ---> Clarify whether at least an external (yard fire hydrants) fire extinguishing system is provided
RO-E-1508 | AFP | RO | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage | Clarify what documents and procedures are needed to conduct fire fighting.
RO-E-1509 | AFP | RO | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
RO-E-1510 | AFP | RO | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
RO-E-1511 | AFP | RO | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Cernavoda Spent Fuel Dry Interim Storage | Please provide additional information regarding the "Licensee and regulatory experience".
RO-E-1512 | AFP | RO | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Radioactive waste storage related to Cernavoda Units 1 |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
RO-E-1513 | AFP | RO | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Radioactive waste storage related to Cernavoda Units 1 | /1/ The waste storage facility on the NPP site is described in Ch. 2.5 of the NAR (PDF p. 33). Active fire protection is covered on less than one dedicated page of the NAR (PDF p. 79+). Much information asked for in the Tec. Spec. is missing. Please provide additional information in accordance with Technical Specification.
RO-E-1514 | AFP | RO | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Radioactive waste storage related to Cernavoda Units 1 |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
RO-E-1515 | AFP | RO | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Radioactive waste storage related to Cernavoda Units 1 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
RO-E-1516 | AFP | RO | Active fire protection | Licensee and regulatory experience |  | Waste | Radioactive waste storage related to Cernavoda Units 1 |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
SE-E-1517 | FSA | SE | Fire safety analysis | Assumptions (TS 02.3) |  | Fuel fabrication facilities | Westinghouse | §2.3: Unfortunately there is a lot of text not covering what should be covered under the different titles, while the needed info is often missing or too high level. Is it useful to ask Sweden again to fill in the needed paragraphs?
SE-E-1518 | FSA | SE | Fire safety analysis | Licensee and regulatory experience |  | Fuel fabrication facilities | Westinghouse |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Radiological/criticality consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. c) Criticality: How has the criticality aspect been taken into account in the analysis and the impact on the fire protection features. d) How have the radiological hazards (radiological, criticality) been taken into account in the development of the fire brigade procedures (onsite, offsite brigades)? 5. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 6. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 7. Results and revisions of the Fire Safety Analyses, additional analyses: Please provide details about: a) Treatment of modifications and changes in the installations as well as updates of the analysis should be addressed. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for fuel fabrication facilities in your country? 8. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
SE-E-1519 | FSA | SE | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Forsmark 2 | For fire phenomena analyses Ringhals refers to a methodology recommendation by Lund University (in 2.1.3.3, p. 47), and OKG mentions a guide SBF 72 (p. 39). Is Forsmark using these methodologies/guides? (3/)
SE-E-1520 | FSA | SE | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Forsmark 2 | 1) P. 30 vs 31, passive components are assumed to be affected by fires in deterministic assumptions, but unaffected in probabilistic assumptions. Is that correct? Then why to have different assumptions? 2) P. 31 (2.1.1.4) Clarify the reason why fires contribute to CDF in cold shutdown more than in power operation.
SE-E-1521 | FSA | SE | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Oskarshamn 3 | P. 38-39: For fire phenomena analyses Ringhals refers to a methodology recommendation by Lund University (in 2.1.3.3). Is Oskarshamn using this guide as well? (3/)
SE-E-1522 | FSA | SE | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Oskarshamn 3 | P.35 Plant fire frequency is uniformly distributed to compartments, but have you made any sensitivity study for the impact of this assumption? Have you compared room fire frequencies to any other data, e.g. from USA or OECD FIRE?
SE-E-1523 | FSA | SE | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Ringhals 3 | P. 47: Fire phenomena analyses of R3 follow a methodology of Lund University. OKG mentions a guide SBF 72 (p. 39), is the guidance of SBF 72 used also by Ringhals? (3/)
SE-E-1524 | FSA | SE | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Ringhals 3 | 1) Have you made any survey on open fire doors at Ringhals NPP to estimate probability for an open door? 2) Have you compared room fire frequencies (achieved with Berry method) to any other data, e.g. USA or OECD FIRE?
SE-E-1525 | FSA | SE | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Forsmark 2 | P. 32: The NAR states: "No periodic review is performed". Can you please clarify if there is no review of the FHA or the Fire PSA in connection to the PSR (as e.g. in case of Oskarshamn (p. 40))?
SE-E-1526 | FSA | SE | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Ringhals 3 | P. 51 (2.1.3.7) Plant modifications and additional procedures are mentioned and referred to see section R3.5 for more details. Is the correct section 3.3?
SE-E-1527 | FSA | SE | Fire safety analysis | Licensee and regulatory experience |  | NPP | Forsmark 2 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
SE-E-1528 | FSA | SE | Fire safety analysis | Licensee and regulatory experience |  | NPP | Oskarshamn 3 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
SE-E-1529 | FSA | SE | Fire safety analysis | Licensee and regulatory experience |  | NPP | Ringhals 3 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
SE-E-1530 | FSA | SE | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | CLAB | Depending on the prevailing ratio between probability and consequence, either the fire event can be considered acceptable, or safety measures need to be taken. Please provide more info of this "prevailing ratio" in terms of risk metrics or importance masures (e.g. Risk Reduction Worth RRW) What is the overall value of frequency of realese due to fire?
SE-E-1531 | FSA | SE | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | CLAB | P. 58 (2.4.3) Two redundant components are mentioned. What has been the design principle to separate the redundancies in the facility?
SE-E-1532 | FSA | SE | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | CLAB |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire safety analyses with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Inventory make-up: Please provide a higher level of detail on the systems used to make-up inventory. 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 5. Additional analyses: Please provide details about: a) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for spent fuel storage facilities in your country? b) Some countries mention that a periodic safety review is performed for spent fuel storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 6. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
SE-E-1533 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Westinghouse | p.104; §3.4.1.1, topic 2/ : Most of the means mentioned are not related to fire prevention but to fire protection (e.g. fire detection, alarms, manual and automatic extinguishing systems, fire ompartments,….). Specific list of means for fire prevention is missing. Please provide information on the above.
SE-E-1534 | PFP | SE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | Westinghouse | p.110,§3.4.4.1.2: Glass sections between workshops and office spaces are EI30, while the fire compartments in the workshops are minimum EI60. Why are glass sections with EI30 considered acceptable (since weak point in the compartment of the workshop)? Info on penetrations and seals fire resistance is missing. Please provide information on the above.
SE-E-1535 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Westinghouse | p.110, §3.4.4.2, topic 6/: Concernign the ventilation in rooms with fire: these rooms are isolated (air blowing side as well as air exhaust side), and that thus all contamination would be retained in the compartment itself, and thus no counting on filtering is necessary. Is this what is assumed in the fire risk analyses and calculation of the radiological consequences (information could not be found in part of fire safety analyses)? What is foreseen then to extinguish the fire in this room (access possible with smoke)?
SE-E-1536 | PFP | SE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Fuel fabrication facilities | Westinghouse | Please describe the timeframes and scope of SSM's updating of the regulations for nuclear facilities other than nuclear power; and whether there will be programmes of inspections and assessment by the regulator A fire occurred in the room for oxidation ovens on May 2, 2022. SSMs assessment (SSM2022-3901-1) - page 116 - what was the cause of the fire (direct and underlying causes) and what improvements have been introduced?
SE-E-1537 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Westinghouse | p.105, §3.4.1.2, topic 3/: Fire loads are said to be checked for compliance several times a day by a hired security company. Is this really several times a day, and on what basis is this hired person performing all these checks? Not clear what is meant by 'when renderings are carried out'. Is there no check by own personnel ? (the regulator later on seems to say there are regular walkdowns by personnel - see e.g. p.127, but the licensee does not mention this). Please clarify this. Also, please provide how permanent ignition sources are controlled.
SE-E-1538 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Westinghouse | Please provide the main considerations on how fire loads are managed, are there limits, what are they and are they linked to nuclear safety? How does fire loading inform design of passive and fire protection systems from a nuclear safety perspective? For example the report states the provision of EI 60 fire barriers in workshops and labs, and EI 30 fire barriers in offices. How is this linked to the fire loads? - page 114.
SE-E-1539 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Westinghouse | p.106, §3.4.1.3.3, topic 4/ : There is only one case of actions for a blocked escape route. Is this the most important one related to fire events and what is its link to actions in order to improve fire prevention?
SE-E-1540 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Westinghouse |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
SE-E-1541 | PFP | SE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | Westinghouse |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
SE-E-1542 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Westinghouse |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SE-E-1543 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Springfields Fuel Ltd |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SE-E-1544 | PFP | SE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Fuel fabrication facilities | Westinghouse |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
SE-E-1545 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Forsmark 2 | page 63/Section 3.1.1.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 63/Section 3.1.1.2/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
SE-E-1546 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Forsmark 2 | section 3.1.1.2: please provide information on the following aspects: - details of the hot work permit system (types of hot work, restrictions, duration) - information on permissible fire loads/limits - information on flammables/ combustibles excluded from the facilities, or design decisions to remove them from vulnerable areas (e.g. presence of flammable gases or liquids stores within building, routing of hydrogen or other flammable gases pipework; location and design of flammable and combustible inventories such as diesel inventories, lubricating oils... presence (or otherwise) or leak prevention measures etc.
SE-E-1547 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Forsmark 2 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
SE-E-1548 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Oskarshamn 3 | page 77/Section 3.2.1.2/3/Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 77/Section 3.2.1.2/ 3/How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
SE-E-1549 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Oskarshamn 3 | 3.2.1/3/ Could you describe the following topics in more detail: -process and requirements for hot work - information on flammables/ combustibles excluded from the facilities, or design decisions to remove them from vulnerable areas (e.g. presence of flammable gases or liquids stores within building, routing of hydrogen or other flammable gases pipework; location and design of flammable and combustible inventories such as diesel inventories, lubricating oils... presence (or otherwise) or leak prevention measures etc. 3.2.1.3.1/4/ What do you consider the plant unit's strenghts or weaknesses related to fire prevention?
SE-E-1550 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Oskarshamn 3 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
SE-E-1551 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Ringhals 3 | page 89/Section 3.3.1.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 89/Section 3.3.1.2/ 3/How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered?
SE-E-1552 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Ringhals 3 | 3.3.1/3/ Could you describe the main fire loads and their locations (related to safety related equipment) in more detail?
SE-E-1553 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Ringhals 3 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
SE-E-1554 | PFP | SE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Forsmark 2 | section 3.1.1.2: please provide information on the following aspects: - presence of fire barriers/ segregation between transformers? From the information provided it appears that redundant trains of safety systems are not fully segregated. Other than the improvements to electrical cabinets referred to in section 3.1.1.3.1, are there any other SSCs from redundant trains which are not fully segregated? Has additional segregation or improving fire rating of fire barriers considered? (page 77) Fire doors stated to be self-closing; are they alarmed to a permanently occupied location or locally? Is there implementation of lobbied door configurations for defence in depth in doors across compartments?
SE-E-1555 | PFP | SE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Forsmark 2 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
SE-E-1556 | PFP | SE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Oskarshamn 3 | p83/1/ What are the requirements for fire doors and penetrations between fire compartments? p83,85/3/ On page 83 it is first declared that there are 13 fire compartments and later that there are over 200. Could you explain this?
SE-E-1557 | PFP | SE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Oskarshamn 3 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
SE-E-1558 | PFP | SE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Ringhals 3 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
SE-E-1559 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Forsmark 2 | page 74/Section 3.1.4.2/1/ Do you have installed HEPA filters in ventilation systems? /Section 3.3.2.1./2/ How are the ventilation systems in fire compartments separating redundant trains? /Section 3.3.2.1./2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences?
SE-E-1560 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Forsmark 2 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SE-E-1561 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Oskarshamn 3 | page 84/Section 3.2.4.2/1/ Have been installed HEPA filters in ventilation systems? /Section 3.3.4.1./1,2,3/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences?
SE-E-1562 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Oskarshamn 3 | p83,85/3/ NAR states that "no fire compartment is sharing ventilation equipment or air ducts with another fire compartment". Should this be fire zones as it is pretty much impossible to achieve this otherwise? (On page 85, there are exceptions provided.)
SE-E-1563 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Oskarshamn 3 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SE-E-1564 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Ringhals 3 | page 99/Section 3.3.4.2/1/ Have been installed HEPA filters in ventilation systems? page 99/Section 3.3.4.2/ 2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences?
SE-E-1565 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Ringhals 3 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SE-E-1566 | PFP | SE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Forsmark 2 | Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements. page 64/Section 3.1.1.3.2/1/ Section 3.4.A/ Did you have OSART and WANO missions? What were lessons learnt from OSART and WANO missions? page 69/Section 3.1.1.3.2/1/ It is written the following sentence "Implementation of a fire prevention system with reduced oxygen in some electrical rooms that has safety related equipment belonging to two redundancies in the same fire compartment". Please describe this system in more detail.
SE-E-1567 | PFP | SE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Forsmark 2 | Prior to 2022, SSM did not have any specific requirements on fire prevention as shown in section 1.2.1 for nuclear power plants. As such, there have not been any inspections and no formal lessons learned with regards to the fire prevention programs for the licensees. How is compliance with the new specific requirements assured? How is the past history of the installation transfered to the nuclear authority?
SE-E-1568 | PFP | SE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Forsmark 2 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
SE-E-1569 | PFP | SE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Oskarshamn 3 | Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
SE-E-1570 | PFP | SE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Oskarshamn 3 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
SE-E-1571 | PFP | SE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Ringhals 3 | Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
SE-E-1572 | PFP | SE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Ringhals 3 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
SE-E-1573 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | CLAB | page 117 - There is limited information on fire load controls other than a statement regarding its minimisation by design implemented; page 126 states the frequency of room rounds (yearly) What is the scope of these (thorough reviews) / versus the daily control rounds that includes checks of fire loads? What is the status of measures credited as 'being prepared to be introduced' (see page 114)?: – installation of two new backup power diesels redundant through fire separation in two different fire cells. – introduce fire separation of all incoming cables
SE-E-1574 | PFP | SE | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | CLAB |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
SE-E-1575 | PFP | SE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | CLAB | page 118 - After an insurance inspection, fire separation walls were introduced between transformers. Please describe fire rating of these fire separation walls. Fire separation/ barriers with two different classes A60 and EI60. - Two buildings in same fire cell; Please provide the rationale for fire cells/ extent of fire cells in relation to fire loading. How was this informed by fire hazard characterisation? Following the results of the FHA, see also chapter 2.4.5.1, vulnerabilities of the plant configuration were identified and actions to improve the fire protection led to repositioning of redundant components and installation of heat radiation protection between in the cooling system. Page 62 fire analysis section includes examples of fire scenarios reviewed; Please clarify if the measures have been implemented? (page 118 may indicate they have not?)
SE-E-1576 | PFP | SE | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | CLAB |  | [generic]: o Compartmentation (as applicable): How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
SE-E-1577 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | CLAB | Please provide the current status of measures credited as 'being prepared to be introduced (see page 114): – improve the fire ventilation in the fuel elevator compartment. – installation of new independent cooling system that cools with air that will give a stronger reliability and durability of the cooling of the storage basins.
SE-E-1578 | PFP | SE | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | CLAB |  | [generic] o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SE-E-1579 | PFP | SE | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | CLAB |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
SE-E-1580 | AFP | SE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Forsmark 2 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
SE-E-1581 | AFP | SE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Forsmark 2 | Page 71 of pdf, section 3.1.3.1.2, assumption 1. “The system predominantly uses multi-criteria detectors”. Please, explain the main features, variables compared, design standards and other general information regarding this type of detectors. - Page 71 of pdf, section 3.1.3.1.2, assumption 1. Are failures of the cable connections announced to the main control room?
SE-E-1582 | AFP | SE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Forsmark 2 | /2/ The design of the fire detection system against earthquake is not mentioned.
SE-E-1583 | AFP | SE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Oskarshamn 3 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
SE-E-1584 | AFP | SE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Oskarshamn 3 | Page 84 of pdf, section 3.2.3.1.2, assumption 1. Fire detectors' technology is not described. Please, describe the systems’ key features and technology (ionization and optical smoke detectors, flame detectors, heat detectors, linear detectors, air sampling detectors or other types). - Page 84 of pdf, section 3.2.3.1.2, assumption 4. Explain the procedures established for the examination, inspection, maintenance and testing of fire detection and alarm features.
SE-E-1585 | AFP | SE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Oskarshamn 3 | /2/ The design of the fire detection system against earthquake is not mentioned.
SE-E-1586 | AFP | SE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Ringhals 3 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
SE-E-1587 | AFP | SE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Ringhals 3 | /2/ The design of the fire detection system against earthquake is not mentioned.
SE-E-1588 | AFP | SE | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Forsmark 2 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
SE-E-1589 | AFP | SE | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Forsmark 2 | Page 73 of pdf, section 3.1.3.2.1, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown or any similar provision? - Page 73 of pdf, section 3.1.3.2.2, assumption 2. It is explained that there is a common storage tank that supplies unit 1 and 2 with fire water and there is a redundant water supply from the low-water reservoir. Regarding the low-water reservoir: explain its inventory, connections and other relevant features. - Page 73 of pdf, section 3.1.3.2.3, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain.
SE-E-1590 | AFP | SE | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Forsmark 2 | /2/ 'p. 68 "The volume of the storage tank allows sprinkling for 90 minutes with a water outlet of 200 kg/s. After 90 minutes, manual actions are required to add water to the tank." Tank has 1500 m3 volume. It should be explained what kind of manual actions are needed to provide extinguishing water. Many NPPs have an inexhaustible water supply. /2/ The design of the fire water supply against earthquake is not mentioned.
SE-E-1591 | AFP | SE | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Oskarshamn 3 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
SE-E-1592 | AFP | SE | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Oskarshamn 3 | Page 85 of pdf, section 3.2.3.2.2, assumption 3. Explain in general the procedures established for the examination, inspection, maintenance and testing of extinguishing systems. - Page 86 of pdf, section 3.2.3.2.4, assumption 3. Explain in general the types of compensatory measures in case of impairment of fire suppression systems.
SE-E-1593 | AFP | SE | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Ringhals 3 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
SE-E-1594 | AFP | SE | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Ringhals 3 | Page 98 of pdf, section 3.3.3.2, assumption 2. Explain if the fire ring include a double supply to buildings containing safety related SSC’s; and if this ring have isolation valves, the aim being to be able to isolate part of the main ring for maintenance or repair. - Page 98 of pdf, section 3.3.3.2.1, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown or any similar provision?
SE-E-1595 | AFP | SE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Forsmark 2 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
SE-E-1596 | AFP | SE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Forsmark 2 | Page 74 of pdf, section 3.1.3.3.1, assumption 1. Please, describe more in depth the content of intervention cards used for firefighting. - Page 74 of pdf, section 3.1.3.3.2, assumption 4. “There is an internal fire brigade stationed on the site”. Explain the minimum staffing, training, organisation, minimum knowledge and physical conditions of the fire brigade.
SE-E-1597 | AFP | SE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Forsmark 2 | /1/ p. 70/71:- Internal fire brigade by contractor -> what is the minimum staffing? - by which criteria the external fire brigade is alerted?
SE-E-1598 | AFP | SE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Oskarshamn 3 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
SE-E-1599 | AFP | SE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Oskarshamn 3 | Page 86 of pdf, section 3.2.3.3.1, assumption 1. Please, describe more in depth the content of firefighting deployment charts. - Page 86 of pdf, section 3.2.3.3.2, assumption 4. Explain the minimum staffing, training, firefighter qualifications, organisation, minimum knowledge, skills and physical conditions of the onsite fire brigade. - Page 86 of pdf, section 3.2.3.3.2, assumption 1. Drills and exercises are not described. Please explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade, content and main lessons learnt. - Page 86 of pdf, section 3.2.3.3.2, assumption 2. Explain the coordination between the onsite fire brigade and the offsite fire brigade. - Page 86 of pdf, section 3.2.3.3.2, assumption 2. Explain the written procedures in place defining responsibility and actions of staff in responding to any fire in the installation.
SE-E-1600 | AFP | SE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Ringhals 3 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
SE-E-1601 | AFP | SE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Ringhals 3 | /2/ 'p. 97: "The criteria to deploy the offsite fire brigade is that a confirmed fire has occurred." - a "confirmed fire" may only be very small. Are there other criteria or how the desicion to alert the externasl fire brigade is taken?
SE-E-1602 | AFP | SE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Ringhals 3 | Page 100 of pdf, section 3.3.3.3.1, assumption 1. Please, describe more in depth the content of intervention layouts and fire compartment layouts. - Page 100 of pdf, section 3.3.3.3.2, assumption 4. Explain the training, firefighter qualifications, organisation, minimum knowledge, skills and physical conditions of the onsite fire brigade.
SE-E-1603 | AFP | SE | Active fire protection | Licensee and regulatory experience |  | NPP | Forsmark 2 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
SE-E-1604 | AFP | SE | Active fire protection | Licensee and regulatory experience |  | NPP | Oskarshamn 3 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
SE-E-1605 | AFP | SE | Active fire protection | Licensee and regulatory experience |  | NPP | Ringhals 3 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
SE-E-1606 | AFP | SE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | CLAB |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
SE-E-1607 | AFP | SE | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | CLAB | (TS 3.2..2.4 Alternative/temporary provisions) pag. 118 --> In addition to when and why alternative/temporary provisions are taken, it would be necessary to know what the main provisions are. --> In addition to the temporary to be taken in the event of systems being unavailable due to lack of operability, it would be useful to highlight the measures to be taken in the event of an earthquake. --> Please highlight weaknesses and any related improvement measures.
SE-E-1608 | AFP | SE | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | CLAB |  | Extinguishing water management [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
SE-E-1609 | AFP | SE | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | CLAB | (TS 3.2..2.4 Alternative/temporary provisions) pag. 118 --> In addition to when and why alternative/temporary provisions are taken, it would be necessary to know what the mainprovisions are. --> In addition to the temporary to be taken in the event of systems being unavailable due to lack of operability, it would be useful to highlight the measures to be taken in the event of an earthquake. --> Highlight weaknesses and any related improvement measures.
SE-E-1610 | AFP | SE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | CLAB |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
SE-E-1611 | AFP | SE | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | CLAB | Clarify how joint rescue service exercises are carried out, whether between professionals or volunteers? Indicate the frequency of the drills and the expected documentation.
SE-E-1612 | AFP | SE | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - wet | CLAB |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
SI-E-1613 | FSA | SI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Krsko NPP | 1 - Please clarify how the design basis fire or reference fire is determined for each fire compartment [Page 20][Section 2.1.2][Assumption 2/]
SI-E-1614 | FSA | SI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Krsko NPP | (p 111, ch 2.1.10.) What is the timetable for the complete update of the fire PSA?
SI-E-1615 | FSA | SI | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Krsko NPP | What is your experience from applying NRC regulations and guidelines (pros and cons) for fire safety analyses?
SI-E-1616 | FSA | SI | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Krsko NPP | (p 111, ch 2.1.10.) What is the timetable for the complete update of the fire PSA?
SI-E-1617 | FSA | SI | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Krsko NPP | What is the basis for requiring an additional update of the FHA at least every two years apart from those updates required after major plant modifications?
SI-E-1618 | FSA | SI | Fire safety analysis | Licensee and regulatory experience |  | NPP | Krsko NPP |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
SI-E-1619 | FSA | SI | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Solid waste storage facility (Krško NPP site) | p 103ff.: What are the underlying fire scenarios for RWSF, DB and WMB? What models or tools were used for the FHA? 104 and p111: The operator assesses the fire possibility as low, whereas the regulator states, that the fire risk for the RWSF is high. How do you assess and adress this difference?
SI-E-1620 | FSA | SI | Fire safety analysis | Licensee and regulatory experience |  | Waste | Solid waste storage facility (Krško NPP site) | p.111: Regarding the self assessment report, were the any findings and if yes, what have been the consequences?
SI-E-1621 | FSA | SI | Fire safety analysis | Licensee and regulatory experience |  | Waste | Solid waste storage facility (Krško NPP site) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
SI-E-1622 | PFP | SI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Krsko NPP | *Page 114. Section 3.1.2 Overview of Arrangements for Management and Control of Fire Load and Ignition Sources. Assumption 3/. "Fixed fire loads are controlled in Fire Hazard Analysis and margins are set for each fire area. Criteria for setting those margins are resistance of fire barriers in a fire area. Plant modifications are controlled per procedure ESP-2.602 “Plant Design Modification” [103], which includes control of fire barriers, fire protection equipment impact and revision of Fire Hazard Analysis [3]. Additional (transient) fire loads are controlled within a process per ADP-1.1.105 “Controlled disposal and storage of material” [61], which considers allowable fire load margins for each fire zone. Thus, control is established not to exceed combined (fixed and transient) quantity of flammable material in a room." Are (fix and temporary) storage areas registered and clearly identified? Are storage areas approved by permits? In that case, is it periodically checked that fire loads remain in the state in which they were approved? Or, is it periodically checked that fire loads do not exceed the allowed margins?. *Page 114. Section 3.1.2 Overview of Arrangements for Management and Control of Fire Load and Ignition Sources. Assumption 3/. "Each activity, that could produce ignition sources, is controlled with “Hot work permit” process. Depending on fire vulnerability at location, measures of firewatch are defined and controlled per procedure FPP-3.7.006 “Fire Permit” [95]." Before issuing a hot work permit, is it considered if there are other alternatives that do not involve hot work? Is the impact on fire protection systems analyzed? Does the evaluation include risk assessment and work methodologies? Is the impact on fire protection systems analyzed? Is it proven that the person in charge of carrying out the hot work has adequate training and knows the risks and fire prevention measures that must be applied before starting the work? Is it taken into account whether there are necessary security systems near the work area and are necessary measures taken to protect said systems? How is the performance of hot work in ATEX areas managed?
SI-E-1623 | PFP | SI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Krsko NPP |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
SI-E-1624 | PFP | SI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Krsko NPP | *Page 136. Section 3.3.1 Prevention of Fire Spreading (Barriers). Assumtpion 4/. There is no information about how access routes for firefighting are maintained. Give this information, some questions are: How are evacuation routes signposted? How is ensured that there is an emergency lighting system? In which documents are these routes defined? How is smoke intrusion into acces routes prevented in case of fire?
SI-E-1625 | PFP | SI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Krsko NPP |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
SI-E-1626 | PFP | SI | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Krsko NPP | *Page 138. Section 3.3.2 Ventilation Systems. Assumtpion 1/. Information about access routes is missing. Please provide this information according to the technical specification.
SI-E-1627 | PFP | SI | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Krsko NPP |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SI-E-1628 | PFP | SI | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Krsko NPP | Page 89. Section 2.1.6.1 Overview of Strengths and Weaknesses Identified. Assumtpion 1/. "Design of Krško NPP does not meet full compliance with the Appendix R requirements (20 feet separation between trains etc.) especially in some common (both train components are within the same rooms/areas) like Component Cooling or Essential Service Building, common cable spreading room or as a most vulnerable Main Control Room. Fire response procedure for the fire in those areas were comprehensive to give instructions to establish all safety functions mostly by a number of manual actions including some special system configuration. One of the goals for the recently implemented Safety Upgrade Program (SUP) were to provide alternative systems to ensure the capability for all the safety functions even if the fire started in a such common areas and consequentially the equipment from both trains can be affected. After the implementation of SUP the capabilities for the alternative strategies to meet safety objectives are provided in the sense of some kind of third Safety train in BB1 and BB2 which is independent from the originally installed ECCS system component." With the application of Safety Upgrade Program, these are weaknesses from the past, several changes have been introduce. Have any weaknesses been identified for the current situation of the plant?
SI-E-1629 | PFP | SI | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Krsko NPP |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
SI-E-1630 | PFP | SI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | Dry SFDS Krško NPP site |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
SI-E-1631 | PFP | SI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | Dry SFDS Krško NPP site |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
SI-E-1632 | PFP | SI | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | Dry SFDS Krško NPP site |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SI-E-1633 | PFP | SI | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Dry SFDS Krško NPP site |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
SI-E-1634 | PFP | SI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Solid waste storage facility (Krško NPP site) | The following does not appear covered: - information on fixed combustible and flammable inventories e.g. presence of flammable gases including hydrogen, oils, diesel within buildings or adjacent to buildings ( section 3.1.2) - characteristics of the hot work permits - causes and actions taken following the fires reported Please describe the above considerations/ questions. The overview of strengths and weaknesses appears focused on active fire protection/ suppression - where and how is coverage of fire prevention and enhancement of passive fire protection provided?
SI-E-1635 | PFP | SI | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Solid waste storage facility (Krško NPP site) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
SI-E-1636 | PFP | SI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Solid waste storage facility (Krško NPP site) | Two of the emergency diesel generators are separated from each other by a rated fire wall (see page 151) - What is the fire rating of the mentioned wall? Consideration of fire containment vs fire influence approach. The fire-rated barriers (3hr) are only quoted for separation between buildings. Are safety trains segregated by 3 hour fire barriers, and are there exceptions to segregation? (see page 151)
SI-E-1637 | PFP | SI | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Solid waste storage facility (Krško NPP site) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
SI-E-1638 | PFP | SI | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Solid waste storage facility (Krško NPP site) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SI-E-1639 | PFP | SI | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Solid waste storage facility (Krško NPP site) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
SI-E-1640 | AFP | SI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Krsko NPP |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
SI-E-1641 | AFP | SI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Krsko NPP | Page 124-126 Section 3.2.1 Topic 1 - what is the nuclear safety class of the fire detection and alarm system? The report discusses actuation of suppression systems but does the fire alarm and detection system actuate any other protection measures such as dampers?
SI-E-1642 | AFP | SI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Krsko NPP | Page 124-126 Section 3.2.1 Topic 1 - Are the fire detection and alarms system cables fire resistant? And are any associated cabinet enclosures fire rated? What is the hazard tolerance of the fire detection system? How is EMIT of the fire alarm and detection system controlled?
SI-E-1643 | AFP | SI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Krsko NPP |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
SI-E-1644 | AFP | SI | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Krsko NPP | Page 126-129 Section 3.2.2 Topic 1 - what is the nuclear safety class of the fire suppression systems and to what standards are they designs? Are the capacities of the suppression system sufficent to protect against the worst case events?
SI-E-1645 | AFP | SI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Krsko NPP |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
SI-E-1646 | AFP | SI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Krsko NPP | Page 129-135 Section 3.2.3 Topic 6 - Are there any issues for the external fire brigades with regards to access to the site?
SI-E-1647 | AFP | SI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Krsko NPP | Firefighters: The diversity of origins of internal and external firefighters raises questions. How are the different missions of each person distributed? Are they both equipped with the same equipment?
SI-E-1648 | AFP | SI | Active fire protection | Licensee and regulatory experience |  | NPP | Krsko NPP |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
SI-E-1649 | AFP | SI | Active fire protection | Licensee and regulatory experience |  | NPP | Krsko NPP | For a site with a relatively high regional seismicity, how are the lessons learned in the field of fire safety from past international events (such as the Kashiwazaki-Kariwa earthquake) taken into account?
SI-E-1650 | AFP | SI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Dry SFDS Krško NPP site | Clear evidence of the fire protection and suppression provisions in the different buildings/Facilities. 'Alternative/temporary provisions --> It should be clarified what specific equipment is present in the Spent fuel storage (Dry SFDS) facility.
SI-E-1651 | AFP | SI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | Dry SFDS Krško NPP site |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
SI-E-1652 | AFP | SI | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | Dry SFDS Krško NPP site |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
SI-E-1653 | AFP | SI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Dry SFDS Krško NPP site |  | Agreement between NPP and municipality
SI-E-1654 | AFP | SI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Dry SFDS Krško NPP site | Clarify what documents and procedures are needed to conduct fire fighting.
SI-E-1655 | AFP | SI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | Dry SFDS Krško NPP site |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
SI-E-1656 | AFP | SI | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | Dry SFDS Krško NPP site |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
SI-E-1657 | AFP | SI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Solid waste storage facility (Krško NPP site) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
SI-E-1658 | AFP | SI | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Solid waste storage facility (Krško NPP site) | /1/ The waste storage facility on the NPP site is described in Ch. 2.5 of the NAR (PDF p. 117). There is no specific treatment of the facility in Chapter 3.2 "Active fire protection" (PDF p. 137 +). Much information asked for in the Tec. Spec. is missing. Please provide additional information in accordance with Technical Specification.
SI-E-1659 | AFP | SI | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Solid waste storage facility (Krško NPP site) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
SI-E-1660 | AFP | SI | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Solid waste storage facility (Krško NPP site) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
SI-E-1661 | AFP | SI | Active fire protection | Licensee and regulatory experience |  | Waste | Solid waste storage facility (Krško NPP site) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
SK-E-1662 | FSA | SK | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Mohovce 34 | P. 27: "L1 PSA covers all operating modes of NPP unit 3, reactor equipment and spent fuel storage pool." However, p. 30 mentions only PSA of operation level. Could you please clarify. (4/) P. 31, 37-38: The FHA evaluates fire hazards in "selected buildings and areas" (p. 31). Later, the NAR gives an impression (p. 37-38) that the FHA is done only for the turbine hall. Is that correct, or were there other areas/buildings analysed? (2/)
SK-E-1663 | FSA | SK | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Mohovce 34 | What about a Level 2 Fire PSA? p 40 Can you please confirm the statement that "no measures resulted from the probabilistic assessment"
SK-E-1664 | FSA | SK | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Mohovce 34 | P. 39 (2.1.5): The NAR states "Fire hazard analysis must be updated according to the actual situation" - are regular updates in connection to PSR not foreseen?
SK-E-1665 | FSA | SK | Fire safety analysis | Licensee and regulatory experience |  | NPP | Mohovce 34 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
SK-E-1666 | FSA | SK | Fire safety analysis | Assumptions (TS 02.4) |  | Spent fuel storage - wet | ISFSF | P. 45 (2.4.3) What are the possible consequences and recovery actions in case of loss of pool cooling?
SK-E-1667 | FSA | SK | Fire safety analysis | Licensee and regulatory experience |  | Spent fuel storage - wet | ISFSF |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire safety analyses with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Inventory make-up: Please provide a higher level of detail on the systems used to make-up inventory. 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 5. Additional analyses: Please provide details about: a) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for spent fuel storage facilities in your country? b) Some countries mention that a periodic safety review is performed for spent fuel storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 6. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
SK-E-1668 | PFP | SK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Mohovce 34 | "the reduction of the said concentration and the disconnection of electrical equipment from the electrical voltage is ensured by appropriate technical means" Please provide additional information on which technical means are used? page 54
SK-E-1669 | PFP | SK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Mohovce 34 | 3/ What is the process for determining ignition sources (other than hot work) and what are the most important sources identified?
SK-E-1670 | PFP | SK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Mohovce 34 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
SK-E-1671 | PFP | SK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Mohovce 34 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
SK-E-1672 | PFP | SK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Mohovce 34 | "the reduction of the said concentration and the disconnection of electrical equipment from the electrical voltage is ensured by appropriate technical means" Please provide additional information on which technical means are used?
SK-E-1673 | PFP | SK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Mohovce 34 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SK-E-1674 | PFP | SK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Mohovce 34 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
SK-E-1675 | PFP | SK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | ISFSF | Some topics, for the "Fire Prevention" are not present (see List of detailed contents for the TS - annex 2), in particular: • (b)"3.1.3 Licensee's experience of the implementation of the fire prevention" (and related subparagraphs) • (b)"3.1.4 Regulator's assessment of the fire prevention" (and related subparagraphs) Please provide the missing information for the above.
SK-E-1676 | PFP | SK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - wet | ISFSF |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
SK-E-1677 | PFP | SK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | ISFSF | NAR section 3.3.4.2.2 pag. 107 -> Please describe/clarify what are type B escape routes and their purpose?
SK-E-1678 | PFP | SK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - wet | ISFSF |  | o Compartmentation (as applicable): How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing?
SK-E-1679 | PFP | SK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | ISFSF | NAR section 3.3.4.2.2 pag. 107 -> Please describe/clarify what are type B escape routes and their purpose?
SK-E-1680 | PFP | SK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - wet | ISFSF |  | [generic] o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
SK-E-1681 | PFP | SK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - wet | ISFSF |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
SK-E-1682 | AFP | SK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Mohovce 34 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
SK-E-1683 | AFP | SK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Mohovce 34 | (p.61) Activities associated with increased fire hazards (welding, thermal cutting, grinding, …) can only be carried out with associated compensatory measures, such as fire patrol and premises walk-around are set up to assist at risk activities. “In some cases, as an alternative measure, monitoring of selected areas by installed camera systems (example: the primary pump room).” While this is positive from a RP point of view, the use of camera and only periodic fire patrols instead does not provide the same assurance than a full-time fire watch present during the works. Please clarify the periodicity of the fire patrols. Please clarify the effectiveness of the CCTV to detect smoke or fire in a timely manner.
SK-E-1684 | AFP | SK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Mohovce 34 | Page 21-22 Section 1.3 Topic 1 - identifies a series of improvements to NPP fire safety which were applied to the design of MO3&4. However, the report does not appear to explain the representiveness of MO3&4 for the other operation NPPs in the Slovak Republic or explain where there are divergences from the MO3&4 active fire protection approach in other stations.
SK-E-1685 | AFP | SK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Mohovce 34 | 1. Section 3.2.1.1.2, page 58. The issue of automatic connection of the reserve (by switching to another electrical section/assembly/cabinet by the action of the automatic load transfer. 2. Section 3.2.1.1.2, page 60. It is not described how: - fire detectors are checked; - whether a metrological verification of the characteristics of sensors/detectors is envisaged (periodic/selective); - which methods/ways of checking electrical wiring (measurement of electrical resistance of insulation and/or visual inspection, etc.) are used.
SK-E-1686 | AFP | SK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Mohovce 34 | Page 55-61 Section 3.2.1.1 Topic 1 - do any of the fire detection system cabinet enclosures have any fire resistance
SK-E-1687 | AFP | SK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Mohovce 34 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
SK-E-1688 | AFP | SK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Mohovce 34 | The strategy for installing and designing the fixed extinguishing systems (FES) is not 100% clear. (p.61) Please clarify why (gaseous) FES are not installed in electrical distribution cabinets, panels in 0.4 kV and 6 kV substations, I&C panels with safety-critical equipment. Clarify also whether and how the main control room and emergency control room are equipped with FES. (p.64) Clarify why FES in cable spaces use high-pressure water mist (for instance instead of gas, which is used in other protected areas). (p.71) Clarify what equipment / rooms of the DG station are protected by the foam FES.
SK-E-1689 | AFP | SK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Mohovce 34 | Page 69-76 Section 3.2.1.2 Topic 1- what is the nuclear safety class of the fire suppression systems?
SK-E-1690 | AFP | SK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Mohovce 34 | Section 3.2.1.1.2, p. 66. Information on measures to neutralize (remove) water after the water fire extinguishing system is activated.
SK-E-1691 | AFP | SK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Mohovce 34 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
SK-E-1692 | AFP | SK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Mohovce 34 | • (p.84) Please clarify vehicles number and types (notably fire trucks) available to the onsite fire brigade (“PFB”). • (p.84) The NAR states that the onsite fire brigade is operated by an external company under a works contract, with a minimum of 15 staff members per shift, of which 1 fire control room operator and fire reporting room and 14 fire-fighters dedicated to effectively fight the most complex scenarios of anticipated fire. Clarify how there is a control room operator integrated in an organization subcontracted. If the onsite fire brigade (PSB) is rather composed by both subcontractors and plant staff, clarify how the coordination is ensured. • (p.84) Please confirm that the following statement is correct: “commencement of activities at the scene of intervention (boarding area for the firefighting unit) within 5 minutes of reporting the incident to the fire reporting room”. Has it been demonstrated during exercise and during actual unplanned fire interventions? What are the intervention times measured for interventions following recent fire alarms? • (p.87) When needed, the onsite fire brigade can be supported by additional external fire brigades from the FaRC. The NAR does not explain the strategy for this. When is the FaRc called for an intervention? Is the FaRC informed of fire interventions of the onsite brigade? How far are the FaRC? How much time is needed for the external brigades to arrive at the place of intervention (including time needed for security checks etc.).
SK-E-1693 | AFP | SK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Mohovce 34 | The information on Organization of control/technical oversight of the condition of cylinders with compressed gas (under pressure) for gas fire extinguishing is missing. Please provide the relevant information.
SK-E-1694 | AFP | SK | Active fire protection | Licensee and regulatory experience |  | NPP | Mohovce 34 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
SK-E-1695 | AFP | SK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | ISFSF |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
SK-E-1696 | AFP | SK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - wet | ISFSF | Interim Spent Fuel Storage facility (ISFS) at the Bohunice (TS 3.2.1 Fire detection and alarm provisions) - 3.2.4.1 pag. 90 --> Please clarify the function, types, main characteristics and performance of fire detection and alarm provisions used in ISFS. ---> In addition to the temporary measures to be taken in the event of systems being unavailable due to lack of operability, it would be useful to highlight the measures to be taken in the event of an earthquake.
SK-E-1697 | AFP | SK | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - wet | ISFSF |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
SK-E-1698 | AFP | SK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - wet | ISFSF |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
SK-E-1699 | AFP | SK | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - wet | ISFSF |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
TR-E-1700 | FSA | TR | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Akkuyu NPP | P. 9-10: Could you please check that all the acronyms are explained (e.g. KD UPS, SAZ). p. 9-11: It is not clear if any PSA studies are yet done. Could you please clarify and explain what the regulatory requirements for the Fire PSA scope (Level 1 only or also Level 2) are? Are low power and shut-down states considered?). (4/)
TR-E-1701 | FSA | TR | Fire safety analysis | PSR and modifications resulting from deterministic and probabilistic fire safety analyses |  | NPP | Akkuyu NPP | P. 11 (2.1.5): What are the plans for the management of changes to and updates of the fire safety analyses in the future?
TR-E-1702 | FSA | TR | Fire safety analysis | Licensee and regulatory experience |  | NPP | Akkuyu NPP |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
TR-E-1703 | FSA | TR | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | İTÜ Research Reactor | 1 - The scope of the engineering judgement is not stated. Does it cover all possible reactor operating modes, including for instance when the reactor is not in operation during non-working hours? [page 12][Section 2.2][Assumption 1/] 2 - Could you describe the main fire scenarios considered by the expert judgement analyses? [page 12][Section 2.2.2][Assumption 1/] 3 - The results of the deterministic safety analysis are not presented in section 2.2.4. What are the main fire accident sequences or scenarios? [page 13][Section 2.2.4][Assumption 4/]
TR-E-1704 | FSA | TR | Fire safety analysis | Assumptions (TS 02.2) |  | Research reactor | İTÜ Research Reactor | 1 - Engineering judgement and expert opinion were used for fire safety analysis, but methodology, fire phenonena and main results were not provided. Please describe or add corresponding information. [page 12-13][section 2.2] [Assumption 2/3/4/]
TR-E-1705 | FSA | TR | Fire safety analysis | PSR and modifications |  | Research reactor | İTÜ Research Reactor | 1 - Current and previous approaches for PSR and modification are not described. Just one improvement was mentioned. Is the PSR conducted from commissioning? [Assumption 1/]
TR-E-1706 | FSA | TR | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | İTÜ Research Reactor | 1 - Section 2.2.6 mentions that "the fire consultant conducted the fire hazard analysis of all areas of the ITU TRIGA facility and determined the requirements to identify the potential fire hazards and the necessary fire protection measures". Could you please describe some findings and give examples of measures? [page 14][section 2.2.6][Assumption 1/]
TR-E-1707 | FSA | TR | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | İTÜ Research Reactor |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
TR-E-1708 | PFP | TR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Akkuyu NPP | page 16/Section 3.1/3/ Describe how is control the hot work during the NPP construction? page 16/Section 3.1 /3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 16/Section 3.1/3/ How is explosion protection (Ex zone, Ex equipment...) considered?
TR-E-1709 | PFP | TR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Akkuyu NPP |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
TR-E-1710 | PFP | TR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Akkuyu NPP | page 28/Section 3.3.1/4/ How are access routes for firefighting maintained?
TR-E-1711 | PFP | TR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Akkuyu NPP |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
TR-E-1712 | PFP | TR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Akkuyu NPP | page 29/Section 3.3.2/2/ How are the ventilation systems in fire compartments separating redundant trains? page 29/Section 3.3.2/2/ Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences? page 29/Section 3.3.2/3/ There is information missing on the topice "In case that a ventilation system serves more than one fire compartments to prevent the spread of fire...". Please give information on this topic.
TR-E-1713 | PFP | TR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Akkuyu NPP |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
TR-E-1714 | PFP | TR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Akkuyu NPP |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
TR-E-1715 | PFP | TR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | İTÜ Research Reactor | Please provide more information on the practise of temporary fire load management.
TR-E-1716 | PFP | TR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | İTÜ Research Reactor |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
TR-E-1717 | PFP | TR | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | İTÜ Research Reactor | "3.3.1 prevention of fire spreading, has not yet been applied or analysed ITU should prepare a fire safety program" (p.27) However, 3.1.2 contains a description of several procedures and routines to minimize fire load and gain experiences from visits by the local fire brigade; Please describe if the above is a description of the present or the expected content of the fire safety analysis.
TR-E-1718 | PFP | TR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | İTÜ Research Reactor | How are the fire classes for fire barriers defined?
TR-E-1719 | PFP | TR | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | İTÜ Research Reactor |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
TR-E-1720 | PFP | TR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | İTÜ Research Reactor | p28" "ventilation" chapter is missing for the RR involved. Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers?
TR-E-1721 | PFP | TR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | İTÜ Research Reactor | "3.3.1 prevention of fire spreading, has not yet been applied or analysed ITU should prepare a fire safety program "(p.27) However, 3.1.2 contains a description of several procedures and routines to minimize fire load and gain experiences from visits by the local fire brigade; Please describe if the above is a description of the present or the expected content of the fire safety analysis.
TR-E-1722 | PFP | TR | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | İTÜ Research Reactor |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
TR-E-1723 | PFP | TR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | İTÜ Research Reactor | "3.3.1 prevention of fire spreading, has not yet been applied or analysed ITU should prepare a fire safety program "(p.27) However, 3.1.2 contains a description of several procedures and routines to minimize fire load and gain experiences from visits by the local fire brigade; Please describe if the above is a description of the present or the expected content of the fire safety analysis.
TR-E-1724 | PFP | TR | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | İTÜ Research Reactor |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
TR-E-1725 | AFP | TR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Akkuyu NPP |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
TR-E-1726 | AFP | TR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Akkuyu NPP | • Please clarify how it is ensured that the fire detection system is capable to withstand the relevant ambient / hazard conditions (including seismic hazards, considering the relative high regional seismicity) • Please clarify how independence between fire detection systems in adjacent compartments is achieved. • (p.21) The NAR states: ""The fire detection system is installed in all buildings […] with the exception of buildings of category B4 and D, buildings with wet processes, ventilation rooms (not serving buildings of categories A and B) and stairwells. In addition, a fire detection system must be installed in all listed buildings of categories A, B, B1-B4."" Clarify the definition of building categories. Clarify what is exactly meant by ""buildings with wet processes "". Clarify fire detection in building B4 (contradicting info in the NAR)."
TR-E-1727 | AFP | TR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Akkuyu NPP | Section 3.2. Absence of information on cable products of automatic fire alarm systems, in particular fire resistance, non-propagation of flame, etc.
TR-E-1728 | AFP | TR | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Akkuyu NPP |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
TR-E-1729 | AFP | TR | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Akkuyu NPP | • (p.22) The NAR states: "[…] pulverized or fine atomized water (water mist / fine spray system) is used as extinguishing agent for cable structures, power transformers […]. Automatic gas fire extinguishing units are used for fire protection of buildings with electronic and electrical equipment." These two sentences are contradicting. Clarify extinguishing means for buildings or rooms containing electrical equipment. • (p.24) Clarify what are the water sources that would be used for fire suppression. What are the base sources, what are the backups, and how much water volume is there available on site in case of need. • Please clarify the seismic resistance of the fire extinguishing provisions (considering the relative high regional seismicity), • Clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy. • What are the fire suppression provisions for the EDGs and main coolant pumps?
TR-E-1730 | AFP | TR | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Akkuyu NPP | 1. Section 3.2. Absence of requirements for fire extinguishing systems of safety systems (qualification of equipment with regard to external hazards, in particular seismic resistance, classification by functions, etc.) 2. Section 3.2.2. Measures to neutralize (remove) gas from the premises after actuation of the gas fire extinguishing systems. 3. Section 3.2.2. The information on technological part of the fire extinguishing systems (e.g. water tanks and water/gas supply sources, in particular, safety systems) is missing. Please provide this information.
TR-E-1731 | AFP | TR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Akkuyu NPP |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
TR-E-1732 | AFP | TR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Akkuyu NPP | • Clarify firefighting strategies, how they are ensured (written procedures, training provision, frequency of emergency exercises, …). • Clarify the organisation between onsite and offsite firefighters, including criteria for deploying onsite and offsite firefighting resources, how coordination is achieved between the plant personnel and the offsite resources, if the plant internal firefighting capability is supported by offsite resources, how it is ensured that the firefighting resources are familiar with the hazards of the plant, and adequate time for security control is provided, safety culture and how the above are reinforced through emergency training, drills and exercises, type and contents of firefighting documentation available to onsite and offsite firefighting resources, • Clarify what specific provisions are in place for firefighting situations with loss of access routes to the installation within the site boundary, and with loss of access routes to the site (considering the relative high regional seismicity, and the regional tsunami hazard). • How far are the external fire brigades located and what are their size? How much time is needed for them to reach a fire inside the NPP installation (has this been assessed and exercised?)? • Clarify the strategy for isolation or overpressurization of escape routes and access routes for firefighters..
TR-E-1733 | AFP | TR | Active fire protection | Licensee and regulatory experience |  | NPP | Akkuyu NPP |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
TR-E-1734 | AFP | TR | Active fire protection | Licensee and regulatory experience |  | NPP | Akkuyu NPP | • For a site with a relatively high regional seismicity, how are the lessons learned (in the field of fire safety) from past international events (such as the Kashiwazaki-Kariwa earthquake) taken into account?
TR-E-1735 | AFP | TR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | İTÜ Research Reactor |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
TR-E-1736 | AFP | TR | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | İTÜ Research Reactor | Please clarify seismic resistance of the fire detection (considering relative high regional seismicity).
TR-E-1737 | AFP | TR | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | İTÜ Research Reactor |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
TR-E-1738 | AFP | TR | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | İTÜ Research Reactor | Please clarify seismic resistance of extinguishing provisions (considering relative high regional seismicity).
TR-E-1739 | AFP | TR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | İTÜ Research Reactor |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
TR-E-1740 | AFP | TR | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | İTÜ Research Reactor | • Please clarify the active fire protection arragements specific to experiments • Please clarify firefighting capability, responsibilities and organisation (such as onsite internal fire brigade, organisation between onsite and offsite firefighters, etc.), including criteria for deploying onsite and offsite firefighting resources, how coordination is achieved between the plant personnel and the offsite resources, if the plant internal firefighting capability is supported by offsite resources, how it is ensured that the firefighting resources are familiar with the hazards of the plant, and adequate time for security control is provided, safety culture and how the above are reinforced through emergency training, drills and exercises.
TR-E-1741 | AFP | TR | Active fire protection | Licensee and regulatory experience |  | Research reactor | İTÜ Research Reactor |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
UA-E-1742 | FSA | UA | Fire safety analysis | Licensee and regulatory experience |  | NPP | Rivne 4 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UA-E-1743 | FSA | UA | Fire safety analysis | Licensee and regulatory experience |  | NPP | South Ukrainian NPP 1 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UA-E-1744 | FSA | UA | Fire safety analysis | Licensee and regulatory experience |  | Research reactor | WWR-M Instittute for nuclear research |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UA-E-1745 | PFP | UA | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Rivne 4 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UA-E-1746 | PFP | UA | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | South Ukrainian NPP 1 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UA-E-1747 | PFP | UA | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Rivne 4 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UA-E-1748 | PFP | UA | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | South Ukrainian NPP 1 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UA-E-1749 | PFP | UA | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Rivne 4 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UA-E-1750 | PFP | UA | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | South Ukrainian NPP 1 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UA-E-1751 | PFP | UA | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Rivne 4 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UA-E-1752 | PFP | UA | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | South Ukrainian NPP 1 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UA-E-1753 | PFP | UA | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | WWR-M Instittute for nuclear research | Please provide more information on the practise of temporary fire load management.
UA-E-1754 | PFP | UA | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Research reactor | WWR-M Instittute for nuclear research |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UA-E-1755 | PFP | UA | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | WWR-M Instittute for nuclear research | How are the fire classes for fire barriers defined?
UA-E-1756 | PFP | UA | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Research reactor | WWR-M Instittute for nuclear research |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UA-E-1757 | PFP | UA | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | WWR-M Instittute for nuclear research | No NAR. But same question than the other RR can be asked regarding the TOI : Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers?
UA-E-1758 | PFP | UA | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Research reactor | WWR-M Instittute for nuclear research |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UA-E-1759 | PFP | UA | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Research reactor | WWR-M Instittute for nuclear research |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UA-E-1760 | PFP | UA | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Spent fuel storage - dry | ISF-2 SSE ChNPP |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UA-E-1761 | PFP | UA | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Spent fuel storage - dry | ISF-2 SSE ChNPP |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UA-E-1762 | PFP | UA | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Spent fuel storage - dry | ISF-2 SSE ChNPP |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UA-E-1763 | PFP | UA | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Spent fuel storage - dry | ISF-2 SSE ChNPP |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UA-E-1764 | AFP | UA | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Rivne 4 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
UA-E-1765 | AFP | UA | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | South Ukrainian NPP 1 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
UA-E-1766 | AFP | UA | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Rivne 4 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UA-E-1767 | AFP | UA | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | South Ukrainian NPP 1 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UA-E-1768 | AFP | UA | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Rivne 4 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
UA-E-1769 | AFP | UA | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | South Ukrainian NPP 1 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
UA-E-1770 | AFP | UA | Active fire protection | Licensee and regulatory experience |  | NPP | Rivne 4 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
UA-E-1771 | AFP | UA | Active fire protection | Licensee and regulatory experience |  | NPP | South Ukrainian NPP 1 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
UA-E-1772 | AFP | UA | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Research reactor | WWR-M Instittute for nuclear research |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
UA-E-1773 | AFP | UA | Active fire protection | Fire suppression (TS 3.2.2) |  | Research reactor | WWR-M Instittute for nuclear research |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UA-E-1774 | AFP | UA | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Research reactor | WWR-M Instittute for nuclear research |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
UA-E-1775 | AFP | UA | Active fire protection | Licensee and regulatory experience |  | Research reactor | WWR-M Instittute for nuclear research |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors.
UA-E-1776 | AFP | UA | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | ISF-2 SSE ChNPP |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
UA-E-1777 | AFP | UA | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | ISF-2 SSE ChNPP |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UA-E-1778 | AFP | UA | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | ISF-2 SSE ChNPP |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
UA-E-1779 | AFP | UA | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | ISF-2 SSE ChNPP |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
UK-E-1780 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Hunterston B NPP |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UK-E-1781 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Dounreay Prototype Fast Reactor | p135, the licensee stated that fire loading is largely contained in discrete accumulations. Is there a guide to justify/explain that fire loads are far enough from each other ?
UK-E-1782 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Dounreay Prototype Fast Reactor |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UK-E-1783 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | Decommissioning | Pile 1 Sellafield |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the decommissioning facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and decommissioning activities: In how far and how have risks from transient combustibles and decommissioning activities (ignition sources by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in fire the analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences: Please provide description for: a) Methodology of assessment of the radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the analysis. 12. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for facilities under decommissioning in your country? c) Some countries mention that a periodic safety review is performed for decommissioning facilities. It would be good to know more on the applicability and periods of performance of PSR for such facilities in your country in order to identify potential strengths. 13. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UK-E-1784 | FSA | UK | Fire safety analysis | Assumptions (TS 02.3) |  | Fuel fabrication facilities | Springfields Fuel Ltd | Fire compartmentation p94, Springfields Fuels Ltd states that it requires the use of non-hydrogenous firefighting agents in buildings where there is the potential for a criticality event. It provides 50 kg dry powder trolley units for site fire service use… How is the amount of powder determined (Lack of non-hydrogenous firefighting agents - Rocky flats facility fire feedback)?
UK-E-1785 | FSA | UK | Fire safety analysis | Assumptions (TS 02.3) |  | Fuel fabrication facilities | Springfields Fuel Ltd | • II2.3.3: models, data consequences are not discussed (referring to II-2.3.2 -> where can these be found ?) • II-2.3.4, p.95: there is no information on main results/dominant events
UK-E-1786 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | Fuel fabrication facilities | Springfields Fuel Ltd |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. b) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? 2. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 3. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 4. Radiological/criticality consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. c) Criticality: How has the criticality aspect been taken into account in the analysis and the impact on the fire protection features. d) How have the radiological hazards (radiological, criticality) been taken into account in the development of the fire brigade procedures (onsite, offsite brigades)? 5. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 6. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 7. Results and revisions of the Fire Safety Analyses, additional analyses: Please provide details about: a) Treatment of modifications and changes in the installations as well as updates of the analysis should be addressed. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for fuel fabrication facilities in your country? 8. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UK-E-1787 | FSA | UK | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Sizewell B | Can you please provide information on how ongoing updates and/or studies are handled? What is the corresponding timetable?
UK-E-1788 | FSA | UK | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Sizewell B | Is a reactor trip assumed to occur in the event of (any) fire? What is the overall risk contribution from fire scenarios? Is the SZB PSA updated in the same way as the HY2 PSA?
UK-E-1789 | FSA | UK | Fire safety analysis | Assumptions (TS 02.1) |  | NPP | Hinkley Point C | If possible, can you please provide some examples of plant strength/weaknesses regarding fire?
UK-E-1790 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | NPP | Heysham 2 |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UK-E-1791 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | NPP | Sizewell B |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UK-E-1792 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | NPP | Hinkley Point C |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UK-E-1793 | FSA | UK | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) | p114, Sellafield Ltd. reports that fire service intervention is considered a defence in depth mitigation measure, but not claimed, designated or substantiated in its safety cases. DiD is a fire safety principle and includes fire extinguishing. So why fire services, are not claimed in the safety case ? What would it change if the fire services were designated in the safety case?
UK-E-1794 | FSA | UK | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) | p.113: Regarding the semi-quantative fire loading assessment, what was the basis for decision making when assigning values for different areas? p.118: What is the worst case scenario for the Waste Victification plant and the others? p.119: There is a programme in place to implement revised nuclear fire safety assessments (prompted by a finding from the 2022 periodic safety case review), emergent work may arise. Can you elaborate on those findings and on the topics, which were revised? p.123: Since Sellafield Ltd. adopted the above classification criteria in 2018, there have been no recordable fires in Waste Vitrification Plants, Encapsulation Plants, Sellafield Product and Residue Store or BEPPS-DIF nuclear facilities.What about events prior to 2018?
UK-E-1795 | FSA | UK | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) | p104, The review identifies fire requirements such as nuclear fire compartments/barriers and passive fire protection of SSCs. Are the safety requirements for fire detection/suppression regarding DiD principles ?
UK-E-1796 | FSA | UK | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) | p. 123: Since Sellafield Ltd. adopted the above classification criteria in 2018, there have been no recordable fires in Waste Vitrification Plants, Encapsulation Plants, Sellafield Product and Residue Store or BEPPS-DIF nuclear facilities.What about events prior to 2018?
UK-E-1797 | FSA | UK | Fire safety analysis | Assumptions (TS 02.5) |  | Waste | Sellafield Product and Residues Store (interim storage) | p.118: What is the worst case fire scenario for SPRS? p. 123: Since Sellafield Ltd. adopted the above classification criteria in 2018, there have been no recordable fires in Waste Vitrification Plants, Encapsulation Plants, Sellafield Product and Residue Store or BEPPS-DIF nuclear facilities.What about events prior to 2018?
UK-E-1798 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UK-E-1799 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UK-E-1800 | FSA | UK | Fire safety analysis | Licensee and regulatory experience |  | Waste | Sellafield Product and Residues Store (interim storage) |  | [generic/general]: 1. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the Fire Protection structures, systems and components (SSCs)? b) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? c) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. d) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? 2. Applicability of PSA: According to the Technical Specifications of the TPR II, performance of Fire Probabilistic Safety Assessment is considered mandatory for NPPs. However, it would be useful to know if Fire PSA have been performed or are intended to be performed for the waste storage facilities. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 8. Radiological consequences: Please provide description for: a) Assessment of radiological consequences of a fire in the fire analysis and criteria and corresponding threshold values applicable in the success criteria. b) Radiological confinement measures during a fire. 9. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed – and, as far as available, also from other nuclear installations – is considered in the fire analysis. 11. Results and revisions of the Fire Safety Analyses and additional analyses: Please provide details about: a) The process carried out to update the fire analysis. b) Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for waste storage facilities in your country? c) Some countries mention that a periodic safety review is performed for waste storage facilities. It would be good to know more on the applicability and frequency of PSR for such facilities in your country in order to identify potential strengths. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified.
UK-E-1801 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Hunterston B NPP | *Page 11. Key parameters. - Please describe the intended end state of decommissioning. - Year of authorization for decommissionong is not mentioned (May be there isn't one yet.) * Page 138, section A-I-3.1.1 Design considerations and prevention means. Assumption 3/. Who is responsible for carrying out the independent verification?. *Page 139, section A-I-3.1.2 Overview of arrangements for management and control of fire load and ignition sources. assumption 3/. "EDF NGL identifies and demarcates predetermined laydown areas at each location for temporary and permanent storage." What are the main criteria taken into account for the preselection of storage areas? For example, is it taken into account for the preselection of areas that the fire loads are as far away as possible from SSCs important for safety? , or the proximity tofire hose stations is taken into account if there are no fixed extinguishing systems? Proximity to ignition sources?
UK-E-1802 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Hunterston B NPP |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1803 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Dounreay Prototype Fast Reactor | *Page 25. Key parameters. - Please describe the intended end state of decommissioning. - Year of authorization for decommissioning is not mentioned (May be there isn't one yet.) *Page 172. Section F-I Dounreay; F-I-3.1.1 Design considerations and prevention means. Assumption 3/. " DFARS are the Appointed Persons for issuing hot works permits after an inspection of the work area and equipment. All fire safety prevention measures are detailed on the permit. " Is the possibility of carrying out alternative work without risk of fire evaluated?. *Page 172 F-I-3.1.2 Overview of arrangements for management and control of fire load and ignition sources. Assumption 3/. "Dounreay reports that there are no limits on fire loading at PFR. There is a site general requirement to minimise combustibles". Why are there no fire load limits set for the PFR?
UK-E-1804 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Dounreay Prototype Fast Reactor | Section F-I-3.1.2; P.173; (2). Please provide information on what fire safety measures are in place to protect against a possible ignition and fire of stored sodium and which remained in the pool. Section F-I-3.1.2; p.172; (3). Why are there no fire load limits set for the PFR?
UK-E-1805 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Dounreay Prototype Fast Reactor |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1806 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Pile 1 Sellafield | *Page 18. Key parameters. - Please describe the intended end state of decommissioning. - Year of authorization for decommissionong is not mentioned (I guess there isn't one yet.) | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1807 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Pile 1 Sellafield | Section E-I-3.3.1. Please provide information about types of permanent and temporary fire loads and potential ignitions source.
UK-E-1808 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Decommissioning | Pile 1 Sellafield |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1809 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Hunterston B NPP | *Page 256. Section A-I-3.3.1.2 Description of fire compartments and/or cells design and key features ( Maintenance of access routes). SZB has pressurised stairwells to prevent smoke ingress. How does HNB deal with smoke ingressing escape routes?
UK-E-1810 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Hunterston B NPP | Section A-I-3.3.1. Please provide information about fire compartmentation of Hunterstorn B NPP. Section A-I-3.3.1.1; P.253; (1). What design and safety cases have been updated throughout the life of the Hunterston B NPP?
UK-E-1811 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Hunterston B NPP |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1812 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Dounreay Prototype Fast Reactor | *Page 287. Section F-I-3.3.1.2 Description of fire compartments and/or cells design and key features. Assumptions 1/ and 2/. “Due to the open plan nature of the main processing areas of the PFR complex, there are only a small number of fire barriers located in the building though these were not installed as fire barriers. • A 60-minute fire barrier separates the Reactor Hall and Decontamination Hall from the adjacent SGB and Surveillance Centre/Admin Building. • A number of 30-minute fire barriers are located in the Caesium Removal Plant (CRP) and the SDP…..” Is the fire rate commensurate with the fire risks (fire severity) present in the area? Are there other elements like fire doors, sealings... between these areas? Just in case, what is their fire rate? *Page 287. Section F-I-3.3.1.2 Description of fire compartments and/or cells design and key features. Assumption 4/. "Access routes are maintained by utilising delineated markings. These markings lead personnel to exits, from which they can progress through compartmentation to another building." How is ensured that routes are maintained as decommissioning changes occur?
UK-E-1813 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Dounreay Prototype Fast Reactor | Section F-I-3.3.1. Please provide more detailed information about the fire compartmentations and about the fire barriers of compartments.
UK-E-1814 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Dounreay Prototype Fast Reactor |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1815 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Pile 1 Sellafield | *Page 282. Section E-I-3.3.1.2 Description of fire compartments and/or cells design and key features. Assumption 4/. "Firefighting access routes are required to be fire sterile and within fire resisting structures as required by mandatory legislation. At Sellafield Ltd, this requirement is managed by the dutyholder specifically the Building Manager and Safety Case Manager to ensure implementation of these requirements as specified in the fire analyses." Please provide information on how access routes are maintained as changes occur as a result of decommissioning.
UK-E-1816 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Decommissioning | Pile 1 Sellafield |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1817 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Hunterston B NPP |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UK-E-1818 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Dounreay Prototype Fast Reactor |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UK-E-1819 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Pile 1 Sellafield |  | [generic]: o Maintenance/Access/Inspection of fire dampers (if relevant): What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UK-E-1820 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Decommissioning | Pile 1 Sellafield | Section E-I-3.3.2; (4). What is the fire resistance rating of the ventilation systems?
UK-E-1821 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Hunterston B NPP | * Page 260. Section A-I-3.3.3.1 Overview of strengths and weaknesses. Assumption 1/. Is written for HY2 and SZB, but not for HNB. Please provide this information for HNB. *Page 260. Section A-I-3.3.3.2 Lessons learned from events, reviews fire safety related missions, etc. Assumption 1/. "Lessons learnt are addressed in Section A-I-4.3.3.1." This section as mentioned could be found in the NAR. So lessons learnt could be missing. Please provide clarity about the HNB lessons learned in the NAR or if they are missing provide this information.
UK-E-1822 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Hunterston B NPP |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UK-E-1823 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Dounreay Prototype Fast Reactor |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UK-E-1824 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Pile 1 Sellafield |  | [generic]: o Decommissioning: fire safety strategy, with indications of development for decommissioning activities Describe which elements of the fire safety strategy (in the areas of prevention, passive safety and ventilation as covered by the NAR) have/had to be further developed or modified for the decommissioning phase and how? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UK-E-1825 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Decommissioning | Pile 1 Sellafield | Section n E-I-3.1.4.2; P.171; (2). Please provide information about fire events at Sellafield related to the implementation of the process for management of hot work. Please provide information on the root causes of fires that occurred during the hot cutting.
UK-E-1826 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel enrichment facilities | Urenco enrichment | page 148 /Section C-I-3.1.2/3/Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements.
UK-E-1827 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel enrichment facilities | Urenco enrichment |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1828 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel enrichment facilities | Urenco enrichment | page 267/Section C-I-3.3.1.1/1,2/What are fire-resistances for fire barriers (walls, fire doors, fire dampers...) in all buildings with radiological risks? page 267/Section C-I-3.3.1.2/1,2,7/Describe deficiencies regarding fire barriers (walls, fire doors, penetrations, fire dampers...)? Describe improvements or modifications regarding fire barriers (walls, fire doors, penetrations fire dampers...)?
UK-E-1829 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel enrichment facilities | Urenco enrichment |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1830 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Springfields Fuel Ltd | p.157-158, topic 2/: The only means of fire prevention described is about hot works. Are there no other means at all? There is no info on design considerations. Please provide information on the above. Please describe the practice for the management of temporary fire loads.
UK-E-1831 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Springfields Fuel Ltd | C-II-3.1.2, p.159, topic 3/: 'fire risk assessments that are undertaken on a three yearly basis'. Is this correct, since this seems not to be described in the fire safety analysis part (only 10 yearly review seems to mentioned)? If yes, what does this three yearly assessment include?
UK-E-1832 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel fabrication facilities | Springfields Fuel Ltd |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1833 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | Springfields Fuel Ltd | p.271, C-II-3.3.1.2: should describe fire compartments design and key features, but there is no information given: which compartments, fire resistance values for compartments (incl. those with nuclear materials), doors, penetrations, ... ? Typical values are given on p.273, but it is not clear if typical in regulation, or effectively applied as such at Springfields. Please provide this information.
UK-E-1834 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel fabrication facilities | Springfields Fuel Ltd |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1835 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Fuel fabrication facilities | Springfields Fuel Ltd | p276: In 2011 there were approximately 71 fire dampers in the facility with 24 fire dampers being thermal link/frangible bulb type. Are other fire dampers (=without thermal fuse) closed manually or are they connected to a fire/smoke detection system?
UK-E-1836 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Fuel fabrication facilities | Springfields Fuel Ltd |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UK-E-1837 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Fuel reprocessing facilities | Magnox plant - Sellafield |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1838 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Fuel reprocessing facilities | Magnox plant - Sellafield |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1839 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Heysham 2 | * Page 138, section A-I-3.1.1 Design considerations and prevention means. Assumption 3/. Who is responsible for carrying out the independent verification?. *Page 139, section A-I-3.1.2 Overview of arrangements for management and control of fire load and ignition sources. assumption 3/. "EDF NGL identifies and demarcates predetermined laydown areas at each location for temporary and permanent storage." What are the main criteria taken into account for the preselection of storage areas? For example, is it taken into account for the preselection of areas that the fire loads are as far away as possible from SSCs important for safety? , or the proximity to hose stations is taken into account if there are no fixed extinguishing systems? Proximity to ignition sources?
UK-E-1840 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Heysham 2 | 3/ Are there any fire risks related to hydrogen?
UK-E-1841 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Heysham 2 |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1842 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Sizewell B | * Page 138, section A-I-3.1.1 Design considerations and prevention means. Assumption 3/. Who is responsible for carrying out the independent verification?. *Page 139, section A-I-3.1.2 Overview of arrangements for management and control of fire load and ignition sources. assumption 3/. "EDF NGL identifies and demarcates predetermined laydown areas at each location for temporary and permanent storage." What are the main criteria taken into account for the preselection of storage areas? For example, is it taken into account for the preselection of areas that the fire loads are as far away as possible from SSCs important for safety? , or the proximity to hose stations is taken into account if there are no fixed extinguishing systems? Proximity to ignition sources?
UK-E-1843 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Sizewell B | 3/ Are there any fire risks related to hydrogen?
UK-E-1844 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Sizewell B |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1845 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | NPP | Hinkley Point C |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1846 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Heysham 2 | *Page 255. Section A-I-3.3.1.1 Design approach (fire barrier manteinance). Assumption 5/ "EDF NGL reports that all fire barriers are inspected, tested and maintained to the relevant EDF NGL Company Technical Standard." How often are inspections carried out? What percentage of barriers are covered in each inspection? *Page 256. Section A-I-3.3.1.2 Description of fire compartments and/or cells design and key features ( Maintenance of access routes). Assumption 4/. The information mainly refers to the presence of fire protected stairwells. Are evacuation routes signposted on floor, doors, walls...? Is there an emergency lighting system? In which documents are these routes defined (emergency procedures)? SZB has pressurised stairwells to prevent smoke ingress. How HY2 deal with smoke ingressing into escape routes?
UK-E-1847 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Heysham 2 |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1848 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Sizewell B | *Page 255. Section A-I-3.3.1.1 Design approach (fire barrier manteinance). Assumption 5/. "EDF NGL reports that all fire barriers are inspected, tested and maintained to the relevant EDF NGL Company Technical Standard." How often are inspections carried out? What percentage of barriers are covered in each inspection? *Page 256. Section A-I-3.3.1.2 Description of fire compartments and/or cells design and key features ( Maintenance of access routes). Assumption 4/. The information mainly refers to the presence of fire protected stairwells. Are evacuation routes signposted on floor, doors, walls...? Is there an emergency lighting system? Where are these routes defined (emergency procedures)?
UK-E-1849 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Sizewell B |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1850 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | NPP | Hinkley Point C |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1851 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Heysham 2 |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UK-E-1852 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Sizewell B |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UK-E-1853 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | NPP | Hinkley Point C |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UK-E-1854 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Heysham 2 | *Page 260. Section A-I-3.3.3.2 Lessons learned from events, reviews fire safety related missions, etc. Assumption 1/. "Lessons learnt are addressed in Section A-I-4.3.3.1." I am not able to find this mentioned section in the NAR. So lessons learnt could be missing.
UK-E-1855 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Heysham 2 |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UK-E-1856 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Sizewell B | *Page 260. Section A-I-3.3.3.2 Lessons learned from events, reviews fire safety related missions, etc. Assumption 1/. "Lessons learnt are addressed in Section A-I-4.3.3.1." I am not able to find this mentioned section in the NAR. So lessons learnt could be missing.
UK-E-1857 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Sizewell B |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UK-E-1858 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | NPP | Hinkley Point C |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UK-E-1859 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) | Section E-I-3.1.2; P.168. Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined?
UK-E-1860 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1861 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) | Section E-I-3.1.2; P.168. Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined?
UK-E-1862 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1863 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Sellafield Product and Residues Store (interim storage) | Section E-I-3.1.2; P.168. Please provide information about fire loads and the different types of potential ignition sources of the facility. What are the permissible limits for permanent and temporary fire loads and how are they determined?
UK-E-1864 | PFP | UK | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) |  | Waste | Sellafield Product and Residues Store (interim storage) |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications.
UK-E-1865 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) | Section E-I-3.3.1.2; P.282. Please provide information about the fire compartmentation for all buildings.
UK-E-1866 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1867 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) | Section E-I-3.3.1.2; P.282. Please provide information about fire compartmentation for all buildings.
UK-E-1868 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1869 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Sellafield Product and Residues Store (interim storage) | Section E-I-3.3.1.2; P.282. Please provide information about fire compartmentation for all buildings.
UK-E-1870 | PFP | UK | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) |  | Waste | Sellafield Product and Residues Store (interim storage) |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers?
UK-E-1871 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UK-E-1872 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UK-E-1873 | PFP | UK | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) |  | Waste | Sellafield Product and Residues Store (interim storage) |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made?
UK-E-1874 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UK-E-1875 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UK-E-1876 | PFP | UK | Fire prevention/Passive Fire Protection | Licensee and regulatory experience |  | Waste | Sellafield Product and Residues Store (interim storage) |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries).
UK-E-1877 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Hunterston B NPP |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
UK-E-1878 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Hunterston B NPP | It is difficult to identify systematic information describing active fire safety issues for this facility. Only general information about the facility is provided. Please provide more systematic information for this facility in this report.
UK-E-1879 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Dounreay Prototype Fast Reactor |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
UK-E-1880 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Dounreay Prototype Fast Reactor | Paragraph 2.6. For the Dounreay Prototype Fast Reactor, only general fire safety conclusions are given without a description of the fire detection and alarm system. Please provide information on which these conclusions are based.
UK-E-1881 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Decommissioning | Pile 1 Sellafield |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
UK-E-1882 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Hunterston B NPP |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1883 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Dounreay Prototype Fast Reactor |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1884 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Dounreay Prototype Fast Reactor | Paragraph 2.6. For the Dounreay Prototype Fast Reactor, only general fire safety conclusions are given without a description of the fire suppression issues. Please provide information on which these conclusions are based.
UK-E-1885 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | Decommissioning | Pile 1 Sellafield |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1886 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Hunterston B NPP |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
UK-E-1887 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Dounreay Prototype Fast Reactor |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
UK-E-1888 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Decommissioning | Pile 1 Sellafield |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. • What evaluation has been carried out in order to adapt / modify the active fire protection strategy considering the evolution from operation to decommissioning (including changes in the new fire safety analysis, changes in fire loads, ignition sources, radiological environment, decommissioning activities, …)
UK-E-1889 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Hunterston B NPP |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
UK-E-1890 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Dounreay Prototype Fast Reactor |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
UK-E-1891 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | Decommissioning | Pile 1 Sellafield |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
UK-E-1892 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Fuel reprocessing facilities | Magnox plant - Sellafield |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
UK-E-1893 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | Fuel reprocessing facilities | Magnox plant - Sellafield |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1894 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | Fuel reprocessing facilities | Magnox plant - Sellafield | Need more information about extinguishing means. Only automatic or semi automatic means are mentioned. What about fire extinguisher, water hozes, water pipes, vehicules, etc ... ? p232-233: Are there any safety reasons to not use automatic fire suppression systems instead of manual systems ? same for dampers.
UK-E-1895 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Fuel reprocessing facilities | Magnox plant - Sellafield |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
UK-E-1896 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Fuel reprocessing facilities | Magnox plant - Sellafield | Fire brigade : It is not very clear if some people of this team are exclusively dedicated to fire fighting or can also participate to other rescue operations. Please clarify the issue.
UK-E-1897 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | Fuel reprocessing facilities | Magnox plant - Sellafield |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
UK-E-1898 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Heysham 2 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
UK-E-1899 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Heysham 2 | Is the detection system covered all rooms or not ? Is it adressable ? Is it reported to the fire brigade. This chapter about detection system is very unclear. Necessary to ask simple question on what is important instead of generic description of the system. p 182 : "EDF NGL states that the fire protection panels are backed up from their own local batteries": how long time for batteries ??
UK-E-1900 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Heysham 2 | Page 185 of pdf, section A-I-3.2.1.9, assumption 4. Explain more in depth the types of compensatory measures in case of impairment of fire detection systems.
UK-E-1901 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Sizewell B |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
UK-E-1902 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Sizewell B | Is the detection system covered all rooms or not ? Is it adressable ? Is it reported to the fire brigade. This paragraph is unclear p 182: no batteries ? what about standardization? batteries are not mandatory ?? p 185: "Alternative provisions are assessed and deployed by means of fire risk assessments with reference to Technical Specification requirements and company specifications, which detail the period of time a detection and alarm system may be isolated and necessary compensatory measures to be deployed during the period of isolation or unavailability. Further detail is provided in the licensee self-assessment" : ??? what they do if system failed???
UK-E-1903 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Sizewell B | Page 185 of pdf, section A-I-3.2.1.9, assumption 4. Explain more in depth the types of compensatory measures in case of impairment of fire detection systems.
UK-E-1904 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Hinkley Point C |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems.
UK-E-1905 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Hinkley Point C | p 195 : is JDT seismically qualified ?
UK-E-1906 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | NPP | Hinkley Point C | Page 195 of pdf, section A-II-3.2.1.1, assumption 1. In general, are SSC important to safety covered by fire detectors? If not, please explain. - Page 196 of pdf, section A-II-3.2.1.1, assumption 1. “The system will also initiate pressurisation of access zones adjacent to the affected volume to facilitate personnel evacuation and emergency services intervention”. Please, describe more in depth this part of the fire detection system. Which access zones are over-pressured in case of fire? How are the signals transmitted and analyzed from the fire detectors to fans and dampers? Are the fans started automatically or manually? Are the air intake and smoke extraction dampers opened automatically? - Page 197 of pdf, section A-II-3.2.1.1, assumption 4. Explain the types of compensatory measures in case of impairment of fire detection systems.
UK-E-1907 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Heysham 2 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1908 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Heysham 2 | Fire suppression system: only sprinkler detailed, what about manual extinguisher, water hoses, hydrants, ...
UK-E-1909 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Heysham 2 | Page 186 of pdf, section A-I-3.2.2.2, assumption 1. The use of standpipe hoses inside the main buildings is not described. Please, describe the type of hoses, lengths, separation between them and other features. Are all SSC important to safety covered by the jet from at least one hose? - Page 187 of pdf, section A-I-3.2.2.2, assumption 2. Describe fire water tanks or other sources of supply; including their inventory, connections and other relevant features. - Page 187 of pdf, section A-I-3.2.2.2, assumption 2. Explain if the fire ring include a double supply to buildings containing safety related SSC’s; and if this ring have isolation valves, the aim being to be able to isolate part of the main ring for maintenance or repair. - Page 189 of pdf, section A-I-3.2.2.3, assumption 2. "There are no seismically qualified fire suppression systems at HNB/HY2 or SZB which are required to function to meet nuclear safety requirements". In the event of a safe shutdown earthquake (SSE), is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown or any similar provision? How does the fire brigade suppress fires in the event of a SSE? Are there other fire extinguishing provisions qualified against seismic events? - Page 189 of pdf, section A-I-3.2.2.4, assumption 3. Explain more in depth the types of compensatory measures in case of impairment of fire suppression systems.
UK-E-1910 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Sizewell B |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1911 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Sizewell B | Fire suppression system: only sprinkler detailed, what about manual extinguisher, water hoses, hydrants, ...
UK-E-1912 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Sizewell B | Page 186 of pdf, section A-I-3.2.2.2, assumption 1. The use of standpipe hoses inside the main buildings is not described. Please, describe the type of hoses, lengths, separation between them and other features. Are all SSC important to safety covered by the jet from at least one hose? - Page 187 of pdf, section A-I-3.2.2.2, assumption 2. Clarify the inventory of the two water reservoirs. - Page 187 of pdf, section A-I-3.2.2.2, assumption 2. Regarding fire pumps: describe electrical pumps and diesel-driven pumps; including flow and pressure, electrical supply, seismic category, separation between them and other relevant features. - Page 187 of pdf, section A-I-3.2.2.2, assumption 2. Explain if the fire ring include a double supply to buildings containing safety related SSC’s; and if this ring have isolation valves, the aim being to be able to isolate part of the main ring for maintenance or repair. - Page 189 of pdf, section A-I-3.2.2.3, assumption 2. "There are no seismically qualified fire suppression systems at HNB/HY2 or SZB which are required to function to meet nuclear safety requirements". In the event of a safe shutdown earthquake (SSE), is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown or any similar provision? How does the fire brigade suppress fires in the event of a SSE? Are there other fire extinguishing provisions qualified against seismic events? - Page 189 of pdf, section A-I-3.2.2.4, assumption 3. Explain more in depth the types of compensatory measures in case of impairment of fire suppression systems.
UK-E-1913 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Hinkley Point C |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1914 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | NPP | Hinkley Point C | Page 199 of pdf, section A-II-3.2.1.3, assumption 2. “Four firefighting water pumps (one per train with each train powered from a different division)”. “The pumps’ power supply is backed up from the emergency diesel generators, and two of the four are also backed up from the Ultimate Diesel Generator (UDG) in case of loss of the EDGs”. Which is the capacity of these pumps (100%, 50% or other)? Are they seismically qualified? Is each fire pump with its motor and controls located separately from the other fire pumps by fire resistant walls? In the control room, is there an alarm signal to indicate pumps running, driver unavailability, failure to start and low water pressure in the main external ring? - Page 200 of pdf, section A-II-3.2.1.5, assumption 3. Explain in general the types of compensatory measures in case of impairment of fire suppression systems.
UK-E-1915 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Heysham 2 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
UK-E-1916 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Heysham 2 | Page 191 of pdf, section A-I-3.2.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 191 of pdf, section A-I-3.2.3.2, assumption 4. "The specification lists the expected minimum firefighting skills and capabilities of the Incident Response teams". What are the firefighter qualifications, organization, fitness requirements, skills, duties during normal operation and training of the incident response team? Is there a professional onsite fire brigade or only offsite fire brigade? How far from the plant are the offsite fire services located? Which is the minimum staffing? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for the offsite fire services?
UK-E-1917 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Sizewell B |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
UK-E-1918 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Sizewell B | Page 191 of pdf, section A-I-3.2.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 191 of pdf, section A-I-3.2.3.2, assumption 4. "The specification lists the expected minimum firefighting skills and capabilities of the Incident Response teams". What are the firefighter qualifications, organization, fitness requirements, skills, duties during normal operation and training of the incident response teams? Is there a professional onsite fire brigade or only offsite fire brigade? How far from the plant are the offsite fire services located? Which is the minimum staffing? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for the offsite fire services?
UK-E-1919 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | NPP | Hinkley Point C |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
UK-E-1920 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | NPP | Heysham 2 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
UK-E-1921 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | NPP | Sizewell B |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
UK-E-1922 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | NPP | Hinkley Point C |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs.
UK-E-1923 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Spent fuel storage - dry | SZB dry store |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
UK-E-1924 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | Spent fuel storage - dry | SZB dry store |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1925 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Spent fuel storage - dry | SZB dry store |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...).
UK-E-1926 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | Spent fuel storage - dry | SZB dry store |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
UK-E-1927 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
UK-E-1928 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
UK-E-1929 | AFP | UK | Active fire protection | Fire detection and alarm (TS 3.2.1) |  | Waste | Sellafield Product and Residues Store (interim storage) |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)?
UK-E-1930 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1931 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1932 | AFP | UK | Active fire protection | Fire suppression (TS 3.2.2) |  | Waste | Sellafield Product and Residues Store (interim storage) |  | [generic] • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break ? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy.
UK-E-1933 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
UK-E-1934 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) | /3/ Regarding OPEX, malfunctions of fire protection equipment (e.g. from periodic inspections) were not discussed. Please provide additional information.
UK-E-1935 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
UK-E-1936 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) | /3/ Regarding OPEX malfunctions of fire protection equipment (e.g. from periodic inspections) were not discussed.
UK-E-1937 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Sellafield Product and Residues Store (interim storage) |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties.
UK-E-1938 | AFP | UK | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) |  | Waste | Sellafield Product and Residues Store (interim storage) | /3/ Regarding OPEX, malfunctions of fire protection equipment (e.g. from periodic inspections) were not discussed. Please provide additional information.
UK-E-1939 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | Waste | Sellafield High Level Waste Plant /Waste Vitrification Plant/ or Encapsulation (HLW) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
UK-E-1940 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | Waste | Sellafield Box Encapsulation Plant Product Store – Direct Import Facility (BEPPS-DIF (ILW – interim storage) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.
UK-E-1941 | AFP | UK | Active fire protection | Licensee and regulatory experience |  | Waste | Sellafield Product and Residues Store (interim storage) |  | [generic] Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems.

## Countries
Question ID | Reviewer (Country authorities) | Country/NAR | Fire Protection Thematic | Chapter and relevant section of TS (for experts' questions) | Page no. in NAR (if specified) | Installation type (NPP, RR, SFS…) | Installation name | Question - installation specific (experts' questions) | Question - General (including generic/general experts' questions for type of installation) | Country's response | Cross reference to to another question-reply (Question ID) | Any remarks
AT-C-1 | Poland | AT | 03.1 - Fire prevention |  | 30 |  |  |  | Can you elaborate and give examples of alternative fire safety measures that contractors use during their work?
AT-C-2 | Poland | AT | 03.2 - Active fire protection |  | 33 |  |  |  | How do you assess placement of fire detectors?
AT-C-3 | Poland | AT | 03.2 - Active fire protection |  | 34 |  |  |  | What kind of analyis lead to decision to use no authomatic extinguishing system and no plant fire brigade ?
AT-C-4 | Poland | AT | 03.4 - Licensee's experience |  | 42 |  |  |  | What the selection process of officers looks like? How do you ensure their sufficent qualifications?
BE-C-5 | Czech Republic | BE | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
BE-C-6 | Czech Republic | BE | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
BE-C-7 | Czech Republic | BE | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
BE-C-8 | Czech Republic | BE | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
BE-C-9 | Germany | BE | 01-General information |  | 19 |  |  |  | It is stated that a probabilistic fire hazard analysis, supplementing the deterministic approach, shall be carried out. However, this requirement applies to NPPs and is not binding for other nuclear facilities. Could Belgium please explain if using the PSA or other probabilistic methods in the safety analysis (especially fire safety) for BR2 are considered?
BE-C-10 | Germany | BE | 02- Fire safety analyses |  | 22 |  |  |  | The Report mentions that an update of the FHA for CNT3 in the framework of LTO (>2025) is ongoing. Could Belgium please inform whether this update has been finished in the meantime or when this update will be finalized?
BE-C-11 | Germany | BE | 02- Fire safety analyses |  | 22 or 24 ff. |  |  |  | Could Belgium please specify when the last FHA for the DE building has been performed and when the next FHA will be done?
BE-C-12 | Germany | BE | 02- Fire safety analyses |  | 24 ff. |  |  |  | Have there been any actions identified due a FHA for the DE building?
BE-C-13 | Germany | BE | 02- Fire safety analyses |  | 24 |  |  |  | The report mentions that a specific methodology adressing seismically-induced fires (SIF) is under development. Could Belgium please give further information when this methodology is expected to be available and applicable?
BE-C-14 | Germany | BE | 02- Fire safety analyses |  | 36 |  |  |  | BR2 is with thermal power of 125 MW one of the most powerful research reactors worldwide. In the NAR it is stated that the residual heat of the reactor can be evacuated to the pool by natural convection immediately after shutdown. Is it a common situation in a normal operation? Is the pump circulation not at all required for the residual heat removal? Could belgium please provide more information on the cooling capacity of the reactor?
BE-C-15 | Germany | BE | 02- Fire safety analyses |  | 38 |  |  |  | For BR2 Actions several recommendations/ actions due to fire safety assesment have been identified. The report mentions that these have not yet been fully completed. Could Belgium please give further information on the time that the implementation of all recommendations is expected to be finalized?
BE-C-16 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, pp. 3 -39 |  |  |  | Specification is needed how shutdown states of the reactor are treated.
BE-C-17 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, pp. 3 -39 |  |  |  | It should be described if and (if yes) which bounding scenarios are applied as basis for justification of the assessment.
BE-C-18 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, pp. 3 -39 |  |  |  | Information, in how far event combinations of fires and other hazards are considered is needed.
BE-C-19 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, pp. 3 -39 |  |  |  | Clarification in how far not only permanently present combustibles but also transient fire loads are considered in the fire safety analyses is needed.
BE-C-20 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, pp. 3 -39 |  |  |  | Precise information on the methods applied for analysis and assessment, particularly of direct and indirect fire effects, is missing.
BE-C-21 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, pp. 3 -39 |  |  |  | Clarification is needed which methods and analytical tools are applied for fire safety analyses.
BE-C-22 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, pp. 3 -39 |  |  |  | Information on how the direct and indirect fire effects are assessed and which methods and data are used is missing.
BE-C-23 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, pp. 3 -39 |  |  |  | Please clarify how plant modifications are considered/reflected in the updates of the PSR.
BE-C-24 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, pp. 3 -39 |  |  |  | Information is missing, if and how the operating experience with fires and fire protection related issues (not only from BR2 itself but also other relevant experience) is considered.
BE-C-25 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, p. 38 |  |  |  | Details on the licensee´s experience are missing.
BE-C-26 | Germany | BE | 02- Fire safety analyses |  | Regarding BR 2, pp. 38-39 |  |  |  | Details on how the regulatory body assesses the focus on conventional fire protection aspects and the result of this assessment are missing.
BE-C-27 | Germany | BE | 02- Fire safety analyses |  | Regarding Tihange 3, pp. 22-37 |  |  |  | The main results of the Fire PSA are mentioned. However, justification for these are not given. More information for result justification is needed.
BE-C-28 | Germany | BE | 02- Fire safety analyses |  | Regarding Tihange 3, pp. 22-37 |  |  |  | The basis for the action plan should also be provided.
BE-C-29 | Germany | BE | 02- Fire safety analyses |  | Regarding Tihange 3, pp. 22-37 |  |  |  | How are direct and indirect fire effects. considered in the analyses?
BE-C-30 | Germany | BE | 02- Fire safety analyses |  | Regarding Tihange 3, pp. 22-37 |  |  |  | Which plant design weaknesses regarding fire protection have resulted in plant modifications?
BE-C-31 | Germany | BE | 02- Fire safety analyses |  | Regarding Tihange 3, pp. 22-37 |  |  |  | Information on the operating experience from Tihange 3 and other installations from fire events and events with deterioration of fire protection features and their consideration in fire safety analyses should be provided (as generic information)..
BE-C-32 | Germany | BE | 02- Fire safety analyses |  | Regarding Tihange 3, pp. 22-37 |  |  |  | There is a lack of considering fire and fire protection related operating experience adequately within FHA and Fire PSA in the past. Clarity is needed on how and when this has been or is being resolved.
BE-C-33 | Germany | BE | 02- Fire safety analyses |  | Regarding KCD3, pp. 22-37 |  |  |  | In the NAR, it is briefly mentioned that the design basis earthquake (DBE) has to be considered. However, clarification on the general consideration of combinations of fires and other hazards in the safety analyses needs to be given.
BE-C-34 | Germany | BE | 02- Fire safety analyses |  | Regarding KCD3, pp. 22-37 |  |  |  | Information on the operating experience from KCD3 and other installations from fire events and events with deterioration of fire protection features and their consideration in fire safety analyses should be provided.
BE-C-35 | Germany | BE | 02- Fire safety analyses |  | Regarding KCD3, pp. 22-37 |  |  |  | Information how the performance levels are achieved through the adopted design and plant layout is missing.
BE-C-36 | Germany | BE | 02- Fire safety analyses |  | Regarding KCD3, pp. 22-37 |  |  |  | Consideration of direct and indirect fire effects as well as of permanent and transient fire loads and potential ignition sources is missing.
BE-C-37 | Germany | BE | 02- Fire safety analyses |  | Regarding KCD3, pp. 22-37 |  |  |  | It is mentioned that weaknesses were identified by the FHA and Fire PSA. However, these mainly concern the methodologies for the analyses. Details on the plant weaknesses are not provided. Clarification and additional information is needed.
BE-C-38 | Germany | BE | 02- Fire safety analyses |  | Regarding SCG, p. 40 |  |  |  | On p. 40 of the NAR the fire resistance of the fuel containers is given with 600 °C for a period of 1 h. Could you please justify the approach? Remark: This temperature is below the temperature of 800 °C from IAEA requirements for transport and below temperatures of developed compartment fires.
BE-C-39 | Germany | BE | 03.1 - Fire prevention |  | 44 |  |  |  | - 3.1.1.1 Could Belgium please explain what are maintenance intervalls for batteries (e.g. fill level of battery acid, charge status, sample checks or replacement every 5 years in general?)?
BE-C-40 | Germany | BE | 03.1 - Fire prevention |  | 45 + 46 |  |  |  | Regarding the alarm of the installed system to measure flammable gases (Hydrogen) there is a difference between CNT3 (alarm is set at 2%) and KCD3 (alarm is set at 3%). Could Belgium please explain why this difference occurs?
BE-C-41 | Germany | BE | 03.1 - Fire prevention |  | 45 |  |  |  | - 3.1.1.1 - Could Belgium explain who is at CNT3 responsible for the installation of the mobile H2-recombinator and who decides to install?
BE-C-42 | Germany | BE | 03.1 - Fire prevention |  | 48 |  |  |  | - 3.1.1.2 - Could Belgium explain why there are only 30min for observation after hot work? Smouldering fire is characterized for durations of hours until ingnition.
BE-C-43 | Germany | BE | 03.1 - Fire prevention |  | 49 |  |  |  | The report mentions that a harmonization process on the fire load storage policies of the Doel and Tihange sites is ongoing. Could Belgium please specify when this harmonzation process started and is expected to be finalized?
BE-C-44 | Germany | BE | 03.1 - Fire prevention |  | Regarding BR2, pp. 57-58 |  |  |  | It is not precisely stated how (permanent as well as transient) fire loads are separated/segregated from potential ignition sources or how that is ensured by which requirement.
BE-C-45 | Germany | BE | 03.1 - Fire prevention |  | Regarding Tihange 3 & KCD 3, p. 44 |  |  |  | On p. 44 of the NAR it is reported: "As it is not always possible to maintain a sufficient distance between the devices and the bundles of wires of different trains, use is made of screens made of fireproof material to separate them. The actual crossing of the cables is filled with fire-resistant materials." How are these compensatory measures qualified?
BE-C-46 | Germany | BE | 03.1 - Fire prevention |  | Regarding KCD 3, p. 46 |  |  |  | On p. 46 of the NAR it is reported that the alarm for hydrogen in the reactor building is set 3 % (cf. UEL 4 %) which is quite high also in comparison to Tihange (2 % limit). Could provide information how the value is justified?
BE-C-47 | Germany | BE | 03.1 - Fire prevention |  | Regarding Tihange 3 & KCD 3, p. 45 |  |  |  | Could you add the fire specific characteristics of the turbine oil used?
BE-C-48 | Germany | BE | 03.1 - Fire prevention |  | Regarding SCG, p. 59 |  |  |  | On p. 59 of sect. "3.1.4.1. Design considerations and prevention means": By which approach a kerosine fire was defined to be covered by a temperature of 600 °C for a period of 1 h?
BE-C-49 | Germany | BE | 03.2 - Active fire protection |  | 69-70 |  |  |  | According to the report at CNT3 a second intervention team (ESI) exists. As the members also work as voluntary firefighters for an external fire brigade are there special measures taken if they should act - due to an fire somewhere else - as firefighters outside the plant and at the same time a fire might occur at the plant?
BE-C-50 | Germany | BE | 03.2 - Active fire protection |  | 70 |  |  |  | For KCD3 the public fire brigade is located in the nearby town of Beveren. Could Belgium please specify how many people are permanently located there and how they are informed, especially who at KCD3 decides whether the public fire brigade is needed?
BE-C-51 | Germany | BE | 03.2 - Active fire protection |  | 75 |  |  |  | - 3.2.1.3 CNT3/KCD3 but all installations: Who is responsible to keep documents (fire plans, etc.) up to date and is responsible to share with all stakeholders (onsite fire brigade, public fire brigade, regulator)?
BE-C-52 | Germany | BE | 03.2 - Active fire protection |  | 75 |  |  |  | The Belgian NAR states: "As the public fire brigade is located across the street of the Tihange site, there is no need for a procedure to give directions to the public fire brigade to come to the site." This statement sounds a little bit strange and contradictory. As described on p. 70 for the CNT site, the external fire brigade is "systematically called upon for each fire event unless otherwise decided based on the assessment of the situation by the ESI." Is this description a defined, existing procedure with a clear direction for the extrenal fire brigade?
BE-C-53 | Germany | BE | 03.2 - Active fire protection |  | 77 |  |  |  | - 3.2.1.3 How is it ensured that people with necessary keys are available in case of an emergency or fire event? (stay at place, no other responsibilities, etc.) Most events happen without an anouncement.
BE-C-54 | Germany | BE | 03.2 - Active fire protection |  | 81 |  |  |  | - 3.2.2.2 Is it ensured that canal and large surface waters can be reached at all times/weahter conditions (e.g. snow) and are the ways mantained (free of trees, bushes, etc.)?
BE-C-55 | Germany | BE | 03.2 - Active fire protection |  | 81 |  |  |  | For BR2 the report describes that a large water transport system can foresee an infinite water supply of 4000 l/min up to 8000 l/min as the site of SCK CEN is located very close to a canal and a set of large surface waters. Is this also feasible in a situation during long, dry heat periods, i.e. regarding dropped water levels in external water supplies (possible is also climate change)?
BE-C-56 | Germany | BE | 03.2 - Active fire protection |  | 84 ff. |  |  |  | How much time does it take in general from information of an extrenal fire brigade until arrival of external support at BR2? Are there exercises performed with an external fire brigade taking into account the special situation at BR2 (site access)?
BE-C-57 | Germany | BE | 03.2 - Active fire protection |  | Regarding BR2, pp. 78-87 |  |  |  | This section is very detailed (perhaps a little bit too much on the extinguishing systems), providing data on regular inspection periods is quite useful. This is a good example for a meaningful NAR.
BE-C-58 | Germany | BE | 03.2 - Active fire protection |  | Regarding BR2, p. 82 |  |  |  | What is the reason/basis for relatively long inspection periods (most yearly) of the fire extinguishing systems and equipment?
BE-C-59 | Germany | BE | 03.2 - Active fire protection |  | Regarding BR2, p. 83 |  |  |  | Parts on the texts on fire protection for the experiments would better fit in the corresponding sub-section of fire safety analyses.
BE-C-60 | Germany | BE | 03.2 - Active fire protection |  | Regarding Tihange 3 & KCD 3, pp. 61-62 |  |  |  | Are the fire detection systems designed against earthquake?
BE-C-61 | Germany | BE | 03.2 - Active fire protection | [5 empty] | Clarification is needed, in which areas which types of fire detectors are installed; however, the overall number of detector seems to be adequate.
BE-C-62 | Germany | BE | 03.3 - Passive fire protection |  | Regarding BR2, p. 97 |  |  |  | Information how the fire resistance rating is estimated is missing. Particularly in comparison to the information given on active fire protection, the information is too limited and does not reflect the requirements of the Technical Specification for this NAR section.
BE-C-63 | Germany | BE | 03.3 - Passive fire protection |  | Regarding BR2, p. 97 |  |  |  | How is the function of the command center in the reactor building ensured for 1 hour? Clarification is needed.
BE-C-64 | Germany | BE | 03.3 - Passive fire protection |  | Regarding Tihange 3 & KCD 3, p. 89 |  |  |  | The NAR states on p. 89: "Following the RGIE/AREI [10], the cables must have a specific fire resistance according to IEC60332 and EN50399, depending on the configuration and area of application. Since the insulating material is non-combustible, mainly due to non-halogenated additives, cables must be also compliant with EN 61034 for smoke production, and EN 60754 and EN 50267-2-1 for corrosive gasses in case of a fire." Could you specify for which applications fire rated or non-combustible cables are used?
BE-C-65 | Germany | BE | 03.3 - Passive fire protection |  | Regarding Tihange 3 & KCD 3, p. 92 |  |  |  | On p. 92 of the NAR it is stated: "Each safety related train is separated from the other redundant trains and of the nonsafety related by: • minimum distances of 1 m (horizontal) and 1.5 m (vertical);" How were these distance criteria justified?
BE-C-66 | Germany | BE | 03.4 - Licensee's experience |  | Regarding BR2, pp. 101-102 |  |  |  | The operating experience is presented nicely here with a lot of beneficial information. However, information in section 2 on fire safety analyses is missing how this information has been applied in fire safety analyses.
BE-C-67 | Germany | BE | 03.4 - Licensee's experience |  | Regarding BR3, pp. 101 |  |  |  | A fire accident in the controlled area with a vacuum cleaner is reported where the filter banks soon started to clog and visibility was low. What lessons can be learned from the accident? Does the filter-capacity needs to be increased or other means to ensure visibility needs to be installed?
BE-C-68 | Germany | BE | 03.4 - Licensee's experience |  | Regarding SCG, Section 3.4 |  |  |  | Remark: Section 3.4 on SFS is quite short, important point were already addressed in section 3.1.
BE-C-69 | Germany | BE | 03.5 - Regulator's assessment |  | 104 |  |  |  | The presence of the on-site fire brigade (during working hours) as well as the relation with the local public fire brigade are identified as a strong point. Does the operator have a specific cooperation agreement with the external fire brigade? Could Belgium please elaborate more, if there are clear procedures (roles, responsibilities, etc.) covering the interface between the internal and external fire brigade at BR2?
BE-C-70 | Poland | BE | 02- Fire safety analyses |  | 23 |  |  |  | For the Fire PSA Level 2 studies currently underway for CNT3 (rector), what are the specific challenges or complexities associated with assessing the integrity of the reactor containment and atmospheric releases?
BE-C-71 | Poland | BE | 02- Fire safety analyses |  | 27 |  |  |  | In the context of the Fire Phenomena Analyses, how is the ventilation flow rate for each room assessed? How critical is this parameter in evaluating the consequences of fire events, and what measures are in place to ensure accurate data collection in this regard?
BE-C-72 | Poland | BE | 02- Fire safety analyses |  | 28 |  |  |  | What is the estimated value of reactor core damage frequency? What is the contribution of significant fire sceanrios to the CDF?
BE-C-73 | Romania | BE | 03.4 - Licensee's experience | [5 empty] | Please provide some information on how are temporary modifications to fire protections features, systems and organizational arrangements managed, for nuclear power plants.
BE-C-74 | Romania | BE | 03.4 - Licensee's experience | [5 empty] | Please provide some information on how are permanent and temporary modifications to nuclear installations and administrative arrangements analyzed with regard to their potential impact on fire protection for nuclear power plants.
BG-C-75 | Czech Republic | BG | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
BG-C-76 | Czech Republic | BG | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
BG-C-77 | Czech Republic | BG | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
BG-C-78 | Czech Republic | BG | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
BG-C-79 | Finland | BG | 02- Fire safety analyses |  | 20-25, 28-31 |  |  |  | Combinations of fires and other events are included in the analysis according to the chapters 2.1.1 and 2.1.2. Within the results being discussed in the chapter 2.1.4, nothing is mentioned about the event combinations. What is your conclusion on the significance of the combinations of fires and other events compared to the internal fires?
BG-C-80 | Finland | BG | 02- Fire safety analyses |  | 27 |  |  |  | In the chapter 2.1.3, Deterministic fire hazard analysis, is mentioned "Uncertainties that may affect the results of the FHA are assessed by sensitivity analysis. Uncertainty analysis refers to statistical combinations of the input data and accounting for the uncertainties in the data on a parameter that results from the calculation." -> Suggestion for a good performance.
BG-C-81 | Poland | BG | 02- Fire safety analyses |  | general |  |  |  | How is the cliff-edge effect considered in the safety assessment? What mitigation measures are in place?
BG-C-82 | Poland | BG | 02- Fire safety analyses |  | 31 |  |  |  | How does the analysis take into account operator training and decision making during fire scenarios?
BG-C-83 | Poland | BG | 03.3 - Passive fire protection |  | 97 |  |  |  | Have you considered using independent experts to ensure an objective assessment and a high standard of fire safety?
BG-C-84 | Poland | BG | 04 - Overall assessment and general conclusions |  | 117 |  |  |  | With regard to the ongoing equipment replacement programme (e.g. the replacement of detectors for the AlgoRex CS1140 Modular Fire Detection System), how does the licensee ensure a smooth transition without compromising fire safety?
CZ-C-85 | Austria | CZ | 01-General information |  | 19 |  |  |  | As stated in 1.2.3. FRS performs inspections of nuclear power plants on an annual basis, always on one selected building. FRS has performed a comprehensive inspection of all nuclear power plant buildings in 2013 at Temelín NPP. However, one of the conclusions was that due to the scope and documentation requirements of such an action and the resulting inadmissible duration of the entire inspection process, the feedback effect of the inspection process completely disappears. Thus, the FRS followed the path of annual inspections of one selected building from the list of risk buildings determined by deterministic analysis. How many buildings are declared significant? How are those inspected? Are there any other inspections (e.g. conditions of fire detection of fire extinguishing systems and components)? How often are they inspected?
CZ-C-86 | Austria | CZ | 02- Fire safety analyses |  | 20 |  |  |  | Regarding "Audit No. 5", which examined the design of significant nuclear power plant buildings in relation to the terms between fire hazards and safe shutdown of the nuclear reactor according to the criteria defined in US 10CFR50, Appendix R and NUREG-8000, Part 9.5.1 (1995). How do you define significant buildings?
CZ-C-87 | Austria | CZ | 02- Fire safety analyses |  | 21 |  |  |  | Regarding the study prepared by Nuclear Research Institute Řež, Energoprojekt Praha for the purposes of the Topical Peer-Review "Fire Protection" division many areas were covered but some of the most important areas for Nuclear Safety are not mentioned (e.g. MCR, cable spreading rooms, etc.). Please elaborate on the reasons for not mentioning these areas.
CZ-C-88 | Austria | CZ | 02- Fire safety analyses |  | 24 |  |  |  | In 2011, a "Technical Assistance" document was prepared to examine the suitability and addition of Electrical Fire Detectors (EFD) in selected areas of the reactor and auxiliary buildings. A fire risk analysis was made for each room and, where values were exceeded for rooms without fire risk, the actual values were verified on site. Could you explain which rooms were covered here and what does “where values were exceeded for rooms without fire risk” mean? On which basis was the status “without fire risk” determined and what was e.g. the probability of fire ignition for those rooms?
CZ-C-89 | Austria | CZ | 02- Fire safety analyses | [5 empty] | It is stated that power cables and most low-current cables have enhanced resistance to the spread of fire, complying with IEC 332.3 category A, or IEC 331 tests, in all nuclear safety-important buildings. Were all original cables replaced in a course of pre-start up modernization at Temelin?
CZ-C-90 | Austria | CZ | 02- Fire safety analyses |  | 25 |  |  |  | It is stated that documentation is actualized as required by the Fire Protection Act. This document approves the South Bohemian Regional Fire Rescue Service. The latest version of the fire risk assessment of the 1st reactor turbine hall has approval issued on 18 April 2016. What is the frequency of the updates as per applicable regulations? How of the is the fire risk assessment for all buildings updated?
CZ-C-91 | Austria | CZ | 02- Fire safety analyses |  | 30 |  |  |  | The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 20.3% level. This is a rather high contribution from internal fires, possibly indicating a safety challenge in this area. On which total CDF is 20.3% fire related?
CZ-C-92 | Austria | CZ | 02- Fire safety analyses |  | 31 |  |  |  | The contributions of internal fires to the overall risk of unit operation are generally of little importance. The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 20.3% level. What about MCR and cable spreading areas?
CZ-C-93 | Austria | CZ | 02- Fire safety analyses |  | 33 |  |  |  | In this section, it is mentioned that the water SE, which protects the cable compartments, is obsolete. At present, the Dukovany NPP has developed a requirement for the selection of the most suitable method of securing the cable compartments by the SE. A working group has been set up to evaluate the different options. Since fire in the cable spreading areas is likely the dominant risk factor, when will this be completed and why was it not done before?
CZ-C-94 | Austria | CZ | 02- Fire safety analyses |  | 33 |  |  |  | Conference on fire protection and nuclear safety. Fire protection specialists obtain information on the latest trends in the field of fire safety. The information can be used to comment on new actions, or specialists recommend the implementation of these innovations a NPP. GOOD PRACTICE
CZ-C-95 | Austria | CZ | 02- Fire safety analyses |  | 35 |  |  |  | “The introduction of the elements of cooperation and real distress cannot be replaced by any training for the members of the Fire Rescue Service.” Please clarify what is meant by this statement.
CZ-C-96 | Austria | CZ | 02- Fire safety analyses |  | 35 |  |  |  | In regards to the inspection activities performed by the SÚJB and the Fire Rescue Service results. What is the frequency and scope of the inspections?
CZ-C-97 | Austria | CZ | 02- Fire safety analyses |  | 36 |  |  |  | On this page it is mentioned that temperatures of several 1 000 °C are reached during the combustion of chemical gases and vapors. Several thousand degrees sounds rather high.
CZ-C-98 | Austria | CZ | 02- Fire safety analyses |  | 39 |  |  |  | It is mentioned that the next fire exercise is planned for 2023. Did the mentioned fire exercise already take place and what are the outcomes? Are any exersices planned that would focus on safety significant sequences (for systems of the RR itself) rather than on the sources?
CZ-C-99 | Austria | CZ | 02- Fire safety analyses |  | 40 |  |  |  | In this section, it is mentioned that the LVR-15 reactor has not been affected by a significant fire since the 1989 reconstruction and the last documented fire was in the reactor hall in the cable line, which was extinguished. How many fires have there been in the LVR-15 reactor facility in total?
CZ-C-100 | Austria | CZ | 03.1 - Fire prevention |  | 43 |  |  |  | It is mentioned that in the USSR, the basic requirements for fire safety were based on production categories only. Could you please explain what “Production Category” means? What is the relation of “Production Category” to “Safety Class”?
CZ-C-101 | Austria | CZ | 03.1 - Fire prevention |  | 47 |  |  |  | Here it is noted that non-conformities detected are at a very low level (2022: 73/942). This does not sound low; it is 8% of the inspection. Could you please comment on the findings?
CZ-C-102 | Austria | CZ | 03.1 - Fire prevention |  | 72 |  |  |  | The permanent fire water supply consists of a steel tank with a volume of 70 m3. On which basis was it determined that a 70 m3 tank volume would be sufficient for e.g. seismically induced fire extinguishing, in case the resupply is damaged by the same seismic event?
CZ-C-103 | Austria | CZ | 03.2 - Active fire protection |  | 78 |  |  |  | It is stated that protected piping is not required for the supply system tubes, which filters outdoor air containing radioactive aerosols for the control room when necessary, and does not need to be used for fire sectioning for the following reasons. The system is only operational when the outdoor air is contaminated with radioactive substances. This seems to imply that an event with a release of radioactivity (e.g. radioactivity in ambient) and a simultaneous fire are deterministically excluded. On which basis was such an exclusion justified?
CZ-C-104 | Austria | CZ | 03.2 - Active fire protection |  | 79 |  |  |  | The report mentions that the parallel installation of different divisions of cable routes of the secured power supply systems in compartments without separation by construction with fire resistance of at least 90 minutes is assessed and evaluated in detail in special documentation "engineering solutions". In how many cases does such a situation of multiple redundancies in one fire compartment occur? What are typical “engineering solutions” to assure power supply to redundant trains in a case of fire in such rooms?
CZ-C-105 | Austria | CZ | 03.2 - Active fire protection |  | 81 |  |  |  | Temporary measures to ensure the required fire safety are applied e.g. during shutdowns of fire safety equipment, repairs, modifications and maintenance. How often are such temporary measures activated on average (per unit and per years)?
CZ-C-106 | Austria | CZ | 03.2 - Active fire protection |  | 103 |  |  |  | In the report it is stated that the fire resistance of the pipe penetrations through the fire separating structures prove a certificate according to the approved test methodology from 1995. Has the test methodology for penetration been upgraded since 1995? As for the plant life extension, how does the life extension affect the penetrations and their testing in the sense of the fire resistance? How are those penetrations inspected in the course of life extension?
CZ-C-107 | Austria | CZ | 03.3 - Passive fire protection |  | 106 |  |  |  | It is stated that the Vltava River is used as the main source of firewater in the reactor hall with a total water supply of 14.000 liters. Is there any firewater tank available at the site? What does the 14000-liter volume for the reactor hall refer to?
CZ-C-108 | Austria | CZ | 03.3 - Passive fire protection |  | 116 |  |  |  | The fire resistance of the penetration seals installed in critical areas is 90 minutes. Does this apply to both the piping and electrical (cables) penetration? How do you define “critical areas”, and how many critical areas are defined in each NPP unit?
CZ-C-109 | Austria | CZ | 03.3 - Passive fire protection |  | 120 |  |  |  | In the report, it is mentioned that flammable air filters are designed in such a way that they cannot leak radioactive substances above the specified limits in the event of a fire. The filter is automatically separated from the rest of the channel by closing the air dampers. Are those dampers gas-tight ones? If so, to which over-pressure are those designed? E.g. for the main charcoal filter in the MCR clean-up system?
CZ-C-110 | Austria | CZ | 03.3 - Passive fire protection |  | 120 |  |  |  | It is noted that part of the dampers are designed so that when a temperature of 130°C is reached, the damper blade is "baked" - sealed in the pipe. Which dampers are designed to have such a feature?
CZ-C-111 | Austria | CZ | 03.3 - Passive fire protection |  | 121 |  |  |  | The originally undivided reactor building is being divided into fire sections subsequently during use; the division is not complete and finished. What exactly is unfinished and when will it be finished?
CZ-C-112 | Germany | CZ | 02- Fire safety analyses |  | Regarding Temelin NPP, p. 21 |  |  |  | The NAR states on p. 21: "In 2011, a "Technical Assistance" document was prepared to examine the suitability and addition of Electrical Fire Detectors (EFD) in selected areas of the reactor and auxiliary buildings. A fire risk analysis was made for each room and, where values were exceeded for rooms without fire risk, the actual values were verified on site." Could you provide information on the criteria used for the analysis? Is there a minimum risk for fire detectors to be installed in the areas of the reactor and the auxiliary buildings?
CZ-C-113 | Germany | CZ | 02- Fire safety analyses |  | Regarding Temelin NPP, p. 22 |  |  |  | On p. 22, Algorithm for fire safety assessment Could you explain the meaning of the "coefficient of fire safety, k8"? How is the "equivalent fire duration" calculated?
CZ-C-114 | Germany | CZ | 02- Fire safety analyses |  | Regarding Temelin NPP, p. 28 |  |  |  | On p. 28, Sect. "2.1.A.6.2. Lessons learned from events, reviews, fire safety related missions", the sources for lessons learned are explained; however, examples for lessons learned are missing. Could you please provide examples?
CZ-C-115 | Germany | CZ | 02- Fire safety analyses |  | Regarding all installations, different pages, staring on p. 20 |  |  |  | The phrase "fire section" is used many times all over the NAR for different facilities. A definition could not be found. It is correctly understood that "fire section" could either mean "fire compartment" or "fire cell"? A clarification and distinction between "fire compartment" and "fire cell" would be appreciated.
CZ-C-116 | Germany | CZ | 02- Fire safety analyses |  | Regarding Dukovany NPP, p. 30 |  |  |  | On p. 30 of the NAR, regarding special cables like optic cables, coaxial cables "which could not be manufactured to meet the test according to IEC 332.3 category A in order to ensure their functionality, their resistance to the spread of fire is ensured by covering their entire length in steel tubes". How and against what type of scenario is this solution qualified?
CZ-C-117 | Germany | CZ | 02- Fire safety analyses |  | Regarding Dukovany NPP, p. 33 |  |  |  | On p. 33, Sect. "2.1.B.6.2. Lessons learned from events, reviews, fire safety related missions", the sources for lessons learned are explained; however, examples for lessons learned are missing. Could you please provide examples?
CZ-C-118 | Germany | CZ | 02- Fire safety analyses |  | Regarding LVR 15, pp. 36-40 |  |  |  | The scope of the analyses covering also shutdown states during outages should be more clearly (and not only implicitly) addressed.
CZ-C-119 | Germany | CZ | 02- Fire safety analyses |  | Regarding LVR 15, pp. 36-40 |  |  |  | Information on how the presence of permanent and temporary fire loads is considered and addressed in the fire safety analyses is missing.
CZ-C-120 | Germany | CZ | 02- Fire safety analyses |  | Regarding LVR 15, pp. 36-40 |  |  |  | What is the reason for not considering the radiation hazard of a release from burning radioactive waste in the fire safety analysis?
CZ-C-121 | Germany | CZ | 02- Fire safety analyses |  | Regarding LVR 15, pp. 36-40 |  |  |  | Detailed information on how the direct and indirect fire effects are assessed and which methods and data are used is missing.
CZ-C-122 | Germany | CZ | 02- Fire safety analyses |  | Regarding all installations, pp. 36-43 |  |  |  | Information on consideration of plant modifications in updates of the safety reviews and how they are addressed is missing.
CZ-C-123 | Germany | CZ | 02- Fire safety analyses |  | Regarding all installations, pp. 36-43 |  |  |  | Information in how far and how information from the operating experience regarding deterioration of fire protection features at the Czech installations reported in the NAR and from fire events at other nuclear installations applicable to the installations reported is applied in the fire safety analyses should be provided.
CZ-C-124 | Germany | CZ | 02- Fire safety analyses |  | Regarding LVR 15, pp. 36-40 |  |  |  | The INSARR mission in 2020 revealed the need for fire hazard reduction (disposal of older technologies) and for comprehensive instructions for personnel response (emergency procedures and emergency instructions) also in case of fire. This statement needs some basic information for justification.
CZ-C-125 | Germany | CZ | 02- Fire safety analyses |  | 36 |  |  |  | A PSA study is mentioned for LVR-15. Did you perform a full scope Probabilistic Safety Analysis (including Fire Analysis) for this research reactor? Could Czech Republic please provide information on the probabilistic analysis and the major findings?
CZ-C-126 | Germany | CZ | 02- Fire safety analyses |  | 40 |  |  |  | The inclusion of the internal FRSU in the region's alarm plans and the possibility of the unit's departure to the nearby surroundings to cooperate with the Regional FRS is identified as a good practice. Could Czech Republic please provide more information on the means and procedures at LVR-15 to guarantee the smooth cooperation between the FRSU and FRS?
CZ-C-127 | Germany | CZ | 03.1 - Fire prevention |  | Regarding Temelin NPP, p. 42 |  |  |  | In the NAR on p. 42, under Chapter 3, 3A - Temelin it is mentioned that weak points were found in a 2003 study. However, the weaknesses were not mentioned. It was only reported that "None of these "weak points" relate to the potential impact of fire on nuclear safety." The weak points should be mentioned in some detail in order to allow the community to learn from each other.
CZ-C-128 | Germany | CZ | 03.1 - Fire prevention |  | 44 |  |  |  | It is stated that the company's FRSU has a contract with Nuclear Research Institute Řež PLC. Is FRSU an internal fire department of LVR-15? Could Czech Republic please provide more information on the structure of fire fighting and involved parties?
CZ-C-129 | Germany | CZ | 03.1 - Fire prevention |  | Regarding Dukovany NPP, p. 51 |  |  |  | On p. 51, section "3.1.B.3.2. Lessons learned from events, fire safety related mission evaluations" the way findings are generated and treated is explained, but the findings itself are not reported. Could you please give some examples for findings?
CZ-C-130 | Germany | CZ | 03.1 - Fire prevention |  | Regarding Temelin and Dukovany NPPs, p. 80 |  |  |  | Could you add the fire specific characteristics of the turbine oil used?
CZ-C-131 | Germany | CZ | 03.1 - Fire prevention |  | Regarding LVR 15 |  |  |  | What is the regulatory basis for conducting firefighting drills at least one per two years?
CZ-C-132 | Germany | CZ | 03.2 - Active fire protection |  | Regarding Temelin NPP |  |  |  | The frequently used "semi-stable" extinguishing equipment should be defined. It is understood so far as a piping system for fire extinguishing agents which need manual support. Could you comment and define?
CZ-C-133 | Germany | CZ | 03.2 - Active fire protection |  | Regarding both NPPs |  |  |  | The flow capacity of the fire water systems should be explained and for what scenario it is designed (e.g. the largest fire extinguishing system plus x water hoses).
CZ-C-134 | Germany | CZ | 03.2 - Active fire protection |  | Regarding LVR 15 |  |  |  | There are no fixed fire extinguishing systems at LVR 15. What is the basis for justification?
CZ-C-135 | Germany | CZ | 03.3 - Passive fire protection |  | Regarding Temelin and Dukovany NPPs, pp. 112 - 117 |  |  |  | On p. 112 (p. 117) of the NAR the actual fire resistance is reported to range from 15 to 240 min for walls and ceilings and from 15 to 90 min for doors and hatches. For fire dampers and fire seals (for pipework, cables) no actual fire resistance is given. How was the given fire resistance rating determined? Please provide information on the required fire resistance rating of fire barriers and their elements and the justification for that. Is the required fire resistance given by calculations or by prescriptive requirements?
CZ-C-136 | Germany | CZ | 03.3 - Passive fire protection |  | Regarding Temelin NPP, p. 115 |  |  |  | From p. 115 it can be read that fire dampers were only installed in the place of "penetrations of ventilation equipment smaller than 0.04 m2" depending on certain criteria. How is the max 0.04 m2 opening area is justified? The criteria mentioned for closing penetrations smaller than 0.04 m2 with dampers do not include structural protection of redundant trains. How is this considered?
CZ-C-137 | Germany | CZ | 03.3 - Passive fire protection |  | Regarding LVR 15, pp. 123 |  |  |  | In the NAR it is written on p. 123 regarding fires close to the pump house: "A fire in any of these spaces can disable the cooling function for the prescribed 30 minutes." Could you explain why in case of such event the cooling function is restored after 30 min?
CZ-C-138 | Germany | CZ | 03.4 - Licensee's experience |  | Regarding all installations, pp. 124-125 |  |  |  | The two licensee's experience chapters are very unspecific and may be extended by examples.
CZ-C-139 | Finland | CZ | 03.2 - Active fire protection |  | 94 |  |  |  | Has another extinguishing agent been considered instead of CO2?
CZ-C-140 | Finland | CZ | 03.2 - Active fire protection |  | 79, 101 |  |  |  | How is the flooding induced by actuation of fire extinguishing systems considered?
CZ-C-141 | Finland | CZ | 03.3 - Passive fire protection |  | 119-120 |  |  |  | Do fire dampers have the same fire resistance requirement as the penetrated fire-separating structure?
CZ-C-142 | Finland | CZ | 03.3 - Passive fire protection |  | 120 |  |  |  | What is the structural separation between turbine hall and reactor buildings? Are there any systems important to safety located inside the turbine hall?
CZ-C-143 | Poland | CZ | 02- Fire safety analyses |  | 40 |  |  |  | Was the potential aspects of gas generation from waste or spent fuel considered in the safety analyses?
CZ-C-144 | Poland | CZ | 02- Fire safety analyses |  | 56 |  |  |  | Was the cliff-edge effect taken into consideration in the fire safety analyses?
CZ-C-145 | Slovakia | CZ | 01-General information |  | page 17; chapter 1.2.2 and throughout the report |  |  |  | 50 - SG - D2 rev.1 was valid from 1992 to 2004 and is now invalid. In 2004 it was superseded by NS-G.1.7. Since 2021 NS-G-1.7 has been superseded by SSG-64. SSG - 64 and SSG - 77 are safety standards currently in force for fire safety.The report needs to be assessed in the context of currently applicable safety standards and corrected as necessary.
CZ-C-146 | Slovakia | CZ | 03.2 - Active fire protection |  | page 25; chapter 2.1.A.4 |  |  |  | In the case of an oil leakage between the 1st and 2nd section of the low-pressure of a steam turbine, one of the worst outcomes is an oil leakage into the insulation, which is not listed in the report. Only an oil leakage from a +15m to a -8.20m floor is indicated.
CZ-C-147 | Slovakia | CZ | 03.2 - Active fire protection |  | page 39; chapter 2.2.6.1 |  |  |  | Is Halotron allowed to be used as a fire extinguishing medium in the Czech Republic? If it is banned, is there a replacement and a recycling process ready, or underway?
DK-C-148 | Poland | DK | 02- Fire safety analyses |  | 18 |  |  |  | How did the fire safety analysis at the Riso site lead to the decision to disband the on-site fire department? Do the employees of fire department in the municipality of Roskilde receive any additional training for their additional duties? | The fire safety analysis was carried out with the purpose of investigating the possibility of disbanding the on-site fire department and instead relying on the nearby fire department in the municipality of Roskilde. The background for this decision stemmed from the significantly decreased operational activities at the Risø site during the years 1998 -2000. The Execute Order no. 1085 of 25 October 2019 on Risk-Based Sizing of the Municipal Rescue Service stipulates that the municipal rescue service must be able to provide a preventive, limiting, and remedial effort in relation to local risks. The municipal rescue service must identify and analyse local risks, which must form the basis for sizing the rescue service (risk profile). The municipal council determines the level of the municipal rescue service's task performance (service level) based on the risk profile as well as its organization, operations, alerting, sizing, and equipment based on the risk profile and service level.
DK-C-149 | Poland | DK | 02- Fire safety analyses |  | 23 |  |  |  | How has the coordination among multiple authorities been managed in practice to ensure effective oversight of fire safety in nuclear facilities? Is there a working group made up of employees from the authorities? Are there regular meetings? | The regulation of fire safety at the nuclear facilities in Denmark is shared among Danish Health Authority, Danish Emergency Management Agency and Danish Authority of Social Services and Housing. There is no formal working group with representatives from these authorities covering all aspects on fire safety at the nuclear facilities. There is a tradition of consulting the respective authorities before new legislation is put into effect, and meetings are held on a case-by-case basis. Regulatory meeting are held among Danish Health Authority and Danish Emergency Management Agency as they jointly constitute the Nuclear Regulatory Authority.
DK-C-150 | Poland | DK | 02- Fire safety analyses |  | 23 |  |  |  | Can you provide more information on what types of non-compliances with the fire safety provisions have been found? | The instances of non-compliance with fire safety provisions have primarily involved storage of unnecessary combustible materials, need for additional fire alarms or blocking of emergency exits.
DK-C-151 | Poland | DK | 03.2 - Active fire protection |  | 38 |  |  |  | How was the placement and selection of fire detectors determined in the building, and what considerations led to the use of mainly optical smoke detectors with thermal detectors in specific areas to avoid false alarms? | All manual fire-extinguishing equipment, including fire detectors, is dimensioned and placed according to the instructions of the fire technical advisers who carry out fire supervision.
Finland-C-152 | Czech Republic | Finland | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
Finland-C-153 | Czech Republic | Finland | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
Finland-C-154 | Czech Republic | Finland | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
Finland-C-155 | Czech Republic | Finland | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
Finland-C-156 | Germany | Finland | 03.2 - Active fire protection |  | 81 |  |  |  | In the NAR a "high safety culture" is mentioned as a strength of the Licensee’s experience in the implementation of the active fire protection. Could Finnland please give a more detailed explaination how this conlcusions are made?
Finland-C-157 | Poland | Finland | 03.2 - Active fire protection |  | 45 |  |  |  | Is the number of false alarms on each nuclear unit monitored? If, such statistics are kept, what is the trend since the beginning of measurements?
Finland-C-158 | Poland | Finland | 04 - Overall assesssment and general conclusions |  | 104 |  |  |  | What types of weaknesses exist in OL3 in terms of fire protection? Are they dependent on the design of this block, or can they be improved in the next blocks of this type?
Finland-C-159 | Slovakia | Finland | 03.1 - Fire prevention |  | page 36; chapter A 3.1.4.1 |  |  |  | The report describes that oil leakages of the lubricant oil system is not under control. Technical measures to control oil leakages of the lubricant oil system should be planned/described.
Finland-C-160 | Slovakia | Finland | 03.2 - Active fire protection |  | page 48; chapter A 3.2.2.2 |  |  |  | When starting the carbon dioxide fire extinguishing system manually, the ventilation system is not shut-off. In this scenario, the extinguishing concentration of carbon dioxide may not be achieved.
Finland-C-161 | Slovakia | Finland | 03.2 - Active fire protection |  | page 63; chapter B3.2.2.2 |  |  |  | Is Halotron allowed to be used as a fire extinguishing medium in Finland? If it is banned, is there a replacement and a recycling process ready or underway?
FR-C-162 | Austria | FR | 02- Fire safety analyses |  | 20 |  |  |  | On page 20 it is stated that, "In the light of this worst-case approach, a situation involving two or more simultaneous fires with independent causes and affecting the rooms in the same plant unit or different plant units, is not postulated." Could you please provide some information if there are plans to add a worst-case scenario in which such situations are investigated?
FR-C-163 | Austria | FR | 02- Fire safety analyses |  | 21 |  |  |  | Do you intend to extend combinations of events for future probabilistic fire risk assessement, like fire and interal initiating events, fire and internal hazards (internal flooding and HELB), fire and seismic initiating event, fire and other external evnts, fire and explosions, mulitiple compartment fire interaction analysis.
FR-C-164 | Austria | FR | 02- Fire safety analyses |  | 35 |  |  |  | Please add information on the internal fire CDF for RP1300.
FR-C-165 | Austria | FR | 03.1 - Fire prevention |  | 96ff |  |  |  | In the chapter improvements regarding incidents related to hot works and implemented measures are noted. Please provide some additional information on the capacity building measures in order to enhance safety culture at all levels.
FR-C-166 | Austria | FR | 03.3 - Passive fire protection |  | 202ff |  |  |  | Please provide additional information on the action plans in this chapter as mentioned in 4.5.
FR-C-167 | Austria | FR | 02- Fire safety analyses |  | 25 |  |  |  | Please provide additional information on the implemention of additional protection provisions and clarify when these backfittings were implemented in Tricastin 1 and add the status of implementation of other relevant NPPs.
FR-C-168 | Austria | FR | 03.1 - Fire prevention |  | 125 |  |  |  | Please provide additional information on the actions taken by ASN to monitor the progress by the licencee on drafting of hot work permits and the management of fire loads (E-3.1.4.).
FR-C-169 | Austria | FR | 03.1 - Fire prevention |  | 130f |  |  |  | Please provide additional information on requested actions by ASN to improve the safety culture of the licensee regardings management of fire loads, and training of the facility personel mentioned on page 260.
FR-C-170 | Austria | FR | 03.1 - Fire prevention |  | 130 |  |  |  | In the Section F-I-3.1.3.3 several recommendation of the last periodic safety review are noted. Please provide some information on the state of implementation and highlight some of the actions taken to adresse the recommentations.
FR-C-171 | Belgium | FR | I-2.1.2. Key assumptions and methodologies |  | 22 |  |  |  | The text mentions: "For a given room, the reference fire is that which takes account of all the combustible items in this room and with the most serious consequences in terms of duration and severity." => would it be possible to receive more information about how concretely this reference fire is defined? What are the criteria to choose the most serious consequences?
FR-C-172 | Belgium | FR | I-2.1.2. Key assumptions and methodologies |  | 28 |  |  |  | The CPY fire PSA allows: ⚫ an evaluation of the risk of core melt (RFC) following a fire (on the basis of a “BR model”) for the reactor at power or shut down states (level 1 PSA); ⚫ an evaluation of the risk of uncovering of the fuel present in the spent fuel pool (on the basis of a “BK model”) for the reactor at power or shut down states (level 1 PSA); ⚫ an evaluation of the risk of releases to atmosphere in the event of an onset of an accident with core melt following a fire (level 2 PSA). The scope of the study covers the nuclear island and the conventional island of the Tricastin NPP units 1 and 2. => is it correct to interpret this statement as there is no Fire PSA Level 2 developped for the Spent Fuel Pools? (as the Level 2 PSA only mentions Core Melting scenarios)
FR-C-173 | Belgium | FR | I-2.3.2. Key assumptions and methodologies |  | 46 |  |  |  | The methodology followed by GBII consists in: ⚫ identifying the feared situations on the basis of studies of the accident situations in the Safety Analysis Report; ⚫ defining the scale of severity and probability of these situations; ⚫ defining the probability/severity pair assessment chart. => is the REX from other similar installations also taken into account?
FR-C-174 | Belgium | FR | III-2.3.7.3. Conclusions drawn on the adequacy of the licensee’s fire safety analyses |  | 63 |  |  |  | The data considered in the fire risk analyses are acceptable. => ok, but what about the results of those analyses?
FR-C-175 | Belgium | FR | IV-2.3.1. Types and scope of the fire safety analyses |  | 63 |  |  |  | The fire risk analysis which contributes to the Mélox nuclear safety case is performed using a prudent deterministic approach => what is a “prudent” deterministic approach in comparison to a “normal” one?
FR-C-176 | Belgium | FR | A-I-3.2.2.2. Types, main characteristics and performance expectations |  | 137, 138 |  |  |  | the nuclear island (outside the reactor building) is reinforced in lot B => what is lot B? Is it so that the fixed extinguishing systems of the conventional island were designed to sustain SSE contrary to the nuclear island (outside RB) where they were designed to sustain “only” an OBE? On the other hand, one can find at page 138: ": the distribution system of the conventional island (not designed to seismic standards) can be isolated by paraseismic valves." => seems in contradiction with p137
FR-C-177 | Belgium | FR | 03.2 - Active fire protection |  | 140 |  |  |  | According to § A-I-3.2.3, firefigthing in the NPPs is based on complementary actions between the internal fire-fighting organisation and the SDIS. However, in France, due to the location of the SDIS and the location of the NPPs, the time to arrive to the NPP could be important. In certain particular cases, the foreign countries could dispose of professional fire-fighters nearer to the French NPPs than France (Chooz). Is this considered in the fire protection concept ? Does France consider some transfrontalier arrangments in its approach to fire protection?
FR-C-178 | Belgium | FR | 03.2 - Active fire protection |  | 140-141 |  |  |  | The § on detection mentions that any person who notices a potential fire event must use the extinguishing means at their disposal (without jeopardising their own safety). On p141, it is mentioned that all the personnel concerned by the fire response is trained and regularly refreshed. Does this mean that all the people on site must be and are concerned by this training? Or is this training and refreshment adressed to the verification officiers mentioned in §identification and verification and to the internal response team mentioned in the emergency services? What percentage of the NPP personnel is concerned with the training?
FR-C-179 | Belgium | FR | 03.2 - Active fire protection |  | 140 |  |  |  | For NPPs, France could elaborate on the size of the internal response team for each site and their capabilities to manage parallel events on different units. Some NPP sites are quite large (i.e. Gravelines) and it should be confirmed that the intervention times are always met despite of the size of the sites.
FR-C-180 | Belgium | FR | A-I-3.2.3.2. Firefighting capabilities, responsibilities, organization and |  | 141 |  |  |  | Is it correct to consider that all the mentionned intervention times do not correspond to Fires occuring inside the Reactor Building?
FR-C-181 | Belgium | FR | A-I-3.3.1.3. Performance assurance through lifetime |  | 205 |  |  |  | the text mentions: "With regard to the floor drains, their trap is checked daily as part of routine servicing with a daily frequency and at least once a month (depending on the evaporation rate observed in the room)." => what is the actual frequency of those checks? Daily or monthly?
FR-C-182 | Belgium | FR |  |  | 208 |  |  |  | Text mentions: "For example, the fire doors which must be kept closed have been identified and will be subject to specific monitoring." Would'nt it be a good practice to consider that all fire doors have to be kept closed (and maybe be have some administrative rules permitting to keep some open for a limited time for "good" reasons)?
FR-C-183 | Belgium | FR | documentation onsite and offsite |  | 238 |  |  |  | Although not part of the candidate installations, a section on the approach for amending the passive fire protection during dismantling for Fessenheim. Based on the information given for Operational NPPs (Tricastin) and the ones in decommissioning, it appears that the sectorization is quite different. Can France give some information on how the sectorization will be amended during the decommissioning activities in Fessenheim (when?, how?, and based on which criteria?).
FR-C-184 | Czech Republic | FR | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
FR-C-185 | Czech Republic | FR | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
FR-C-186 | Czech Republic | FR | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
FR-C-187 | Czech Republic | FR | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
FR-C-188 | Germany | FR | 02- Fire safety analyses |  | 42 |  |  |  | It is stated that the nature convection cooling by passive opening of spring-loaded valves guarantees a safe state of research reactor. Is the nature convection sufficient to cool the reactor immediately after shutdown? Is it a common situation in a normal operation? Is the pump circulation not at all required for the residual heat removal? Could France please provide more information on the cooling capacity of the reactor?
FR-C-189 | Germany | FR | 02- Fire safety analyses |  | 45 |  |  |  | What are the requirements used for fire hazard analysis for the Fuel Cycle Facilities? Are this only national requirements or also additional requirements as a reference, such as the IAEA Safety Requirement SSR-4?
FR-C-190 | Germany | FR | 02- Fire safety analyses |  | Regarding ROMANS/CERCA, p.53 |  |  |  | Can you provide more details on the FHA, where the highest risks in terms of the plant design are and what the reason is?
FR-C-191 | Germany | FR | 02- Fire safety analyses |  | Regarding ROMANS/CERCA, p.53 |  |  |  | What are the reference scenarios?
FR-C-192 | Germany | FR | 02- Fire safety analyses |  | Regarding ROMANS/CERCA, p.55 |  |  |  | A list of PSR results and implemented significant upgrades should be provided or more information.
FR-C-193 | Germany | FR | 02- Fire safety analyses |  | Regarding SILO 130 La Hague, p. 77 |  |  |  | Can you provide a clarification on the underlying fire hazard on which basis all prevention and protection measures to be adopted are identified?
FR-C-194 | Germany | FR | 02- Fire safety analyses |  | Regarding SILO 130 La Hague, p. 77 |  |  |  | Are more details on the underlying assumptions and models available?
FR-C-195 | Germany | FR | 02- Fire safety analyses |  | Regarding SILO 130 La Hague, p. 79 |  |  |  | Are there ongoing or intended modifications/changes?
FR-C-196 | Germany | FR | 02- Fire safety analyses |  | Regarding OSIRS, pp. 80-86 |  |  |  | Information if and how the operating experience from fire events and events concerning fire protection features (at the Osiris RR and at other installations) is considered in the fire safety analyses should be provided.
FR-C-197 | Germany | FR | 02- Fire safety analyses |  | Regarding OSIRS, pp. 80-86 |  |  |  | Information if and how combinations of fires and other hazards are considered should be provided.
FR-C-198 | Germany | FR | 02- Fire safety analyses |  | Regarding OSIRS, pp. 80-86 |  |  |  | Information on the potential direct and indirect effects is missing and should be provided.
FR-C-199 | Germany | FR | 02- Fire safety analyses |  | Regarding UNGG, pp. 86-90 |  |  |  | Information on if and how the operating experience from events concerning fire protection features at other installations is considered in the fire safety analyses should also be addressed.
FR-C-200 | Germany | FR | 02- Fire safety analyses |  | Regarding UNGG, pp. 86-90 |  |  |  | It is stated that there were no fires in 2021 and 2022, but information on fires occurred before should be provided.
FR-C-201 | Germany | FR | 02- Fire safety analyses |  | Regarding UNGG, pp. 86-90 |  |  |  | Information if and how combinations of fires and other hazards are considered should be provided.
FR-C-202 | Germany | FR | 02- Fire safety analyses |  | Regarding UNGG, pp. 86-90 |  |  |  | Information on the potential direct and indirect effects should be provided.
FR-C-203 | Germany | FR | 02- Fire safety analyses |  | Regarding RHF, pp. 39-45 |  |  |  | The scope of the analyses, in particular if covering also shutdown states during outages should be addressed. b) Event combinations of fires and other hazards are not addressed. Information needs to be provided.
FR-C-204 | Germany | FR | 02- Fire safety analyses |  | Regarding RHF, p. 40, also concerning MELOX, pp. 64-65 |  |  |  | The fire related safety analyses for the operating conditions lead to the identification of PIC-S and their classification in four levels. Clarification is needed on the selection of operating conditions instead of consideration of different POSs. More information on the above-mentioned four PIC levels would also provide more clarity.
FR-C-205 | Germany | FR | 02- Fire safety analyses |  | Regarding Tricastin NPP, pp. 20 and p. 23 |  |  |  | Regarding the fire scenarios, how is the fire spread considered, and, particularly, how are fire doors left open, etc. considered?
FR-C-206 | Germany | FR | 02- Fire safety analyses |  | Regarding Tricastin NPP, pp. 26 |  |  |  | Regarding the studies on fire propagation by unburned gases, could you please explain why an ignition by hot fire gases is not taken into account for such scenarios?
FR-C-207 | Germany | FR | 03.1 - Fire prevention |  | Regarding RHF, pp. 39-45 |  |  |  | Information on the consideration of the presence of permanent and transient fire loads and ignition sources in the fire safety analyses is missing.
FR-C-208 | Germany | FR | 03.1 - Fire prevention |  | Regarding RHF, pp. 39-45 |  |  |  | Detailed information how direct and indirect fire effects are assessed and which methods and data used need to be provided.
FR-C-209 | Germany | FR | 03.1 - Fire prevention |  | Regarding RHF, pp. 39-45 |  |  |  | Details on the licensee´s experience with weaknesses from the PSR are missing
FR-C-210 | Germany | FR | 03.1 - Fire prevention |  | Regarding RHF, p. 45 |  |  |  | On p. 45, one fire event is mentioned; but it is unclear how fire events and events with impact on fire protection features from RHF but also from other installations are principally considered in the fire safety analyses.
FR-C-211 | Germany | FR | 03.1 - Fire prevention |  | 100 |  |  |  | In the report, the measures for the management of movable fire loads before start of the reactor cycle at ILL are mentioned. Which measures are made for management of movable fire loads during the reactor cycle?
FR-C-212 | Germany | FR | 03.1 - Fire prevention |  | Regarding MELOX, pp. 117 |  |  |  | In section "C-IV-3.1.1. Design considerations and prevention means" it is stated in the NAR with respect to the "Rules limiting combustible materials": "The hydrogen and diesel fuel storage areas are situated outside the nuclear buildings. Inflammable chemical products are stored in fire-resistant safety cabinets ventilated by the extraction network of their installation room's ventilation system." Can you justify how spreading from hydrogen explosions/fires and diesel fuel fires in the storage areas outside nuclear buildings to these buildings is prevented (sufficient distance of ..., fire barrier quality, etc.)? What is the fire resistance rating of the safety cabinets and how is it justified?
FR-C-213 | Germany | FR | 03.2 - Active fire protection |  | Regarding Tricastin NPP, p. 136 |  |  |  | Among the listed criteria to install fixed fire extinguishing systems, unsuitable conditions for manual firefighting are not mentioned. Could you provide some information for explanation?
FR-C-214 | Germany | FR | 03.2 - Active fire protection |  | 154 |  |  |  | One of the identified weaknesses for the ILL is the lack of the own fire-fighting forces. Which measures do you have in place to compensate this weakness and to optimise the cooperation with the external fire-brigade (e.g. detailed procedures, automatic notification system in case of fire, cooperation agreements, what is the time frame to arrive)?
FR-C-215 | Germany | FR | 03.2 - Active fire protection |  | Regarding FCFs (BNI), pp. 160 |  |  |  | Remark: Lessons learned from the operating experience with issues concerning active fire protection features are addressed. This is an example of a good performance.
FR-C-216 | Germany | FR | 03.3 - Passive fire protection |  | 213 |  |  |  | The last PSR for the ILL reactor revealed some weaknesses in the fire protection. Could France please provide more information on these findings and implemented (or still planed) countermeasures?
FR-C-217 | Germany | FR | 03.3 - Passive fire protection |  | Regarding FCF (MELOX), p. 225 |  |  |  | The NAR states regarding a "Fire sector" the following: "The rooms containing a fire load density of more than 400 MJ/m2 are classified as fire sectors." Assuming that a fire sector is treated like a fire compartment consisting of typically more than one room surrounded by a 120 min fire resistant barrier, the question is why a fire load density of 400 MJ/m2 is used and what is the justification for this choice. The 120 min rating seems anyhow conservative.
FR-C-218 | Germany | FR | 03.4 - Licensee's experience |  | Regarding FCF, pp. 244-249 |  |  |  | Remark: The fire and fire protection means related operating experience of the fuel cycle facilities has been clearly addresses in section 3.4 under C. This is an example for a meaningful NAR. However, links in the respective subsection on fire safety analyses to sub-section 3.4 would be useful.
FR-C-219 | Finland | FR | 02- Fire safety analyses |  | 36 |  |  |  | Under item "III-1 a" is said "More specifically, an incipient fire is postulated in the event of a failure of rotating machines containing combustible fluids". Thus, are the non-rotating electrical components (transformers, switchgears, I&C cabinets, etc) included in the EPR fire safety analysis as ignition sources, or excluded?
FR-C-220 | Finland | FR | 02- Fire safety analyses |  | 39 |  |  |  | Under item "III-3" is said "A significant number of deviations were detected and have to be dealt with before commissioning; they encourage ASN to be very vigilant on the subject." Could you explain what are the most important deviations or the technical areas related to the deviations?
FR-C-221 | Finland | FR | 05 - Other |  | All |  |  |  | The report does not include a list of abbreviations.
FR-C-222 | Poland | FR | 01-General information |  | 7 |  |  |  | Please provide more information on why the TRICASTIN-1 reactor was selected over all 900 MW reactors in France. TRICASTIN-1 is a representative of the 900 MW CP1 reactors, while according to the IAEA Power Reactor Information System, reactors belonging to the older series - 900 MW CP0, are also operated in France, e.g. BUGEY-2.
FR-C-223 | Poland | FR | 03.5 - Regulator's assessment |  | 258 |  |  |  | Please explain how ASN wants to enforce licensees to have greater fire-fighting independence and be less reliant on the external emergency services, on which the EDF strategy is based at present, as written in point 3.6.A.
FR-C-224 | Poland | FR | 05 - Other |  | 270 |  |  |  | Please explain why the chemical purification laboratory (LPC, BNI 54), described in point 3.2.3 of the Appendix, doesn’t present significant radiological risk in case of fire.
FR-C-225 | Romania | FR | 02- Fire safety analyses |  | 27 |  |  |  | It is mentioned that the hazard studies, including the fire studies, take account of the operator intervention times. Please provide information on how these intervention times are verified and validated taking account of all the estimated conditions in the respective areas in case of fire.
FR-C-226 | Romania | FR | 03.4 - Licensee's experience | [5 empty] | Please provide some information on how are temporary modifications to fire protections features, systems and organizational arrangements managed, for nuclear power plants.
FR-C-227 | Romania | FR | 03.4 - Licensee's experience | [5 empty] | Please provide some information on how are permanent and temporary modifications to nuclear installations and administrative arrangements analyzed with regard to their potential impact on fire protection for nuclear power plants.
FR-C-228 | Romania | FR | 03.4 - Licensee's experience |  | 94 |  |  |  | It is mentioned that it is difficult to use the information on authorised fire loads in each room in its current form (no room by-room picture of the authorised fire loads). What measures have been identified and implemented to improve the verification of the actual fire loads and to prevent and detect any unauthorized changes to the fire load? Are the measures established for this purpose those mentioned in Section A-I-3.1.3.3. Overview of actions and implementation status (fire-proof boxes) or are there any other opportunities for improvement identified?
FR-C-229 | Romania | FR | 03.2 - Active fire protection |  | 96 |  |  |  | Regarding the mention of failure to return fire detector disabling permits after hot work, please provide information on generic actions taken to address this issue. Are there specific requirements for the configuration control of fire detectors and routines for checking their availability through inspection and / or testing?
FR-C-230 | Romania | FR | 03.4 - Licensee's experience | [5 empty] | Is there an ageing management program implemented for the fire protection systems and structures in nuclear power plants?
FR-C-231 | Slovakia | FR | 03.1 - Fire prevention |  | page 94; chapter A-I-3.1.3.2 |  |  |  | The chapter describes analyses of the fire events, the root cause analyses are not described. Are the root cause analyses also being carried out?
FR-C-232 | Slovakia | FR | 03.2 - Active fire protection |  | page 144; chapter A-I-3.2.5.1 |  |  |  | Is EDF considering setting up a professional fire brigade for NPPs along the lines of those from other countries? In the event of a large fire, there is a risk due to a small number of intervening power plant employees acting as internal fire brigade and a long wait time for external professsional fire brigades intervention.
FR-C-233 | Slovakia | FR | 03.2 - Active fire protection |  | page 163; chapter C-II-3.2.2.1 |  |  |  | What kind of extinguishing gas is used in the stable gas extinguishing systems?
FR-C-234 | Slovakia | FR | 03.1 - Fire prevention |  | page 268; Appendices 2.2.3 |  |  |  | Has Sodium been neutralized from the PHENIX plant ( BNI 71 ), or when is it planned for?
DE-C-235 | Austria | DE | 02- Fire safety analyses |  | 54 |  |  |  | It is mentioned, that regular fire protection inspections are carried out with the nuclear supervisory authority and the authorities responsible for fire protection. Are there any specific challenges when working with multiple authorities?
DE-C-236 | Austria | DE | 02- Fire safety analyses |  | 60 |  |  |  | It is stated that the PSR for the ZLN facility is currently awaiting final approval from the authority. Are there any preliminary results that can be shared regarding the PSR?
DE-C-237 | Austria | DE | 02- Fire safety analyses |  | 56 |  |  |  | Throughout the document authorized experts are mentioned. Could you please elaborate on the authorization/qualification process of fire protection experts?
DE-C-238 | Austria | DE | 02- Fire safety analyses |  | 54, 55, 61, 66,… |  |  |  | Throughout the document, it is mentioned that experiences from exercises are assessed to improve fire protection. Could you please elaborate on the findings of these exercises? Especially in regards to exercises with external fire brigades and joint exercises.
DE-C-239 | Austria | DE | 03.2 - Active fire protection |  | 95 |  |  |  | Are the additional water supply sources for the UAG facility part of regular exercises?
DE-C-240 | Austria | DE | 01-General information |  | 3 |  |  |  | Since the last three German NPPs went into decommissioning rather recently and in quick succession, were/are there any challenges (e.g. procedural, administrational) that needed to be overcome?
DE-C-241 | Austria | DE | 03.4 - Licensee's experience |  | 145, 149 |  |  |  | In this section, it is mentioned that the process of dismantling/decommissioning leads to the challenge of keeping up with changing and dynamic fire loads, ignition sources, etc. What are the strategies of the licensees to overcome this challenge?
DE-C-242 | Belgium | DE | 01-General information |  | 23 |  |  |  | The document states that the german regulations (KTA) require a fire protection concept and a fire hazard analysis for NPPs, and to update it regularly. In the same paragraph, a similar sentence is written for fire PSA but the scope is specified as "commercially operated NPPs". Does the distinction mean that the German regulations require to update the fire protection concept and FHA also for NPPs under decommissioning? If yes, what is the required frequency? If not, what is the reasoning for not updating the fire protection concept once under decommissioning?
DE-C-243 | Belgium | DE | 03.2 - Active fire protection |  | 83 |  |  |  | For NPPs in decommissioning, it is mentioned that the active fire protection is progressively removed from the beginning of dismantling. What is are criteria once the dismantling has began for deciding to amend progressively the active fire protection? Is it related to the fire loads evolution ? or the source term evolution? What is the meaning of 'individual boundary conditions"?
DE-C-244 | Belgium | DE | 03.2 - Active fire protection |  | 83 |  |  |  | For NPPs in decommissioning, it is mentioned that the fire detection and fire alarming are shifting from automated systems to human detection and alarming. What is the reasoning for replacing an automated system by human detection? Is it for economic reasons or related to an optimised critical path for the dismantling?
DE-C-245 | Belgium | DE | 03.2 - Active fire protection |  | 106 |  |  |  | It is mentioned that "A professional qualified fire protection officier is appointed for each nuclear power plant". Does it mean one person 7/7 24/24 (so 5 to 6 persons) or 1 person? How are the tasks of this officer performed during the off-hours, holidays or sickness? Does this mean that no other professional firefighters are available on site?
DE-C-246 | Belgium | DE | 02- Fire safety analyses |  | 29 |  |  |  | "According to the design of the installation against internal explosion (KTA 2103 /KTA 15c/) and lightning effects (KTA 2206 /KTA 22/), there is usually no causality between these events and a consequential fire." Could you further develop how fires consequential to an internal explosion or lightning event is excluded ? Is it based on derterministic and/or probabilistic considerations ? Is the risk of explosion consequential to a fire event considered ? (e.g. fire scenario involving a pressuriezd gas storage)
DE-C-247 | Belgium | DE | 03.1 - Fire prevention |  | 77 |  |  |  | In §3.1.2, the report provides an overview of the measures in place in order to minimize temporary fire loads and list some controls performed in order to ensure compliance (incl. regular fire safety-specific site walk-throughs). Are there metrics (or indicators) associated with the respect of the rules associated with fire prevention measures, including storage of combustible materials, or other insight related to the fire safety awareness of the plant personnel ?
DE-C-248 | Belgium | DE | 02- Fire safety analyses |  | 41 |  |  |  | FR MZ: "inherent safety of the reactor due to the design of the fuel elements and the fuel in a manner that even in the event of fire and/or the failure of infrastructure, no release can occur as a result of fuel assembly cladding damage" Could you explain why no release can occur as a result of fuel assembly cladding damage by a fire?
DE-C-249 | Belgium | DE | 02- Fire safety analyses |  | 42 |  |  |  | FRM II: "In the German design approach, detailed analyses of the fire effects (e.g. temperature, pressure, soot) within a fire sub-compartment are not necessary because in the event of fire, all SSC in the affected fire sub-compartment are conservatively assumed to fail" What are the safety functions to be ensured during and after a fire?
DE-C-250 | Czech Republic | DE | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
DE-C-251 | Czech Republic | DE | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
DE-C-252 | Czech Republic | DE | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
DE-C-253 | Czech Republic | DE | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
DE-C-254 | Poland | DE | 02 - Fire safety analyses |  | 58 |  |  |  | Is the number of false alarms on each nuclear unit monitored? If, such statistics are kept, what is the trend since the beginning of measurements?
DE-C-255 | Poland | DE | 03.2 - Active fire protection |  | 100, 126, 129 |  |  |  | Do regulations in Germany specify the number of on-site firefighting crew required? What number of firefighters should be provided to support fire safety activities at each nuclear power plant in Germany? Is the number of on-site firefighters the same for a nuclear power plant as for fuel cycle facilities?
HU-C-256 | Austria | HU | 02- Fire safety analyses |  | 33 |  |  |  | In this section the measures considered absolutely necessary to reduce the impact on fires for the PAE facility are listed. Further, it is mentioned wich measures are completed and wich measures are still ongoing. Namely, the installation of a closed-circuit television network and a passive protection of calb ducts. Are these measures already implemented? If not, what is the schedule for the implementation?
HU-C-257 | Austria | HU | 02- Fire safety analyses |  | 38 |  |  |  | Please elaborate on the time schedule for the construction of the tanks for temporary short-term storage of contaminated oil with built-in fire extinguishing equipment at 4 locations in the controlled access area?
HU-C-258 | Austria | HU | 02- Fire safety analyses |  | 42 |  |  |  | In this section it is mentioned that the deterministic fiere risk analysis is in a unique inter-authority zone. Are there any challenges that HAEA was/is experiencing when working toghether with another authority (in this case the authority for fire safety)? Maybe there were learnings that other authorities can benefit from?
HU-C-259 | Austria | HU | 02- Fire safety analyses |  | 50 |  |  |  | What is the schedule for the review of the PSR documentation by the nuclear safety authority, described in 2.2.5.2? Are there any preliminary results that HAEA can share? Can you specify the modifications mentioned in the last bullet point.
HU-C-260 | Austria | HU | 02- Fire safety analyses |  | 52 |  |  |  | In 2.2.7.2 it is stated that the regularity of on-site visits needs to be increased in order to discuss and check the fulfilment of the requirements at the facility. What is the frequency of on-site visits at the moment, and to what extend does it need to be increased in the opinion of HAEA?
HU-C-261 | Austria | HU | 02- Fire safety analyses |  | 52 |  |  |  | When will the development of the fire risk analysis of the BME OR facility be finished? Are there any expected outcomes?
HU-C-262 | Austria | HU | 02- Fire safety analyses |  | 60 |  |  |  | In 2.4.5.2 (Implementation status of modification/changes) it is stated that there is no significant non-conformity and therefore there is no cause for change. This would imply that there are minor non-conformities. Could you please elaborate further on those?
HU-C-263 | Austria | HU | 03.1 - Fire prevention |  | 71 |  |  |  | In section 3.1.3.1.2 it is stated that corrective actions concerning minor issues/non-compliances in the BME OR facility are not recorded in written form. What kind of issues/non-compliances are meant in this statement? Why are the corrective measures not recorded? Keeping record of these minor non-compliances and corrective actions could improve fire safety culture at the facility.
HU-C-264 | Austria | HU | 03.2 - Active fire protection |  | 99 |  |  |  | In section 3.2.3.2.3 it is stated that the primary intervener in case of a fire emergency at the KKÁT facility is the Professional Firefighting Headquaters of Paks (PFH). What happens in case the PFH is occupied with a fire at the PAE facility? Would a conventional firefighting brigade be notified? Does the PFH have enough resources to take care of two fires, one at PAE one at KKÁT?
HU-C-265 | Czech Republic | HU | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
HU-C-266 | Czech Republic | HU | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
HU-C-267 | Czech Republic | HU | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
HU-C-268 | Czech Republic | HU | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
HU-C-269 | Czech Republic | HU | 02- Fire safety analyses |  | 48 |  |  |  | Please describe further how extinguishing with halon pipes works, described on page 50, works?
HU-C-270 | Czech Republic | HU | 03.1 - Fire prevention |  | 97 |  |  |  | Which authority (regulator/ firebrigades) inspects firefighting equipment every six months?
HU-C-271 | Czech Republic | HU | 03.2 - Active fire protection |  | 87 |  |  |  | How the current use of halons compares with the requirements of Regulation (EC) No. 1005/2009 on substances that deplete the ozone layer on non-use halons even in critical structures?
HU-C-272 | Finland | HU | 02- Fire safety analyses |  | 32 |  |  |  | COMPBRN IIIe is mentioned, how the program is validated for the analysis of extensive fires in large rooms in line with corresponding analysis results? How about other fire dynamics simulation (FDS) tools?
HU-C-273 | Finland | HU | 02- Fire safety analyses |  | 32, 33 |  |  |  | What is the structural separation between turbine hall and reactor buildings?
HU-C-274 | Finland | HU | 02- Fire safety analyses |  | 33 |  |  |  | Has the turbine missiles been considered as a source for fire scenario?
HU-C-275 | Finland | HU | 02- Fire safety analyses |  | 38 |  |  |  | Why the order of magnitude of CDF during power operation of the units (2, 1, 3, 4) is different from the CDP results during shutdown of overhaul (1, 4, 3, 2)?
HU-C-276 | Finland | HU | 03.3 - Passive fire protection |  | 103, 104 |  |  |  | What is the structural separation between turbine hall and reactor buildings in PAE?
HU-C-277 | Finland | HU | 04 - Overall assessment and general conclusions |  | 119, 127 |  |  |  | The chapters 4.1.1.4 and 4.2.4 point out, that PSA is updated on a yearly basis. Regular updates of PSA are seen very important and useful based on experiences in Finland, as well.
HU-C-278 | Poland | HU | 01-General information |  | 21 |  |  |  | The method of prevention of occurence of fire in the Dedicated Spent Fuel Storage Facilities was described as control of combustible material. Could you please elaborate further on this control? How often it is conducted? Does the control of combustible material is included in an inspection plan?
HU-C-279 | Poland | HU | 03.1 - Fire prevention |  | 24 |  |  |  | In case of repacement of furniture there is requirement to use non-combustibe material. Is there any requirement regarding floors and replacing the floor? Do the new floor need to meet this requirement?
HU-C-280 | Poland | HU | 02- Fire safety analyses |  | 46 |  |  |  | What was the basis of classification of the systems performing safety functions? Which analyses were taken into account in order to allocate the weight aspect of the fires?
HU-C-281 | Poland | HU | 03.5 - Regulator's assessment |  | 71 |  |  |  | What is the fruequency of the incpection conducted by the Fire Safety Authority? Does the Nuclear Safety Authority conduct independent fire inspections?
HU-C-282 | Slovakia | HU | 01-General information |  | page37; chapter 2.1.3 |  |  |  | 50 - SG - D2 rev.1 was valid from 1992 to 2004 and is now invalid. In 2004 it was superseded by NS-G.1.7. Since 2021 NS-G-1.7 has been superseded by SSG-64. SSG - 64 and SSG - 77 are safety standards currently in force for fire safety.The report needs to be assessed in the context of currently applicable safety standards and corrected as necessary.
HU-C-283 | Slovakia | HU | 03.1 - Fire prevention |  | page 71; chapter 3.1.3.2.1 |  |  |  | The chapter describes analyses of the fire events, the root cause analyses are not described. Are the root cause analyses also being carried out?
HU-C-284 | Slovakia | HU | 03.2 - Active fire protection |  | page 83; chapter 3.2.2.2.1 |  |  |  | What kind of extinguishing gas is used? Are halons or halon alternatives still used, or is carbon dioxide used only?
HU-C-285 | Slovakia | HU | 01-General information |  | throughout the report |  |  |  | The description of the research and training reactors is more detailed than the description of PAE (Paks NPP). However, more attention should be paid to PAE throughout the report. A fire in PAE means a greater fire risk, more damage, and the possibility of affecting the plant's safety systems. Also the PAE fire brigade deserves more attention, which could be listed as good practice.
IT-C-286 | Germany | IT | 03.5 - Regulator's assessment |  | 28 |  |  |  | "the water used to estinguish the fire is collected in dedicated tanks by means of suitable drenage system realized in the floor of the facility. This in order to provide the control of any possible contamination released to the environment." Are there similar provisions against airborne contamination?
IT-C-287 | Germany | IT | 04 - Overall assessment and general conclusions |  | 32 |  |  |  | Personnel shortage "is compensated for by a good safety culture of internal staff and strict collaboration with the fire brigade." Can the shortage be fully compensated (e.g. lack of specialist knowledge)? Are other means being put to practice in order to address the problem? What are the italien approaches for this unforeseen situation?
IT-C-288 | Germany | IT | 02- Fire safety analyses |  | 42, 51 |  |  |  | "the staff and the procedures adopted are implemented considering the LENA as high-risk level. This is due because the centre is an University Building". Vs. "The LENA research reactor is considered as a low risk profile." Why is LENA sometimes considered high-risk and sometimes low-risk? Could Italy please explain this inconsistent categorisation?
IT-C-289 | Germany | IT | 01-General information |  | S.53-63 |  |  |  | Are - or to what extend are - fire protections sytems meshed between the TRIGA RC 1 and the TAPIRO? If they are meshed why was no full probabilistic FHA performed?
IT-C-290 | Poland | IT | 02- Fire safety analyses |  | 18 |  |  |  | How is the collaboration between local fire brigade and operation centre firefighters tested? What are the regulations on the training program and the frequency of the tests?
IT-C-291 | Poland | IT | 02- Fire safety analyses |  | 19 |  |  |  | How does ISIN adress poor policy of know-how transfer and human resoruces management (weakness of LENA Triga MARK II reasearch reactor)?
IT-C-292 | Poland | IT | 02- Fire safety analyses |  | 20 |  |  |  | When the fuel from the spent fuel pool at ITREC and ESSOR-B plant will be transfered to the new dry storage facility? Has ISIN compared the older approach to fire hazards and its influence on the safety aspects? Were there any provisions implemented?
IT-C-293 | Poland | IT | 03.1 - Fire prevention |  | 25 |  |  |  | How frequent are the re-evaluations of fire prevention measures and systematic checks both by ISIN and by the local fire brigade?
LT-C-294 | Czech Republic | LT | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
LT-C-295 | Czech Republic | LT | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
LT-C-296 | Czech Republic | LT | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
LT-C-297 | Czech Republic | LT | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
LT-C-298 | Poland | LT | 03.1 - Fire prevention |  | 145 |  |  |  | On the page 145 we can read that "Rooms of different categories in terms of explosion and fire hazards are separated from each other using enclosing structures or fire barriers with specified fire resistance class and their fire endurance limit." How, if at all, is location of those rooms taken into consideration? Does the proximity to room with higher risk impact the class assigned to surrounding rooms?
LT-C-299 | Poland | LT | 03.4 - Licensee's experience |  | 141 |  |  |  | regarding the OSART mission; "The team noticed that fire response process and procedures are in place however they appear complicated to implement and understand. Plant staff and contractors interviewed did not have clear notion on what to do in the event of a fire." This is a very interesting observation. Could Lithuania provide what measures are taken to ensure that the staff has a good understanding of procedures and especially what steps are taken to ensure that those procedures are easy to follow? Could you share any lessons learned from the process of making your procedures easier to understand and implement.
NL-C-300 | Belgium | NL | Graded approach |  | 38 |  |  |  | According to § 2 of the report: “Systematic and recognized methods are used and a graded approach is followed considering the type of installation, NPP, research reactors and other nuclear installations.” Concerning the FHA and PSA studies, could you identify and describe, in your opinion, the most significant safety requirements (in terms of scope, methodology, assumptions, conservatisms,… ) imposed on RRs (HFR, HOR) that have been graded compared to those imposed on the NPP (KCB)? And how does this translate into the studies actually carried out?
NL-C-301 | Belgium | NL | Review of the Fire Safety Analyses |  | 38, 41 |  |  |  | For the NPP (KCB), it is mentioned that the Fire Safety Analyses (deterministic and probabilistic) are described in corresponding documents, and frequently reviewed. The FHA is reviewed every two years and the PSA every 10 years. Based on your experience, are these frequencies adequate for covering all the major safety modifications during the intermediate period? Or should these frequencies be more closely aligned to the safety level of the modification made to the installation?
NL-C-302 | Belgium | NL | Review of the Fire Safety Analyses |  | 42 |  |  |  | The text mentions: "After implementation of NUREG/CR-6850 a fire in the control room appeared important to consider." Does it mean that the presented results (in the report) consider the scenarios of fire in the control room or not? The NUREG/CR-6850 explicitely considers fire in the control room
NL-C-303 | Belgium | NL | 2.1.3 NPP KCB Fire phenomena analyses: overview of models, data and consequences |  | 42 |  |  |  | The text mentions: "Significant effort is put in reducing the fire risk from ‘a Fire in cable room at power’. Changing the cables from the bunkered systems so they route via another room proved contradictory to general design rules. As part of the PSR of 2013 the fires dominating the PSA risk were further investigated. It was demonstrated that the calculated risk was very conservative and further actions to reduce this fire risk are not justifiable." Some explanations seem lacking: the goal of a PSA is also to verify the adequacy of the design. It seems contradictory with the PSA philosophy to state that re-routing cables to diminish the risk is contradictory to design rules. Furthermore, if the way the risk is calculated is judged as "very conservative", why not revise the study? How is this conservatism treated vs the use of PSA for Risk Informed applications? On the other hand, actual results (in E-6) are announced very conservative, but has a comparison with other countries results been made? Frequencies in E-6 seem not so conservative in comparison to results from other countries for this generation of reactor.
NL-C-304 | Belgium | NL | Results of FHA and suggested improvements |  | 43 |  |  |  | According to § 2.1.4 of the report : “The dominant scenario for the FHA is a fire in the cable spreading room, since it has the greatest fire load. This room contains mainly power cables (6 kV) for supplying motors of safety equipment. In case of a fire in this room [cable spreading room], redundant systems can be affected when the fire is not timely extinguished, which can result in the failure of safety functions of engineered safety features, and would therefore have a significant influence on nuclear safety. Fire in the cable spreading room will be extinguished D15by an automatic water firefighting system. In that scenario also a fire truck can simultaneously be supplied with water by the running fire pump.” In § 2.1.5, it is mentioned that : “For the 10EVA Periodic Safety Review (PSR) of 2013, the most important fire scenarios were evaluated for improvements in the plant. After the evaluation of the scenarios, they turned out to be conservative and no relevant improvements were to be implemented. “ It seems that the separation between the cables of redundant safety equipment is not designed in a fully satisfactory way, since a fire in the cable spreading room can lead to the loss of safety functions. As cable separation is a basic prevention principle for designing the power supply to cope with a fire, it would be useful to obtain more information on the conservatisms mentioned to exclude the fire scenarios cited and potential improvements (such as a better separation of the redundant cables).
NL-C-305 | Belgium | NL | 2.1.5 NPP KCB Periodic review and management of changes |  | 44 |  |  |  | The report mentions: "The original PSA was developed in the early 1990s, and became full scope in 1995. In 2005, the full scope Fire PSA was updated according to the NUREG-685020 and it is an integral part of the KCB PSA. As part of the Periodic Safety Review 2023, the PSA was updated for the combinations of hazards to have a more understandable approach" => it is understood that the “basis” PSA is not updated (eg: internal events etc); how do you ensure the PSA still reflects the actual status of the plant?
NL-C-306 | Belgium | NL | Full-scope PSA developed for NPP and RRs |  | 46, 58 |  |  |  | According to § 2.1.7.1. of the report : “One of the strongest points regarding the fire safety analysis at the KCB, is the early development of both a full scope PSA including fire, and the Fire Hazard Analysis, and their continuous update and improvement. EPZ uses national and international experience to keep these analyses up to date.” According to § 2.2.7.1. of the report : “The Netherlands is one of the very few countries where full-scope PSAs have been developed for non-power reactors. The safety functions and related systems to be protected against fire, together with relevant scenarios, have been identified and assessed. In the HFR, being a research reactor, various irradiation experiments are part of the daily activities. A safety assessment, including fires, is carried out for these activities as well.” These two observations can be suggested as a good practice.
NL-C-307 | Belgium | NL | 2.2.4 RR HFR Main results / dominant events (licensee´s experience) |  | 54 |  |  |  | It is not clear how fire cable frequencies are derived from the NS-G-1.7. Shouldn't it be from the NUREG/CR-6850? Furthermore, the NUREG/CR-6850 also considers other electrical components (electrical cabinets etc) and other source of ignition related to cables (caused by welding and cutting) => to which extent are these areas treated?
NL-C-308 | Belgium | NL | 3.1.1.2 NPP KCB Overview of arrangements for management and control of fire load and ignition sources |  | 88 |  |  |  | The text mentions: "For bringing in fire load in the plant, a permit of the internal fire brigade is obliged." => seems difficult to apply as nearly everything can be considered as a fire load; what are in reality the limits?
NL-C-309 | Belgium | NL | 3.1.1.2 NPP KCB Overview of arrangements for management and control of fire load and ignition sources |  | 88 |  |  |  | The text mentions: "To control the temporary fire load in the plant, the fire brigade uses a software tool to hold a total overview of the incoming and outgoing fire load. This tool is developed by using the results of the fire hazards analysis report and the fire PSA." => it is not understood how the fire analyses can be an input to hold an overview on the temporary fire loads; isn’t it linked to the maximum allowable fire loads in areas or to a list of potentially problematic areas instead?
NL-C-310 | Belgium | NL | 3.1.3.1.1 NPP KCB Design approach |  | 100 |  |  |  | It is not clear how the situation of cable spreading room is dealt within the presented regulation as the text seems to present that various redundant safety systems would be affected by a Fire in this single area
NL-C-311 | Belgium | NL | 3.1.5.1 Overviews of strengths and weaknesses in the fire protection concept |  | 104 |  |  |  | The text mentions: "However, given the operational lifetime of the KCB, one of the weaknesses is that not all the systems can be easily modified to accommodate the findings from the Fire Safety Analysis, inspections, lessons learned or the newest standards. To remedy this, a systematic approach is taken to ensure a sufficient level of protection." => can we get more information about this systematic approach? Is the cable spreading room concerned by this systematic aproach?
NL-C-312 | Belgium | NL | 3.1.5.2 Lessons learnt from inspection and assessment on the implementation of the fire protection concept as part of its regulatory oversight |  | 105 |  |  |  | The text mentions: "“The quality of the water of the fire-fighting pond of the CCB 1.600 m3 is poor. It is doubtful whether it can be used as cooling water. The risk of blocking the equipment of the fire-fighting is unknown. KFD recommends further investigation of the actual usefulness of this cooling water.” This particular comment does not impact directly the firefighting capabilities, but the use of water as a coolant in emergencies." It is not clear how it could be stated that "This particular comment does not impact directly the firefighting capabilities" as the comment specifically points to an issue about the firefighting capabilities
NL-C-313 | Czech Republic | NL | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
NL-C-314 | Czech Republic | NL | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
NL-C-315 | Czech Republic | NL | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
NL-C-316 | Czech Republic | NL | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
NL-C-317 | Czech Republic | NL | 03.1 - Fire prevention |  | 99 (21 resp.) |  |  |  | The responsibility for firefighting has been coordinated with the off-site fire brigade and is procedurally established. Is there organized practices to achieve adequate coordination between plant personnel and external personnel to ensure the familiarisation with the plant's resources and risks?
NL-C-318 | Czech Republic | NL | 03.1 - Fire prevention | [5 empty] | Has the KCB installed Passive Autocatalytic Recombiners in the containment?
NL-C-319 | Germany | NL | 01-General information |  | 30-36 |  |  |  | The Netherlands have a non-prescriptive, goal-orientated legal framework, meaning that nuclear installations have to demonstrate that they achieve the legally required safety standards. For this demonstration many different international nuclear codes and standards are used (e.g. regulations of the IAEA, USA, Germany). The Netherlands are using codes and standards form many different countries and international organisations. Are there arrangements in place in the Netherlands to ensure that the essential legal requirements are fully met and that safety is not compromised?
NL-C-320 | Germany | NL | 02- Fire safety analyses |  | 45 |  |  |  | According to the NPP KCB Licensee’s experience it is a weakness that no Fire Hazard Analysis of the waste storage building has been developed. Are there any plans to develop a FHA of the waste storage building at NPP Borssele? Could the Netherlands please give a possible timeline for development or in case if not, the main reasons for not developing a FHA for the waste storage building?
NL-C-321 | Germany | NL | 02- Fire safety analyses |  | 64 |  |  |  | The HOR is one of the few nuclear facilities with limited power realizing a PSA (incl. a fire risk analyses), which was identified as a strength. Could the Netherlandsplease provide more information on the major findings/improvements that were gained from the PSA regarding the fire protection?
NL-C-322 | Germany | NL | 02- Fire safety analyses |  | 65 |  |  |  | One of the identified weaknesses is that the last complete revision of the licence for HOR was done in the year 1996. What is the current documentation status of HOR? Does it comply with the regulatory requirements? Is the existing documentation still valid? If some updates are necessary, please provide more information on which documents and when should be updated?
NL-C-323 | Germany | NL | 02- Fire safety analyses |  | 66 |  |  |  | How do you generate reliable data for the input of the PSA analysis for the Uranium enrichment Plant?
NL-C-324 | Germany | NL | 02- Fire safety analyses |  | 73 |  |  |  | Why is the risk of using water to extinguish fire in the Urenco Uranium Enrichment Plan negligible?
NL-C-325 | Germany | NL | 02- Fire safety analyses |  | Regarding WSF at KCB, p. 83 |  |  |  | Why is it considered that "Fire ignition or fire propagation to the fire cell containing radioactive sources will directly lead to a full radioactive release from the building to the atmosphere. This is applicable when the fire cell containing the radioactive sources, does not have a complete barrier or..." if the cells are plugged or sealed. Isn't that too conservative?
NL-C-326 | Germany | NL | 02- Fire safety analyses |  | Regarding WSF at KCB, p. 83 ff. |  |  |  | How are changes and modifications addressed in the fire safety analyses?
NL-C-327 | Germany | NL | 02- Fire safety analyses |  | Regarding WSF at KCB, p. 83 ff. |  |  |  | Are PSRs performed for this facility?
NL-C-328 | Germany | NL | 02- Fire safety analyses |  | Regarding KCB NPP, pp. 38-47 |  |  |  | In the NAR core damage frequencies for power operation and for low-power and shutdown states are separately presented as results from Fire PSA. What is the fuel damage frequency for the SFP? And what is the overall contribution of fires to CDF and FDF?
NL-C-329 | Germany | NL | 02- Fire safety analyses |  | Regarding KCB NPP, p. 39 |  |  |  | Combinations of fire with external hazards are considered in fire safety analyses, but to what extent and how are other combinations, e.g. with internal hazards considered?
NL-C-330 | Germany | NL | 02- Fire safety analyses |  | Regarding KCB NPP, p. 41 |  |  |  | The NAR states: "Containment approach: A fire compartment of the KCB has a fire resistance of at least 60 minutes (F60) according to the rules of the Buildings Decree (Bouwbesluit)." This is unusual in Europe. Why is the minimum standard fire resistance rating not 90 min? Deviations are possible with justification.
NL-C-331 | Germany | NL | 02- Fire safety analyses |  | Regarding KCB NPP, pp. 38-47 |  |  |  | The consideration of operating experience (i) from fire events and (ii) for events related to fire protection features, (a) from KCB and (b) from other NPPs being relevant and/or from other installations (as generic information) is missing. Please provide the information.
NL-C-332 | Germany | NL | 02- Fire safety analyses |  | Regarding KCB, p. 41 |  |  |  | "The containment approach is the preferred approach; the influence approach is an alternative for it. The influence approach is applicable in about 54 % of all cases." Could you explain the given 54 % fraction? How it is calculated? Does "lower fire resistance than F 60" practically mean that separation is F 0 or what kind of barriers are practically used? Could you provide examples?
NL-C-333 | Germany | NL | 02- Fire safety analyses |  | Regarding KCB, p. 42 |  |  |  | "The capacity for the automatic firefighting of the oil systems of the main coolant pumps is 33 kg CO2." The amount of CO2 seems quite low. Could you comment this?
NL-C-334 | Germany | NL | 02- Fire safety analyses |  | Regarding KCB, p. 43 |  |  |  | "The dominant scenario for the FHA is a fire in the cable spreading room, since it has the greatest fire load. This room contains mainly power cables (6 kV) for supplying motors of safety equipment. In case of a fire in this room, redundant systems can be affected when the fire is not timely extinguished, which can result in the failure of safety functions of engineered safety features, and would therefore have a significant influence on nuclear safety. Fire in the cable spreading room will be extinguished by an automatic water firefighting system. In that scenario also a fire truck can simultaneously be supplied with water by the running fire pump." It reads like fire fighting with water takes place while the redundant trains are operable and under electrical power. How this is dealt with by the fire brigade?
NL-C-335 | Germany | NL | 02- Fire safety analyses |  | Regarding HFR, pp. 48-60 |  |  |  | It is mentioned in the NAR that in the HFR no larger fire events occurred during the last 10 years. However, what is the situation with smaller incipient fire events? The information on operating experience (i) from fire events and (ii) for events related to fire protection features, (a) from KCB and (b) from other RRs being relevant and/or from other installations (as generic information) and its consideration in the fire safety analyses should be provided .
NL-C-336 | Germany | NL | 02- Fire safety analyses |  | Regarding HFR, pp. 48-60 |  |  |  | Have the improvements required from the INSARR mission and from the Nuclear Insurance Pool survey regarding fire safety already been implemented or what is the status for completion?
NL-C-337 | Germany | NL | 02- Fire safety analyses |  | Regarding HOR, pp. 60-66 |  |  |  | The fire cell approach applied in the fire safety analyses for the HOR is no more state-of-the art (not enough conservative, see SSG-64),but a fire compartment approach should be used. Are there any plans for modifying the analyses correspondingly?
NL-C-338 | Germany | NL | 02- Fire safety analyses |  | Regarding HOR, pp. 60-66 |  |  |  | Combinations of fires and other hazards are only partly addressed. A systematic approach is expected. Clarification should begiven in how far other external and internal hazards in combination with fires are addressed (according to SSG-64).
NL-C-339 | Germany | NL | 02- Fire safety analyses |  | Regarding HOR, pp. 60-66 |  |  |  | It is mentioned in the NAR that the IAEA IRS database is used as generic data source regarding fire events from other installations. However, the information on operating experience (i) from fire events and (ii) for events related to fire protection features, (a) from KCB and (b) from other RRs being relevant and/or from other installations (as generic information) and its consideration in the fire safety analyses should be provided.
NL-C-340 | Germany | NL | 02- Fire safety analyses |  | Regarding HOR, pp. 60-66 |  |  |  | Clarification is needed on the treatment of direct and indirect fire effects.
NL-C-341 | Germany | NL | 02- Fire safety analyses |  | Regarding FCF UNL, pp. 66-74 |  |  |  | A Level 3 PSA is conducted for UNL. This is much more than done in other countries and particularly for this type of installation. Such an analysis could be assessed as a good practice. However, the question is, if the Level 3 PSA (covering fire consequences) is based on a Level 1 and Level 2 PSA (as required in IAEA SSG-3 and SSG-4). Probably this only needs to be precisely stated.
NL-C-342 | Germany | NL | 02- Fire safety analyses |  | Regarding FCF UNL, pp. 66-74 |  |  |  | In line with IAEA SSG-5, combinations of fires and some external hazards are considered. Information on the consideration of combinations of fires with other internal hazards is widely missing and should be systematically given.
NL-C-343 | Germany | NL | 02- Fire safety analyses |  | Regarding FCF UNL, pp. 66-74 |  |  |  | Clarification is needed on the treatment of direct and indirect fire effects.
NL-C-344 | Germany | NL | 02- Fire safety analyses |  | Regarding WSFs at other sites, pp. 85-86 |  |  |  | Combinations of fires and external hazards are considered. Information on the consideration of combinations of fires with other hazards (internal and external hazards) in general should also be provided.
NL-C-345 | Germany | NL | 02- Fire safety analyses |  | Regarding HFR, p. 52 |  |  |  | "• Criterion 2: The exposing cell contains a fire load density of less than 900 MJ/m2 (as defined in HFR internal documentation) and the fire cell boundary consists of a one-hour rated fire barrier on the basis that the fire barrier will prevent a fire spread to the adjacent cell." The filter criterion does not seem to be conservative, at least when the ventilation under fire conditions is not limited. How the criterion is established/justified?
NL-C-346 | Germany | NL | 03.1 - Fire prevention |  | Regarding KCB |  |  |  | Could you add the fire specific characteristics of the turbine oil used?
NL-C-347 | Germany | NL | 03.1 - Fire prevention |  | 93-94 |  |  |  | Are there any exercises (regularly) performed at KCB regarding the cooperation of the internal fire brigade with the external fire brigade(s)?
NL-C-348 | Germany | NL | 03.1 - Fire prevention |  | 95 |  |  |  | For a better understanding - could the Netherlands please clarify the difference between the "provincial governmental fire brigade" and the the off-site fire brigade of the villages Borssele or Nieuwdorp? Which one will be preferred to support the internal fire brigade?
NL-C-349 | Germany | NL | 03.2 - Active fire protection |  | Regarding KCB, p. 88+ |  |  |  | The number of installed fire detectors (approx. 2000) is large, but it is not explained by which criteria the rooms that are monitored by automatic fire detectors are selected.
NL-C-350 | Germany | NL | 03.2 - Active fire protection |  | Regarding KCB, p. 88+ |  |  |  | "... Based on this alarm, the control room operator will take measures such as directing the fire brigade to the affected room or call for the off-site fire brigade, if deemed necessary. The alarm consists of two levels: an early warning and an actual alarm." When is the first alarm level used and what does "early warning" means in that context?
NL-C-351 | Germany | NL | 03.2 - Active fire protection |  | Regarding KCB, p. 90 |  |  |  | Chapter, 3.1.2.2.2, could you explain the difference between "micro drop" and "fine water spray" system . It is not clear whether "micro drop" is used as a brand name.
NL-C-352 | Germany | NL | 03.2 - Active fire protection |  | Regarding KCB, p. 90 |  |  |  | Could you specify the use of the "high pressure extinguishing" system? Which systems or areas are supplied by it?
NL-C-353 | Germany | NL | 03.2 - Active fire protection |  | Regarding KCB, p. 95 |  |  |  | It is written: "The fire brigade consists of a commander, pump operator and two firemen. …" later on it is written: "EPZ fire brigade, 24/7 on shift, composed of a fire team leader, shift operators, truck driver and guide (five employees per firefighting team per shift, the first attack team), which makes use of on-site extinguishing equipment ..." It reads that two firemen are planned as a first attack team using breathing equipment. Will there be a rescue team on standby?
NL-C-354 | Germany | NL | 03.2 - Active fire protection |  | Regarding KCB, p. 95 |  |  |  | The six normative fire scenarios work with quantitative criteria "for approaching the location for incident response". Could you comment on how the criteria are calculated and what do they imply for the timeline of such a scenario?
NL-C-355 | Germany | NL | 03.2 - Active fire protection |  | Regarding HFR, p. 108 |  |  |  | It is written that for some HFR buildings only "partial monitoring" is undertaken. By which criteria is the deployment of fire detectors decided?
NL-C-356 | Germany | NL | 03.2 - Active fire protection |  | Regarding HFR, p. 109 |  |  |  | On firewater supply it is written: "Throughout the EHC, above-ground fire hydrants on a potable water supply system with a capacity of 2,000 litres per minute have been installed as a primary supply." Is there an additional, redundant supply available?
NL-C-357 | Germany | NL | 03.2 - Active fire protection |  | Regarding UNL, pp. 140-141 |  |  |  | Remark (for discussion in workshop): There is no professional on-site fire brigade available. This is different compared to other installations. However, the onsite first responders, etc. are well-trained regularly and familiar with the situation. This issue could be a nicer discussion point of pros and cons in fire brigade presence, etc.
NL-C-358 | Germany | NL | 03.2 - Active fire protection |  | Regarding HFR, p. 83 |  |  |  | On fire resistance it is written: "According to the Dutch reference ‘Jaarboek Brandbeveiliging 2002’, a combustible fire load of 19 MJ/m2 corresponds to an approximate duration for fire combustion of 1 minute (i.e., 900 MJ/m2 = 47 minutes; 230 MJ/m2 = 12 minutes)." Could you validate this approach? Remark: This simplified approach is considered not conservative in comparison to other approaches like NFPA Fire Severity, US NRC Fire Dynamic Tools, or KTA 2101.2.
NL-C-359 | Germany | NL | 03.2 - Active fire protection |  | Regarding KCB, p. 100 |  |  |  | It is written: "Redundant cables in the same compartment (influence approach) that are at a distance of 1.5 m or less, are separated from each other by means of a fire-resistant coating." Could you comment on the 1.5-m-criterion? Where is it justified?
NL-C-360 | Germany | NL | 03.2 - Active fire protection |  | 106 |  |  |  | It is stated that the HFR comply with the Building decree of 2012 and the current building code and regulations are met only to some extent. What gaps the Netherlands did identify in complying with the current regulations? Could the netherlands please elaborate on the actions to be taken?
NL-C-361 | Germany | NL | 03.2 - Active fire protection |  | 108 |  |  |  | It is stated that not all building of HFR are equipped with fire alarm. What is the reason for that? Are there plans to improve? Could the Netherlands please share more information?
NL-C-362 | Germany | NL | 03.2 - Active fire protection |  | 108 |  |  |  | In the event of a fire alarm, the Quick Response Team at the HFR is present in any location on site within six minutes. Could the Netherlands please describe how long does it take for the external fire brigade to arrive and to support the QRT in case of fire? Is there an automatic alarm system for the external fire brigade?
NL-C-363 | Germany | NL | 03.2 - Active fire protection |  | 113 |  |  |  | The HFR has a cooperation with an external local fire brigade.If there are clear procedures (roles, responsibilities, etc.) covering the interface between QRT and the external fire brigade, could the Netherlands please describe them?
NL-C-364 | Germany | NL | 03.2 - Active fire protection |  | Regarding HFR, p. 116 |  |  |  | It is written: "The HFR periodically assesses the fire resistance and stability values of the fire cells and compartments and, if necessary, calls in external expertise. In these assessments, the Building Decree is taken as a starting point." Does the Building Decree require 60 min or 90 min fire resistance?
NL-C-365 | Germany | NL | 03.2 - Active fire protection |  | 125-127 |  |  |  | How long does it take upon alerting that the external fire brigade (VRH-b) arrives at the HOR?
NL-C-366 | Germany | NL | 03.2 - Active fire protection |  | 127 |  |  |  | Could the Netherlands please specify the minimum number of individuals who are belonging to the Emergency Response Fire Service (BHV-b) at HOR?
NL-C-367 | Germany | NL | 03.2 - Active fire protection |  | 128 |  |  |  | How ist it ensured that in case of a fire at the HOR the extrenal fire brigade is able to use the entrances, especially the RSA protected door for trucks?
NL-C-368 | Germany | NL | 03.2 - Active fire protection |  | Regarding HOR, p. 129 |  |  |  | It is written: "The fire delay time of the rooms/buildings depends on the applied standard for the construction." Is the "fire delay time" similar to the fire resistance?
NL-C-369 | Germany | NL | 03.4 - Licensee's experience |  | Regarding KCB |  |  |  | The original standard fire resistance was F 60. When doors, dampers etc. are changed, is KCB willing to upgrade to F 90 rated components?
NL-C-370 | Germany | NL | 03.4 - Licensee's experience |  | 146 |  |  |  | Could the Netherlands please provide the relevant reference to the report on the nine fire alarms at URENCO?
NL-C-371 | Poland | NL | 03.2 - Active fire protection |  | 58 |  |  |  | How the placement of the extra fire detectors in the building was determined? What kind of smoke detectors was selected and what led to this choice?
NL-C-372 | Poland | NL | 02- Fire safety analyses |  | general |  |  |  | In the safety assesment, how is the cliff-edge effect taken into the consideration?
PL-C-373 | Germany | PL | 01-General information |  | 12 |  |  |  | If needed water for fire fighting could be gained from the Świder River. Could Poland please elaborate if using this river is possible at each time of the year - especially under dry and hot weather conditions in summer and are there special precautions for maintenance of accessibility?
PL-C-374 | Germany | PL | 02- Fire safety analyses |  | 18 |  |  |  | It is stated that the fire safety analyses were conducted using probabilistic methods. Could Poland please give more information on the analysis methods. What kind of probabilistic methods were used, was the full scope PSA performed? What were the major findings?
PL-C-375 | Germany | PL | 02- Fire safety analyses |  | 18 |  |  |  | Poland refer MARIA reactor as a low risk facility. However, according to the technical specification for "research reactors, two categories are considered: - RRs with a higher risk profile: RRs with a thermal power ≥ 1 MWth as well as RRs with a thermal power < 1 MWth and with an important additional risk, - RRs with a lower risk profile: RRs with a thermal power < 1 MWth, which do not have any significant additional risk". Please verify the statement on the risk profile of MARIA (thermal power of 30 MW).
PL-C-376 | Germany | PL | 02- Fire safety analyses |  | 19 |  |  |  | It is said that the direct and indirect consequence calculations to determine the specific impacts of a fire are not performed as part of the analyses for the MARIA reactor. Could Poland please explain, what was the subject of the fire analysis and what were the major findings?
PL-C-377 | Germany | PL | 02- Fire safety analyses |  | 20 |  |  |  | In the result of the fire hazard analysis that was performed as part of PSR, some upgrades and corrective actions were identified. What are the identified findings and waht can be said about the status of their implementation? Could Poland please explain that.
PL-C-378 | Germany | PL | 02- Fire safety analyses |  | 21 |  |  |  | - 2.6.1 How do you want to deal with the problem of more frequent training and cooperation between own emergency units and fire brigade (state and voluntary)?
PL-C-379 | Germany | PL | 02- Fire safety analyses |  | 21 |  |  |  | - 2.6.1 Could Poland explain wether the fire brigade is called automatically or by the own emergency service? If not automatically who decides to call and when and why?
PL-C-380 | Germany | PL | 03.1 - Fire prevention |  | 23 |  |  |  | - 3.1.1 In the NAR, labeled areas are described to store flammable and hazardous materials. Could Poland explain wether these areas monitored seperatly or in a special way with special or additional detectors?
PL-C-381 | Germany | PL | 03.1 - Fire prevention |  | 24 |  |  |  | - 3.1.2 Could Poland explain are there further requirements for hot work permission like presence of fire extinguisher, after work visits to take care of smoldering fires, etc.?
PL-C-382 | Germany | PL | 03.1 - Fire prevention |  | 26 |  |  |  | - 3.1.4.2 Could Poland explain are these inspections unannounced for the licencee and how often are these inspections done?
PL-C-383 | Germany | PL | 03.1 - Fire prevention |  | 26 |  |  |  | One of the identifies weaknesses was "mess and disorder resulting from leaving residues from some work, including flammable materials, in inappropriate places (fire escapes, rooms subject to fire load restrictions)" that the inspectors claimed about. What actions are foreseen (or already implemented) to improve the work organisation and the safety culture attitude of the reactor personnel?
PL-C-384 | Germany | PL | 03.2 - Active fire protection |  | 27 |  |  |  | It is stated that in accordance with the requirements of the expertise, and in agreement with the Provincial Headquarters of the State Fire Service in Warsaw, the fire alarm system from the reactor building does not automatically transmit notification to the Fire Service or any other external services. What is the procedure to notify the external fire brigade(s)? Will all differrent external fire units in Otwock and Warsaw be announced at the same time in case of a fire incident? Could you consider an automatic notification in order to reduce the reaction time?
PL-C-385 | Germany | PL | 03.2 - Active fire protection |  | 30 |  |  |  | Could Poland please give more information regarding the "user" who is in charge to perform the daily and monthly inspection of the fire alarm system? Who is "the user" clearly? Is this information documented?
PL-C-386 | Germany | PL | 03.2 - Active fire protection |  | 30 |  |  |  | In case of the major repairs, the affected hydrants are marked with a "NOT FUNCTIONING" sign. Are there any further notifications, e.g. how far and in which direction the functioning hydrant may be found? Do you consider other alternative solutions, e.g. installing a bypass line?
PL-C-387 | Germany | PL | 03.2 - Active fire protection |  | 31 |  |  |  | During the quarterly inspection, the activation of at least one detector or manual fire alarm in each fire zone should be checked. How do you ensure that all the detectors will be frequently checked during these inspections (and not always the same one is triggered)?
PL-C-388 | Germany | PL | 03.2 - Active fire protection |  | 36 |  |  |  | - 3.2.3.3 If there are busses used for evacuation are these busses available 24/7 (always fuelled, enough drivers, maintained, etc.) or is there an alarm chain and evacuation needs more time? If yes, how long does it take?
PL-C-389 | Germany | PL | 03.4 - Licensee's experience |  | 40 |  |  |  | One of the weakness identified is that only alternative solutions specified in the Fire Protection State Expertise are implemented. Could Poland explain if the implemented alternative solutions are adequate to fulfil current regulatory requirement on the fire protection? If there are some gaps identified, please elaborate on the corrective actions and the plan for its implementation.
RO-C-390 | Czech Republic | RO | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
RO-C-391 | Czech Republic | RO | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
RO-C-392 | Czech Republic | RO | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
RO-C-393 | Czech Republic | RO | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
RO-C-394 | Germany | RO | 02- Fire safety analyses |  | 23 |  |  |  | How does Romania maintain the subcriticality in your facility in case of a fire?
RO-C-395 | Germany | RO | 02- Fire safety analyses |  | 29 |  |  |  | Does Romania has an event reporting system to generate experience feedback and lessons learned from events that occur in the Nuclear Fuel Manufacturing Plant?
RO-C-396 | Germany | RO | 04 - Overall assessment and general conclusions |  | 78 |  |  |  | Does Romania share operatinal feedback in the international community for example in the IAEA FINAS Database?
RO-C-397 | Poland | RO | 03.2 - Active fire protection |  | 39; 54 |  |  |  | What are the types of extinguishing agents used in Romanian nuclear installations: HFC, FM-200, Novec 1230 or other?
RO-C-398 | Poland | RO | 03.1 - Fire prevention |  | 10; 11; 12; 14; 18; 20; 34; 66 |  |  |  | Have steps been taken for full implementation of halogen-free cables in Romanian nuclear installations?
SK-C-399 | Austria | SK | 01-General information |  | 18, 56, 107ff |  |  |  | On page 18 it is stated that in the case of major differences in fire protection between Mochovce Unit 3 and MO1&2 and EB3/4 are highlighted in the report. In several subchapters information on differences is given, but there are several subsection where information seems to be missing. Please provide further information on those subsections, especially on subsection 3.4.1 (page 107ff) and subsection 3.2.1.1.2 (Page 56ff).
SK-C-400 | Austria | SK | 01-General information |  | 20 |  |  |  | Please provide further information on the FP design documentation update for MO1&2. Are there similar processes ongoing or planned for EBO 3/4?
SK-C-401 | Austria | SK | 01-General information |  | 21 |  |  |  | Presented on page 21 "In the case of the MO3&4 NPP design, this is a significant shift in safety as a result of the implementation of the current legal requirements compared to the operating units in Mochovce and Bohunice." Please elaboarate if MO3&4 will serve as benchmark for future enhancements in FP for MO1&2 and BO3&4.
SK-C-402 | Austria | SK | 02- Fire safety analyses |  | 23, 31 |  |  |  | Please provide further information on the rational why at a mulitple unit site "two or more fires are not anticipated at the same time at Units 1, 2, 3 or 4 of the Mochovce NPP", especially for the case of an earthquake as postulated event. Do you plan to include such analysis in future assessements?
SK-C-403 | Austria | SK | 02- Fire safety analyses |  | 23, 31 |  |  |  | On page 23 and 31 it is stated that "the occurrence of a fire and another event (e.g. LOCA) at the same time is not postulated, except where it is clear from the analysis that a fire is likely to cause an accident, or vice versa, where an examination of the other risks gives rise to such a risk". Please provide further information on events were such combinations cannot be excluded.
SK-C-404 | Austria | SK | 02- Fire safety analyses |  | 27, 31 |  |  |  | Do you intend to include combinations of events for future probabilistic fire risk assessement, like fire and interal initiating events, fire and internal hazards (internal flooding and HELB), fire and seismic initiating event, fire and other external evnts, fire and explosions, mulitiple compartment fire interaction analysis?
SK-C-405 | Austria | SK | 02- Fire safety analyses |  | 38 |  |  |  | Please provide further information on the CDF contribution in different plant operating states and add data for MO1&2 and EBO 3&4 to allow comparison between the new designed and the exsting units.
SK-C-406 | Austria | SK | 02- Fire safety analyses |  | 40 |  |  |  | On page 40 it is stated "As part of the MO3&4 NPP design, approximately 40 design modifications have been implemented since 2008 with an impact on the original fire safety design". Please provide further information the lessons learned and the retrofitting measures for the existing plants.
SK-C-407 | Austria | SK | 03.1 - Fire prevention |  | 51f |  |  |  | Please provide information on special procedures if the NPP is in shutdown and outage and refueling mode.
SK-C-408 | Austria | SK | 04 - Overall assessment and general conclusions |  | 123 |  |  |  | For completeness, please add the total number of recorded fires on page 123.
SK-C-409 | Czech Republic | SK | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
SK-C-410 | Czech Republic | SK | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
SK-C-411 | Czech Republic | SK | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
SK-C-412 | Czech Republic | SK | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
SK-C-413 | Czech Republic | SK | 03.2 - Active fire protection |  | 89 |  |  |  | What is the concept of deploying external forces according to the alarm plans mentioned in Article 3.2.1.3.2 last paragraph. How were the alarm plans of both NPPs created and what do they look like?
SK-C-414 | Germany | SK | 02- Fire safety analyses |  | Regarding NPPs, par. 2.1.1, B. PSA, p. 28 |  |  |  | Why is only the combination of seismic events and fire analysed within the PSA (and probably only the combination of earthquake and consequential fire, but not the occurrence of both events coincidentally)? Justification is needed here, this limited analysis need at least some justification and explanation if and if yes, how other event combinations have been screened out. Why are combination of fires and other internal hazards are not analysed? Is the situation the same for both NPP sites, and if yes why? The statement on p. 28 is not in line with the statement on p. 32 that the "methodology for preparing the fire PSA, is based on the assessment approach and methodology described in IAEA Safety Standards No. SSG-3 [28], No. SSG-64 [29], No. SSG-77 [30], US NRC guides/documents, and the ASME standard.". The requirements, particularly of SSG-64 and SSG-77 o not seem to be fulfilled. Please provide clarification and justification.
SK-C-415 | Germany | SK | 02- Fire safety analyses |  | Regarding NPPs, par. 2.1.3, A. Deterministic FHA, p. 34 |  |  |  | It seems that when determining the accidental fire load (this should be the transient fire loads) is not performed for low-power and shutdown states. Can you confirm this and if yes, provide more details why this is not done?
SK-C-416 | Germany | SK | 02- Fire safety analyses |  | Regarding NPPs, par. 2.1.3, A. Determnistic FHA, p. 35 |  |  |  | How do you determine an adequate fire resistance rating? It is stated in the list in the NAR that the fire load is determined. But the fire load density [MJ/m2] is the important parameter. Do you consider that for the determination of the fire resistance rating?
SK-C-417 | Germany | SK | 02- Fire safety analyses |  | Regarding NPPs, par. 2.1.3, A. Determnistic FHA, p. 36 |  |  |  | Do you still use the COMPRN IIIe fire simulation code, which is no longer state-of-the art?
SK-C-418 | Germany | SK | 02- Fire safety analyses |  | Regarding NPPs, par. 2.1.3, B. Fire PSA, p. 37 |  |  |  | It is stated: "A 20-foot (about 6.5 m) clear space is considered a fire barrier." This is a spatial separation by distance but not a certified barrier. How is it justified that this distance is sufficient and that spreading of direct (heat, smoke, soot, etc.) and/or indirect fire effects (e.g. by extinguishing agent), particularly in case of an event combination of fire and other (internal or external) hazards, can be excluded from the PSA?
SK-C-419 | Germany | SK | 02- Fire safety analyses |  | Regarding NPPs, par. 2.1.3, B. Fire PSA, p. 38 |  |  |  | According to the assumptions for the Fire PSA in the NAR a damage of passive components, e.g. a pipe, as a result of a fire is not assumed. How is this justified?
SK-C-420 | Germany | SK | 02- Fire safety analyses |  | Regarding NPPs, par. 2.1.3, B. Fire PSA, p. 38 |  |  |  | No fuel damage frequency seems to be determined, a Fire PSA for low-power and shutdown states is not mentioned. If that observation is correct, why hasn´t such an analysis not been performed?
SK-C-421 | Germany | SK | 02- Fire safety analyses |  | Regarding NPPs, par. 2.1.3, pp. 34-38 |  |  |  | Electrically induced fires (including fires from high energy faults, HEAF) typically provide a high contribution to CDF and FDF. These are not addressed in par. 2.1.3. Can you give an explanation and provide justification for this? Therefore the question arises if the Fire PSA is sufficiently conservative and realistic, if several potentially important scenarios are not addressed. In addition, the operating experience from reportable and non-reportable fire events and events with fire protection features deterioration/damage (both plant specific and generic) is neither addressed in the NAR to be considered in the deterministic nor in the probabilistic fire safety analyses. Can you please provide clarification on this aspect as well?
SK-C-422 | Germany | SK | 02- Fire safety analyses |  | Regarding NPPs, par. 2.1.7, p. 50 |  |  |  | Approx. 40 design modifications are mentioned in the NAR regarding fire safety. Details are missing. Can you at least provide information on the most significant modifications?
SK-C-423 | Germany | SK | 02- Fire safety analyses |  | Regarding SFSF, par. 2.4, SFSF, p. 42-46 |  |  |  | Apart from the questions regarding the different plant operational states (POSs) nearly all questions regarding fire safety analyses for thr NPPs also apply to the SFSF. Can you please provide answers here as well?
SK-C-424 | Germany | SK | 02- Fire safety analyses |  | Regarding NPPs, par. 2.7.1, p. 48 |  |  |  | Under strengths and weakness the NAR mentions "fire proofing of the cabling" and the use of "fire resistant cables". Can you clarify what the term fire proofing of the cabling" means? To our knowledge, fire resistant cables do not exist, but only fire retardant ones with improved characteristics in the event of fire (e.g. FRNC cables). Can you please give clarification what is meant in the NAR in this context Can you please provide details on the certification of the "fire-proof spray coatings of cables" .that "were applied at the reference NPP MO 1 & 2 before its commissioning"? According to our experience cable coatings are not rated as fire-proof.
SK-C-425 | Germany | SK | 03.1 - Fire prevention |  | Regarding MO3&4 NPP, par. 3.1.1.2, A., p. 53 |  |  |  | Can you please justify the certification of fire retardant cables in the areas mentioned on p. 53 for MO 3 & 4 NPP?
SK-C-426 | Germany | SK | 03.1 - Fire prevention |  | Regarding EBO3&4 and MO1&2 NPP, par. 3.1.1.2, A., p. 53 |  |  |  | In the NAR it is stated: "In NPP EBO3&4 and NPP MO1&2, within the framework of increasing the level of nuclear safety, spraying with fire protection coating was carried out on all system (critical in terms of nuclear safety) cable ducts, cables and structures located in fire sections with fire duration greater than EI 90 in accordance with the Decree of the MoI No. 94/2004 [7]. In the case of design modifications, existing cables are replaced in these areas with fire retardant cables." What is the quality of the cable coating sprayed on cables (e.g. intumescent or ablative)? Why doe you apply it only in areas where a fire duration of than 90 min is assumed? For the replacement of cablers by fire retardant ones, can you provide justification for the certification of these?
SK-C-427 | Germany | SK | 03.1 - Fire prevention |  | Regarding NPPs, par. 3.1.1.2, B., p. 53 |  |  |  | In the NAR nothing is stated that you consider electrical faults, (e.g. high energy arcing faults, HEAF) as potential fire source? Can you provide an explanation why this fire source is not accounted for?
SK-C-428 | Germany | SK | 03.3 - Passive fire protection |  | Regarding ISFS, par. 3.3.4.1.2, p. |  |  |  | Why are the required fire resistance ratings of different types of structures different depending on their type, e.g. above ground floor and other below? Can you provide information for clarification/explanation and justification?
SK-C-429 | Germany | SK | 03.4 - Licensee's experience |  | Regarding NPPs, par. 3.4.1.2, pp. 113-114 and regarding ISFS, p. 117 |  |  |  | As already in the section on fire safety analyses, information on the consideration of the operating experience from fire events as well as from events with deterioration of active and/or passive fire protection means is missing. Can you pleasde provide the respective information?
SK-C-430 | Finland | SK | 02- Fire safety analyses |  | 27, 36, 38-39, 49-50 |  |  |  | Combinations of fires and other events are included in the analysis according to the chapters 2.1.1, 2.1.3 and 2.8.2. Within the results being discussed in the chapter 2.1.4, nothing is mentioned about the event combinations. What is your conclusion on the significance of the combinations of fires and other events compared to the internal fires?
SK-C-431 | Poland | SK | 03.2 - Active fire protection |  | 77; 84 |  |  |  | Are off-site fire brigades adequately trained in extinguishing nuclear installations? Are they properly equipped with dosimetric devices? Do they regularly train with the Plant Fire Brigade?
SK-C-432 | Poland | SK | 03.1 - Fire prevention |  | 52 |  |  |  | Have steps been taken for full implementation of halogen-free cables in Slovakian nuclear installations?
SK-C-433 | Poland | SK | 03.1 - Fire prevention |  | 52 |  |  |  | Are I&C cabinets equipped with a fire extinguishing system that allows the extinguishing agent to be introduced individually into the cabinet where the fire occurred?
SI-C-434 | Austria | SI | 01-General information |  | 8 |  |  |  | Please provide information on the fire protection of the research reactor. As mentioned in the report, after the event in 2010 a fire safety improvement campain has been implemented. Detailed information on the campain is of interest for other countries with similar RR. Was a PHA performed after this event, and does this PHA and the informations gathered from the 2010 event consitute your path towards the implementation of SRL for RR?
SI-C-435 | Austria | SI | 02- Fire safety analyses |  | 112f |  |  |  | In the report it is mentioned that no seperate FHA for the RWSF has been performed in the past. Nevetheless NEK considers RWSF as a separate fire area (RWS) in the newly prepared revision of fire safety analysis which was under review at the time of the report publication. Please provide further information on the status of the review of the FHA for the RWSF?
SI-C-436 | Austria | SI | 02- Fire safety analyses |  | 19, 20, 46, 127, 147 |  |  |  | On page 20 a list of combinations of fire triggered events with other events is presented. On page 127 it is noted that, Krško NPP Fire Protection System is not seismically qualified and might face degradation (page 46). Are there credible scenario in which an earthquake might trigger an internal fire and the non seismically qualified FPS might induce an addional internal flooding event?
SI-C-437 | Austria | SI | 03.1 - Fire prevention |  | 123 |  |  |  | As mentioned on page 123 "the plant weakness was partially mitigated with the implementation of the fire protection action plan modifications, which removed plant weaknesses with the highest risk impact, while other weaknesses were compensated with appropriate administrative procedures." While an extensive list was presented on the fire protection action plan modifications, please provide additional information on the "appropriate administrative procedures", their implementation and the supervision of those procedures.
SI-C-438 | Austria | SI | 03.1 - Fire prevention |  | 123 |  |  |  | Please elaborate why there are no weaknesses in fire prevention, while the report mentions that plant weaknesses were partially mitigated with modifications and administrative procedures.
SI-C-439 | Austria | SI | 03.3 - Passive fire protection |  | 138 |  |  |  | In section 3.3.1.3 Performance Assurance Through Lifetime an overview on the different items for surveilance is provided. Please add some information on findings and subconsequent actions based on those.
SI-C-440 | Czech Republic | SI | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
SI-C-441 | Czech Republic | SI | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
SI-C-442 | Czech Republic | SI | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
SI-C-443 | Czech Republic | SI | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
SI-C-444 | Germany | SI | 03.2 - Active fire protection |  | 8 |  |  |  | Could Slovenia please provide justification for excluding TRIGA in Ljubljana from the TPR II. It is not clear that the Slovenian research reactor is much different from other TRIGAs in the EU (of each, nearly all participate in the TPR II). Excluding the Slovenian research reactor from the TPR II and from the experiences exchange on fire protection is even more regrettable, because of its experiences with the fire event in 2010.
SI-C-445 | Poland | SI | 01-General information |  | 114 |  |  |  | On the page 114 we can read that "Rules are prescribed that define acceptable micro location for transient loads (e.g. no loads in ex-zones, no loads in cable rooms, no loads in waste storage rooms, combustible loads shall be reduced to a minimum)." Considering the examples provided, it would seem that the term "micro location" refers to the rooms, rather than the position of materials inside said rooms. Could you explain how the term was used?
SI-C-446 | Poland | SI | 03.4 - Licensee's experience |  | 133 |  |  |  | On the page 133 we can read that "Krško NPP has a contract with the local fire brigade PGE Krško. Beside the two professional firefighters from the local fire brigade that are present on-site 24/7, additional three professional firefighters are available 24 hours per day at the local fire brigade (2 km from the plant) and have a response time of less than 10 minutes. Additional 10 professional firefighters are available on-call with a response time of 30 minutes and additional 20 firefighters within 60 minutes." Can Slovenia provide more details regarding communication between Krško NPP and firefighting units in the area? Particularly, is there a direct line of connection established for the sole purpose of notifying firefighters in case of an event.
ES-C-447 | Czech Republic | ES | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
ES-C-448 | Czech Republic | ES | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
ES-C-449 | Czech Republic | ES | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
ES-C-450 | Czech Republic | ES | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
ES-C-451 | Poland | ES | 03.1 - Fire prevention |  | 98 |  |  |  | Vandellós NPP: Do control room cabinets for train A and train B cables are on the same fire zone within the control room or in the separate zones?
ES-C-452 | Poland | ES | 03.1 - Fire prevention |  | 94 |  |  |  | Almaraz NPP and Cofrentes NPP: It is not clearly stated if those NPPs are not using halogenated plastics at all. If the halogenated plastics are being used for cables then were they tested like in Vandellós NPP?
ES-C-453 | Poland | ES | 02- Fire safety analyses |  | 74 |  |  |  | "The Fire Risk Analysis is revised to incorporate the fire-resistant separation wall between the main and standby transformers..." Have you performed analysis for all redundant equipments if they are in different fire zones? Is there any resundant equipment in the same fire zone left?
ES-C-454 | Poland | ES | 03.2 - Active fire protection |  | 174 |  |  |  | Has external public fire brigade been equipped with safety equpment specific for NPPs like dosimeter?
SE-C-455 | Czech Republic | SE | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
SE-C-456 | Czech Republic | SE | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
SE-C-457 | Czech Republic | SE | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
SE-C-458 | Czech Republic | SE | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
SE-C-459 | Germany | SE | 02- Fire safety analyses |  | 57 |  |  |  | Could Sweden explain does the Westinghouse fuel factory share operational feedback and information only in the Westinghouse group or do they inform also other institutions outside Westinghouse, so that they can learn from the experience in the fuel factory?
SE-C-460 | Finland | SE | 03.2 - Active fire protection |  | 82 |  |  |  | What are the alternative provisions, when fire suppression systems are unavailable?
SE-C-461 | Finland | SE | 03.2 - Active fire protection |  | 82 |  |  |  | What are the requirements for on-site fire brigade staffing per shift and response time?
SE-C-462 | Poland | SE | 01-General information |  | 11 |  |  |  | When do you expect the new regulations to be fully applied to the assessments of all the facilities?
SE-C-463 | Poland | SE | 03.1 - Fire prevention |  | 71 |  |  |  | How often trainings related to fire protection (except the annual fire drill) are performed?
CH-C-464 | Austria | CH | 01-General information |  | 14 |  |  |  | Throughout the document, the soon to be published guideline ENSI-G18 is mentioned. Could you please give a short overview of topics covered by ENSI-G18? What is the current publication-status of ENSI-G18? Which improvements concerning fire protection does ENSI expect to see by the publication of ENSI-G18? Does ENSI expect any difficulties for licensees in regards to the implementation of the new guideline ENSI-G18?
CH-C-465 | Austria | CH | 02- Fire safety analyses |  | 29 |  |  |  | Could you please provide the implementation-status of the potential for improvement identified by ENSI in the review of the last PSR with regard to the probabilistic fire analysis? In the NAR it is mentioned that it would be implemented by the end of 2023.
CH-C-466 | Austria | CH | 02- Fire safety analyses |  | 51 |  |  |  | It is mentioned that since PSR2010 six incidents have occured involving fire protection equipment without any additional measures that were derived from these incidents. Could you plese provide a rationale for not implementing additional measures?
CH-C-467 | Austria | CH | 02- Fire safety analyses |  | 51 |  |  |  | Could you please provide furthter information on the false alarm incident in 2019? How long did it take for the staff to recognize that it was a false alarm? What are the mentioned improvements?
CH-C-468 | Austria | CH | 03.1 - Fire prevention |  | 66 |  |  |  | Please elaborate on why no fire protection inspections have taken place at the Zwilag/ZWIBEZ/Interim Storage facility Gösgen for quite some time?
CH-C-469 | Austria | CH | 03.2 - Active fire protection |  | 73 |  |  |  | It is stated that in case of emergency there are additional pipes that can be installed in order to draw water from the Aare River. How time-consuming is the installation? Is the installation part of emergency exercises?
CH-C-470 | Austria | CH | 03.2 - Active fire protection |  | 81 |  |  |  | The section 3.2.2.4 (Alternative/temporary provisions) is assessed by the operator as not relevant. How did the operator come to this assessment? What is the regulators opinion on this assessment?
CH-C-471 | Austria | CH | 03.3 - Passive fire protection |  | 95 |  |  |  | It is stated that components that do not have a fire protection qualification according to national or international standards are assessed according to their construction method. Could you please provide further information about the assessment process for those components? How many/Which of the components do not have official national/international fire protection qualification?
CH-C-472 | Austria | CH | 03.5 - Regulator's assessment |  | 111 |  |  |  | Are there any preliminary results that can be shared regarding the fire protection concept of the KKL facility?
CH-C-473 | Austria | CH | 01-General information |  | 118 |  |  |  | Since the Mühleberg NPP went under decommissioning rather recently, are there any specific experiences/challenges etc. in relation to fire safety/protection that ENSI or the licensee could share that could improve Nuclear Safety of NPPs under decommissioning at other sites?
CH-C-474 | Belgium | CH | 03.2 - Active fire protection |  | 67 |  |  |  | It is mentioned that some fire detectors are subordinate to a halon extinguishing control centre in Beznau. Aren't the other NPPs not protected with halon systems? Why is the approach different between the different NPPs?
CH-C-475 | Belgium | CH | 03.2 - Active fire protection |  | 68 |  |  |  | For both Gosgen and Leibstadt, it is mentioned that some rooms are not under fire monitoring due to high radiation exposure. Would it be possible to provide further reasoning for excluding fire monitoring in such rooms. Do these room also contain important source terms? Would it be possible to precise the number of rooms concerned and whether this concerns rooms with fire loads and with high source terms?
CH-C-476 | Belgium | CH | 03.2 - Active fire protection |  | 92 |  |  |  | Concerning the NPP in decommissioning (Muhleberg), the chapter on Active Fire Protection seems to describe a fully functional active fire protection for a NPP. However, after the full description of the system, the report mentions on p88 that the the fire protection measures are continuously evaluated and adapted due to the evolution of the environmental conditions during the course of decommissioning. That seems good but does not appear to be described in the report, as no examples have been found of such adaptations. Only ENSI, p92, when giving its assessment, mentions: "no long-term need for permanently installed extinguishing systems". Would it be possible to elaborate on the adaptations already performed and those foreseen to the installation in decommissioning and to elaborate on the technical critera used by the licensee and approved by ENSI for triggering the possibility of amending the fire protection system? Is it based on an evolution of the source term, a specific step in the process of decommissioning or ... ?
CH-C-477 | Belgium | CH | 03.2 - Active fire protection |  | 85 |  |  |  | It is mentioned that the fire brigade in Leibstad (and maybe also for Gosgen but this is not clear in the text, while nothing is said for Beznau) can participate in the fire protection system of the neighbourhood and can assist municipalities in case of fire. How is it ensured that enough firefighters are at all times available for quick response to fire events on the nuclear site if they can be called for external emergency?
CH-C-478 | Belgium | CH | 03.2 - Active fire protection |  | 84 |  |  |  | It is often not clear in the text whether the internal fire brigade is composed of full-time dedicated professional firefighters or by employees which act as fire brigad alongside other activities on site. Would it be possible to clarify the status of the members of the internal fire brigades? And also to elaborate on their training and experiences in comparison with the professional external fire brigade? As it is mentioned that real fires are (fortunately) quite rare, how is the lack of experience of the internal fire brigade with real fires managed?
CH-C-479 | Belgium | CH | 02- Fire safety analyses |  | 25 |  |  |  | "In an additional analysis, interactions between the two units were examined. It was shown that the degree of redundancy of the plant is additionally increased by the existing crossconnections between the two units and that no relevant negative interactions result from this." Could you further elaborate on the scope and type on interactions between the twin units that were investigated ?
CH-C-480 | Belgium | CH | 03.1 - Fire prevention |  | 72 |  |  |  | KKB: "From ENSI's point of view, a revision and division into an overarching fire protection concept and individual building concepts as well as the creation of comprehensive fire protection plans are therefore necessary (National area for improvement)" What are the main identified opportunities for improvement ?
CH-C-481 | Belgium | CH | 03.2 - Active fire protection |  | 94 |  |  |  | Is there a company fire brigade at KKB in charge of all fire fighting and suppression activities ? Are there provisions to request support from external (public) fire brigade ?
CH-C-482 | Czech Republic | CH | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
CH-C-483 | Czech Republic | CH | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
CH-C-484 | Czech Republic | CH | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
CH-C-485 | Czech Republic | CH | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
CH-C-486 | Germany | CH | 02- Fire safety analyses |  | i |  |  |  | "high level of protection … against internally and seismically triggered fires": What is the level of protection against other externally triggered fires? Could Switzerland explain and include this information?
CH-C-487 | Germany | CH | 02- Fire safety analyses |  | Regarding KKM, pp. 49-52 |  |  |  | More detailed information on the changes in the fire sources (permanent and transient fire loads and ignition sources) is missing.
CH-C-488 | Germany | CH | 02- Fire safety analyses |  | Regarding KKM, pp. 49-52 |  |  |  | Regarding fire frequencies, it is stated that the PSA for KKM is used as basis. Information on the methodology applied and how the adaption is taking place is missing and needed for clarification.
CH-C-489 | Germany | CH | 02- Fire safety analyses |  | Regarding KKM, pp. 49-52 |  |  |  | It is mentioned that combinations of seismic hazards with fires are considered. Clarification how this done and information for not considering other combinations of fires and other hazards are needed.
CH-C-490 | Germany | CH | 02- Fire safety analyses |  | Regarding KKM, p. 51 |  |  |  | Information from other installations on the operating experience from fire events and events with deterioration of fire protection features and their application in the fire safety analyses is missing.
CH-C-491 | Germany | CH | 02- Fire safety analyses |  | Regarding KKB, KKG and KKL, pp. 31-32: |  |  |  | For all 3 NPPs, it is stated that there were no "relevant" fire events observed. However, there probably have been small incipient fires, which are not assessed as relevant by the licensee. Please provide information on the relevance criteria.
CH-C-492 | Germany | CH | 02- Fire safety analyses |  | Regarding KKB, KKG and KKL, pp. 31-32: |  |  |  | It is not mentioned for KKB that operating experience from events affecting fire protections features (e.g. fire dampers) has been considered. Respective information should be provided.
CH-C-493 | Germany | CH | 02- Fire safety analyses |  | Regarding KKB, KKG and KKL, pp. 31-32: |  |  |  | For all 3 NPPs it is not stated if and how the operating experience with fires or fire protection features has been addressed/considered in the fire safety analyses.
CH-C-494 | Germany | CH | 02- Fire safety analyses |  | Regarding KKB, KKG and KKL, pp. 31-32: |  |  |  | For KKG one short circuit event is mentioned. A few more details on this event would be useful
CH-C-495 | Germany | CH | 02- Fire safety analyses |  | Regarding KKB, KKG and KKL, pp. 15-38: |  |  |  | For all 3 NPPs it is stated that the event combination seismic hazard and fire is considered in the analyses. However, other possible combinations are not mentioned. Are they excluded, and what is the justification?
CH-C-496 | Germany | CH | 02- Fire safety analyses |  | Regarding KKB, KKG and KKL, pp. 32-38: |  |  |  | The regulator has identified areas for improvements: However, some more details on the basis for this assessment and the resulting recommendations would be useful.
CH-C-497 | Germany | CH | 02- Fire safety analyses |  | Regarding KKB, KKG and KKL |  |  |  | What are the criteria for considering event combinations of fires and other hazards in the safety analyses?
CH-C-498 | Germany | CH | 02- Fire safety analyses |  | Regarding Zwilag, p. 40 |  |  |  | The NAR states on p. 40: "The immobile fire load in the storage areas of the buildings amounts to approx. 24 MJ/m², which is significantly less than 90 MJ/m²." How is the value of 90 MJ/m2 justified? Does it consider higher local fire loads?
CH-C-499 | Germany | CH | 03.1 - Fire prevention |  | Regarding KKG, p. 64 |  |  |  | p. 64: "In addition, the following precautionary measures take effect in the KKG in order to be able to either completely exclude fire events or at least limit them: - ... - In areas where there are proximities between redundancies in the reactor building (e.g. superimposed cable routes), independently responding sprinkler systems prevent unacceptable cross-redundancy failures from occurring." It seems that an active measure is taken to protect e.g. cables from redundant trains. What kind of passive measures are used?
CH-C-500 | Germany | CH | 03.3 - Passive fire protection |  | Regarding KKB, KKG and KKL |  |  |  | More information on the fire safety provisions for hot work is needed for clarity.
CH-C-501 | Germany | CH | 03.3 - Passive fire protection |  | Regarding KKG and KKL |  |  |  | More information on the minimisation (and control), e.g. of the following ignition sources: reactive chemicals, explosive atmospheres (ATEX), high energy arcing fault (HEAF) electrical sources, hot work, human failures, should be provided.
CH-C-502 | Germany | CH | 03.3 - Passive fire protection |  | Regarding all installations, p. 22 and p. 96 |  |  |  | It seems that the use of the terms "fire zones" and fire compartment" is different: p. 22: "In the course of detailed fire modelling, selected fire compartments are divided into fire zones and the fire impacts are analysed. …" On p. 96 is explained that components at the fire zone boundaries have a higher fire resistance than components at the fire compartment boundaries. Could you please explain? The term "fire cell" is not used in the NAR. It is commonly used when rated components partly could not be used for the boundaries.
CH-C-503 | Poland | CH | 03.1 - Fire prevention |  | 94 |  |  |  | Are all installed cables halogen-free?
CH-C-504 | Poland | CH | 02- Fire safety analyses |  | 21 |  |  |  | You refer to the development of an extensive list of ignition sources as a result of seismic shocks. What parameters do you take into account when estimating the possibility of fire?
CH-C-505 | Poland | CH | 03.2 - Active fire protection |  | 41 |  |  |  | Are the operators trained in the use of additional firefighting equipment and if so, how often?
CH-C-506 | Poland | CH | 03.4 - Licensee's experience |  | 83 |  |  |  | Are the operators trained in the procedures in accordance with the operator's cooperation agreement with the fire brigade in the field of fire management?
TR-C-507 | Germany | TR | 01-General information |  | 4 |  |  |  | The NAR for ENSREG TPRII mentions that the research reactor ITU TRIGA can be pulsed up to a peak power of about 1000 MW. In its National Report on the Convention on Nuclear Safety Türkiye states, that this reactor can be pulsed up to 1200 MW. Could Türkiye please clarify this discrepancy?
TR-C-508 | Germany | TR | 01-General information |  | 4 - 8 |  |  |  | Could Türkiye please specify how the newly issued regulation "Fire Protection of Nuclear Facilities" stated the requirements related to fire safety?
TR-C-509 | Germany | TR | 01-General information |  | 5 |  |  |  | According to the report a decision on decommissioning of the research reactor TR2 is on the table. Could Türkiye please give an update on this decision, i.e. when will the decommissioning of TR2 start?
TR-C-510 | Germany | TR | 01-General information |  | 6 |  |  |  | Could Türkiye please provide the Figure 1 presenting the connected buildings of Akkuyu NPP that is mentioned on page 6?
TR-C-511 | Germany | TR | 01-General information |  | 7 |  |  |  | The report states that guidelines related to fire safety will be prepared and put into force. Could Türkiye please specify the planned timeline?
TR-C-512 | Germany | TR | 02- Fire safety analyses |  | 11 |  |  |  | Regarding the Fire Safety Analysis for Akkuyu NPP could Türkiye please specify the plans for periodic review, i.e. in which timeframes the Fire Safety Analysis will take place?
TR-C-513 | Germany | TR | 02- Fire safety analyses |  | 14 |  |  |  | Could Türkiye please estimate at which time ITU will have prepared a fire protection program and submit it to NDK?
TR-C-514 | Germany | TR | 03.2 - Active fire protection |  | 24 - 26 |  |  |  | Could Türkiye specify the number of individuals attending the Akkuyu NPP Fire Safety Department, Fire Brigade Unit, and Fire Safety Unit? What is planned to train these persons?
TR-C-515 | Germany | TR | 03.2 - Active fire protection |  | 24-26 |  |  |  | Is it planned for Akkuyu NPP to get support by a fire brigade located nearby? What is planned to have a communication between the onsite fire safety department/Fire Brigade Unit/ Fire Safety Unit with an external fire brigade which might be informed in case if support is needed? How long would it take if such an external fire birgade might be available on site of Akkuyu NPP in order to support in case of a fire?
TR-C-516 | Germany | TR | 03.2 - Active fire protection |  | 26 |  |  |  | Could Türkiye please clarify the abbreviation SPSD?
TR-C-517 | Germany | TR | 03.2 - Active fire protection |  | 27 |  |  |  | Could Türkiye explain how long does it take until an external fire brigade of the Istanbul Metropolitan Municipality, trained for intervention ant ITU TRIGA, will be available at the research reactor in case of fire? How is entrance of external support ensured?
TR-C-518 | Poland | TR | 03.2 - Active fire protection |  | 19 |  |  |  | Is the scope of the annual training between the fire brigade and the operator developed?
TR-C-519 | Poland | TR | 03.2 - Active fire protection |  | 23 |  |  |  | How are automatic gas fire extinguishing units tested for proper operation?
UK-C-520 | Belgium | UK | 02- Fire safety analyses |  | 40 |  |  |  | "Sizewell B: consequential hazards were considered as part of the overall deterministic assessment and design, including fires and flooding caused by seismic events." How were the correlated (i.e. consequential) seismic and fire hazards considered in the deterministic risk analysis ?
UK-C-521 | Belgium | UK | 03.1 - Fire prevention |  | 139-141 |  |  |  | "EDF NGL reports that storage of combustible items is risk assessed by the location Fire Safety Co-ordinator, considering existing risks and control measures and noting any restrictions or control measures to be applied. It also reports that checks are made of the laydown areas during plant walkdowns ensuring all laydown areas are compliant with these measures." and "EDF NGL tracks fire safety metrics for fire safety system health across all sites. The metrics track defects relating to detection, suppression, fire barriers, fire doors, fire dampers etc. to identify at a glance whether the stations are meeting the requirements to maintain safe systems under fire safety." Are there metrics (or indicators) associated with the respect of the rules associated with fire prevention measures, including storage of combustible materials, or other insight related to the fire safety awareness of the plant personnel ?
UK-C-522 | Belgium | UK | 02- Fire safety analyses |  | 58 |  |  |  | "SZB’s fire PSA is based on the station deterministic fire safety case and does not follow modern industry guidance (e.g., NUREG-6850 [36]). Report Section I2.1.1.10 states under Sizewell B: The deterministic fire assessment and the PSA fire assessment have been considered in the three PSRs carried out to date. EDF-NGL states that no significant changes have been considered necessary." Has a benchmarking (or pilot) exercise been carried-out in order to evaluate the impact of updating the Fire PSA model according to NUREG/CR-6850, similarly to what has been performed with HPB for AGRs ?
UK-C-523 | Belgium | UK | 02- Fire safety analyses |  | 58 |  |  |  | About Fire PSA: "SZB’s PSR3 is expected to be submitted to ONR in early 2024. ONR will assess the PSR at that point and it is therefore premature to make a judgement at the time of writing this report." Are there any sign that the conclusion should significantly differ from the previous PSRs ? Is it already possible to say more about the progress of this project and its evaluation by ONR?
UK-C-524 | Belgium | UK | 03.2 - Active fire protection |  | 180 |  |  |  | "SZB - The fire alarms do not actuate the fire protection in the safety classified areas – these use frangible bulbs. However, the fire alarm system closes fire dampers to contain the spread of smoke and actuates the overpressure systems for the stairwells and fire escape routes." Does the rupture of a bulb immediately actuate the fire suprpession ? or is another action required (e.g. pre-actuation and pressure arming by the detection system, or order validation in the MCR) ? If not: how is the risk associated to the untimely rupture of a bulb considered in the safety-classified areas ? Can the fire alarm close fire dampers in ventilation ducts associated with safety-classified systems ?
UK-C-525 | Czech Republic | UK | 01-General information | [5 empty] | Is there legal framework for classifying fire equipment into nuclear safety related classes and a methodology for determining whether or not a fire system has an effect on nuclear safety?
UK-C-526 | Czech Republic | UK | 02- Fire safety analyses | [5 empty] | If not legally required, is such a safety classification of fire equipment performed by NPP as a result of analysis or for the purpose of ageing management?
UK-C-527 | Czech Republic | UK | 03.1 - Fire prevention | [5 empty] | How and at what intervals are realized inspections/revisions of fire safety equipment installed in sections/cells inaccessible during the Unit power operation?
UK-C-528 | Czech Republic | UK | 01-General information | [5 empty] | How is investigated the causes of fires in NPPs and which organization determines the official cause of the fire (NPP commander or FB inspectorate)?
UK-C-529 | Germany | UK | 03.2 - Active fire protection |  | 192 |  |  |  | section "Safety Culture - Emergency Response (Fire): Could UK clearify how the fire drills are associated with safety culture. Is there an explaination for this connection?
UK-C-530 | Poland | UK | 02- Fire safety analyses |  | 33 |  |  |  | Is quality of operator training estimated and taken into accound in the analysis?
UK-C-531 | Poland | UK | 03.2 - Active fire protection |  | 177 |  |  |  | Is the number of false alarms monitored? If so, what results from such statistics - e.g. comparing results from different units, detecting any trends, etc.?
UK-C-532 | Poland | UK | 03.2 - Active fire protection |  | 177 |  |  |  | Are external fire brigade members equipped with equpment specific for nuclear installations - eg. dosimeters?

## Stakeholders
Question ID | Reviewer (Country authorities; organisation name, etc) | Country/NAR | Fire Protection Thematic (AFP, PFP, FSA - for experts' questions) | Chapter and relevant section of TS | Page no. in NAR (if specified) | Installation type (NPP, RR, SFS…) | Installation name | Question - installation specific (experts' questions) | Question - General (including generic/general experts' questions for type of installation) | Country's response | Cross reference to to another question-reply (Question ID) | Any remarks
AT-S-1 | Hungarian Atomic Energy Authority | AT |  | 01- General information | 10 |  |  |  | Are there specific requirements/is it the part of the Austrian national practice to carry out on-site inspections which focuses on fire safety provisions? If so which authority is responsible for these activities or is it an inter-regulator activity? What is the regularity of these activities?
AT-S-2 | Hungarian Atomic Energy Authority | AT |  | 02- Fire safety analyses | 26 |  |  |  | Could you specify which regulator reviews and approves the fire risk analysis, which carries out related on-site inspections, etc.? Could you specify the roles of the various regulatory institutions in the supervision of the fire risk analysis and corresponding actions?
AT-S-3 | Hungarian Atomic Energy Authority | AT |  | 02- Fire safety analyses | 20 |  |  |  | 1., Could you specify what are the scenarios considered in the fire risk analysis (e.g.: Fire in the control room, fire in the corridors, etc.)? 2., Are the different operational states taken into consideration in the safety/fire risk assessment? 3., Are the results of the fire risk assessment taken into consideration during the development/update of the internal Fire Protection Regulations and procedures? 4., Are there requirements on how often the fire risk assessment and correspondingly the internal Fire Protection Regulation have to be updated?
AT-S-4 | Hungarian Atomic Energy Authority | AT |  | 02- Fire safety analyses | 19 |  |  |  | Could you specify what is meant by “For the risk assessment, the burning of storage material, room inventory or technical equipment was considered depending on the use of the room; model calculations going beyond that were not carried out.”?
AT-S-5 | Hungarian Atomic Energy Authority | AT |  | 02- Fire safety analyses | 19 |  |  |  | 1., Could you specify what is meant by: “the collapse of the hall will not generate enough energy to cause the worst-case scenario described above.”? 2., Is mechanical fuel damage, due to the collapsing structure falling into the core, taken into consideration in the assessment? 3., Is the effects of fire (e.g.: highly energetic upward lift due to the hot air escaping from the facility carrying radioactive particles from the damaged core) taken into consideration in the effected range and dose calculations?
AT-S-6 | Hungarian Atomic Energy Authority | AT |  | 03.1 - Fire prevention | 30 |  |  |  | Does the assigned fire station to the reactor carry out periodic fire safety exercises at the site (e.g.: complex situation exercise)? Are there regulations and/or practices on the periodicity for the visits done by the assigned fire station personal?
AT-S-7 | Hungarian Atomic Energy Authority | AT |  | 03.1 - Fire prevention | 28 |  |  |  | Could you provide details on the tasks the fire safety officers and fire safety wardens are responsible for? For example: 1., Who carries out daily walkdowns? Were there cases when the responsible person detected irregularities? If so, how such irregularities are reported, documented and then resolved? 2., Are there comprehensive fire safety walkdowns (e.g.: targeted fire safety inspection done annually)? If so, could you provide examples on the findings that were made during these walkdowns? 3., Who is responsible for monitoring and control of flammable/combustible material transport in and out of the facility (e.g.: packaging materials, furniture, papers used to take notes, etc.)? How does this responsibility manifests in practice (e.g.: are there forms on which transported materials are logged)?
AT-S-8 | Hungarian Atomic Energy Authority | AT |  | 03.2 - Active fire protection | 34 |  |  |  | Does members of the Vienna Professional Fire Brigade receive special training to extinguish fires in areas with potential radioactive contamination? (Not just the reactor hall itself, but also for example in the laboratories containing radioactive materials)
AT-S-9 | Hungarian Atomic Energy Authority | AT |  | 03.3 - Passive fire protection | 39 |  |  |  | Based on the provided descriptions both the walls, the ceilings as well as the fire dampers have 90 minutes fire resistant classification, but the doors themselves have a 30 minutes classification. What is the time frame for fire spreading taken into consideration in the related assessments (e.g.: 30 minutes or 90 minutes)?
BE-S-10 | Jensen Hughes Belgium | BE |  | 01- General information | 11/112 |  |  |  | CNT3 was selected as installation, and KCD4 not, both went in LTO. Why?
BE-S-11 | Jensen Hughes Belgium | BE |  | 01- General information | 11/112 |  |  |  | Waste storage facilities were excluded because of the low radiological risk. What does this mean Radiation is an ignition source?
BE-S-12 | Jensen Hughes Belgium | BE |  | 05 - Other | 106 & 107/112 |  |  |  | The old standard NBN713.020 is mentionned, is this standard still in use and not replaced by its European equivalent?
BE-S-13 | Jensen Hughes Belgium | BE |  | 05 - Other | 0 |  |  |  | How do you cope with the difference in regulations between the Flemish an Walloon region regarding i.e. the fire water retention in case of fire and sprinkling or deluge is used.
BE-S-14 | Jensen Hughes Belgium | BE |  | 05 - Other | 106 & 107/112 |  |  |  | Sometimes the edition (year) is indicated and sometimes not, What is the reason to do so? Does it have an impact on the SER?
BG-S-15 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2 | 20 |  |  |  | -Is an aircraft crash included in the external events considered for all nuclear facilities in Bulgaria?
BG-S-16 | Generali | BG |  | 01- General information; 02- Fire safety analyses; 03.1 - Fire prevention; 03.2 - Active fire protection; 03.3 - Passive fire protection | NA |  |  |  | I haven' t question, thank you
BG-S-17 | Insurance company | BG |  | 02- Fire safety analyses; 03.1 - Fire prevention; 03.2 - Active fire protection; 03.3 - Passive fire protection | 10,75,23,65, 95 |  |  |  | No questions, thank you!
BG-S-18 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 1.1.4 | 9 |  |  |  | Are the current valid WENRA Safety Reference Levels for a) Existing Reactors, for b) Existing Research Reactors, for c) Waste and Spent Fuel Storage and for d) Decommissioning Safety included in the national regulations? And are they already applied in the safety assessment of all nuclear facilities, if not, when will they be applied?
BG-S-19 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2.1 | 20 |  |  |  | -Are beyond-design-basis fires possible? What would be the radiological consequences, if any?
BG-S-20 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2.1.1 | 20 |  |  |  | Kozloduy 5 and 6: “The analyses carried out in the FHA take into account the possible external events that can lead to fire and its spread…. This includes both natural external events such as extreme weather conditions and human-induced events depending on the possible potential fire risks associated with the facility or activity.” ../· -Does it take in account an aircraft crash which can lead to a fire? If yes, what assumptions are made for this aircraft crash with regard to the type of aircraft, the fire temperature and the duration of the fire? -What are the radiological results of this analysis? If no, why not?
BG-S-21 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2.1.3 | 27.29 |  |  |  | “An update of the existing PSA level 1 in case of fire was carried out in 2020-2022. …4.54E-07 1/y for unit 5, 4.49E-07 1/y for unit 6. The total core damage frequency during operation of each of the units is determined as follows: 8.14E-7 1/y for unit 5; 8.03E-7 1/y for unit 6.” · “The analysis of the results shows that, for both units, the contribution of the internal initiating events constitutes about 60% of the total frequency. Internal fire risk accounts for 10% of the total core damage frequency per unit, with turbine hall fires being the dominant factor.” · -What contribution is made by fire events to the frequency of beyond design-basis accidents or accidents involving the release of radioactive substances?
BG-S-22 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2.1.6.2 | 37 |  |  |  | How many and which kind of events/failures per year of the fire protection equipment have been occurred?
BG-S-23 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2.1.7 | 38 |  |  |  | in the Czech Republic, in accordance with the requirements of the SÚJB, a basic set of operational safety indicators is defined, including: · -Unit availability factor · - Fuel reliability · - Number of INES events · - Number and severity of failure events · - Unplanned loss of power factor · - Containment tightness · - Number of fires in the NPP area · ….” · -Are there comparable indicators defined in Bulgaria? And if yes, what are the results and trends of the indicators for the for the Kozloduy 5 and 6?
BG-S-24 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2.2 | 41 |  |  |  | Are beyond-design-basis fires possible? What would be the radiological consequences, if any?
BG-S-25 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2.2.6 | 50 |  |  |  | How many and which kind of events/failures per year of the fire protection equipment have been occurred?
BG-S-26 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2.4.1 | 42 |  |  |  | PSFSF ”From an inspection of the insurance risk of "Kozloduy NPP" EAD in 2023, a Report on the study of nuclear insurance pools for "Civil liability for nuclear damage" insurance was received, in which a recommendation was made to revise the fire hazard analysis of PSFSF. The implementation of this recommendation is planned until 2025.” · -Could you explain why they ask for the revision of the fire hazard analysis?
BG-S-27 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2.5 | 43 |  |  |  | What is the amount of flammable waste at the SFCRAW? What is the result of a beyond design accident of this facility?
BG-S-28 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 2.6 | 45 |  |  |  | What is the amount of flammable waste at Kozloduy 1-4? What is the result of a beyond design accident of this facility?
BG-S-29 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.1 | 48 |  |  |  | A typical cause of internal fires in NPPs is a short circuit in an electrical component or due to ageing cable insulation. Have fires already occurred due to this cause? How are fires from this cause prevented?
BG-S-30 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.1.1 | 49 |  |  |  | -Which redundant safety system equipment and components are not located in separate fire sections?
BG-S-31 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.1.3 | 52 |  |  |  | Experience feedback Nuclear Power Plants: · -What experiences have been made since the start of operation, when and where have fires occurred and what was the cause in each case?
BG-S-32 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.1.3.2 | 53 |  |  |  | Have all recommendations and suggestions from the last OSART (2012/2014) mission been fully implemented? How many recommendations have been given?
BG-S-33 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.1.3.2 | 53 |  |  |  | “In connection with a registered defect of a pipeline from an automatic fire extinguishing system of the safety systems and a conducted analysis, decisions were made to replace the pipelines with corrosion-resistant austenitic steel. The developed design is in the process of implementation. In this regard, a long-term schedule for operational control (thickness measurement) of the pipelines has been developed.” · -Have more defective areas been discovered on the pipelines during follow-up inspections due to the registered defect? Have all pipelines of fire extinguishing systems in the NPP been replaced with corrosion-resistant austenitic steel pipelines?
BG-S-34 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.2.1 | 70 |  |  |  | Are the fire extinguishing systems of all nuclear facilities considered here designed to withstand earthquakes?
BG-S-35 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.3.1 | 93 |  |  |  | Do the power cables in all buildings relevant to nuclear safety have an increased resistance to the spread of fire (e.g. in accordance with IEC 332.3 Category A or IEC 331 or higher)? · Do the special cables (optical cables, coaxial cables), which could not be manufactured in such a way that they fulfil the test according to IEC 332.3 category A to ensure their functionality, have an unsheathing with steel tubes?
BG-S-36 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.3.2.1. | 100 |  |  |  | “MCR / ECR have a common air conditioning system.” · -Is there any plan to divide the air condition systems?
BG-S-37 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.4 | 104 |  |  |  | -How many incidents/failures of fire detection and alarm components, fire extinguishing systems, fire barriers and ventilation systems have occurred in the considered nuclear facilities to date? --Can trends be observed over the last decades?
BG-S-38 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.4 | 111 |  |  |  | “The scope of the aging management process also includes the components of fire extinguishing systems, fire alarm systems and fire dampers.” · -How long has the ageing management process been in place for the components of fire extinguishing systems, fire alarm systems and fire dampers? What are the results, how many ageing effects have occurred in these components? Are there any trends to be observed?
BG-S-39 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 3.6 | 113 |  |  |  | “The results of the inspections are reported in protocols and provided to the licensees. In case of established non-conformities with the existing requirements, the licensee must take actions to eliminate them in a timely manner.” · -What time frame does "timely manner" mean in this context?
BG-S-40 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 4.1 | 117 |  |  |  | "Activities that have not been fully completed at the time of the current peer review are the pending FHA updates (regarding PSFSF) commented on in the national report and the ongoing replacement of equipment associated with the obsolete equipment replacement programme (e.g. the replacement of detectors for the AlgoRex CS1140 modular fire detection system)." · Has the fire hazard analysis of the PSFSF been completed? Does this result in retrofitting measures? If so, which measures and by when must they be completed? Has the replacement of the outdated fire protection equipment in Kosloduy 5 and 6 been completed?
BG-S-41 | Joint Project - Nuclear Risk & Public Control (AT) | BG |  | 4.3 | 118 |  |  |  | Is the safety culture evaluated with regard to fire protection in nuclear facilities? If so, how is this assessed in the respective facilities?
CZ-S-42 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2 | 20 |  |  |  | “The assessment presented in the Operational Safety Analysis Report includes a set of postulated initiating events, which take into account the nature of the event, the type of occurrence and the frequency of the event occurrence. Initiating events include internal and external fire events.” -Is an aircraft crash included in the external events considered for all nuclear facilities in the Czech Republic?
CZ-S-43 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 4 | 126 |  |  |  | Is the safety culture evaluated with regard to fire protection in nuclear facilities? If so, how is this assessed in the respective facilities?
CZ-S-44 | HAEA (Hungarian Atomic Energy Authority) | CZ |  | 01- General information | Page 8. |  |  |  | How are the commonly shared resources (e.g., onsite fire brigade, common drills, etc.) shared between the installations?
CZ-S-45 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 01- General information | 1 |  |  |  | The "Joint Project - Nuclear Risk & Public Control" submitted today a long list of questions for CZ, HU, BG and PL via the survey support form. Sorry but it was not possible to put our questions in your form. I kindly ask you to verify that you received our list and will consider it in the consultation. Thank you!
CZ-S-46 | HAEA (Hungarian Atomic Energy Authority) | CZ |  | 02- Fire safety analyses | Page: 36 |  |  |  | 2.2.3. Fire phenomena analyses: overview of models, data and consequences Question: How are the on-site or off-site fire departments/brigades taken into account in the fire safety analysis.
CZ-S-47 | HAEA (Hungarian Atomic Energy Authority) | CZ |  | 02- Fire safety analyses | Page: 32 |  |  |  | 2.1.B.5. Periodic review and management of changes Question: What regulation/regulations set the requirements for Fire PSA and Deterministic Fire Hazard Analysis?
CZ-S-48 | HAEA (Hungarian Atomic Energy Authority) | CZ |  | 02- Fire safety analyses | Page: 31 |  |  |  | 2.1.B.4 Main results / dominant events (licensee´s experience) Question: Were there major fire events at the Dukovany NPP that was taken into consideration in modifications (engineering or administrative) and/or had an effect on the fire safety assessment?
CZ-S-49 | HAEA (Hungarian Atomic Energy Authority) | CZ |  | 02- Fire safety analyses | Page: 30 |  |  |  | 2.1.B.3. Fire phenomena analyses: overview of models, data and consequences Acc. WENRA SV 6.2: “The extent of reliance on on-site or off-site fire brigades shall be shown to be adequate in the fire hazard analysis.” Question: How are the on-site or off-site fire departments/brigades taken into account in the fire safety analysis?
CZ-S-50 | HAEA (Hungarian Atomic Energy Authority) | CZ |  | 02- Fire safety analyses | Page: 26 |  |  |  | 2.1.A.5. Periodic review and management of changes Question: What regulation/regulations set the requirements for Fire PSA and Deterministic Fire Hazard Analysis?
CZ-S-51 | HAEA (Hungarian Atomic Energy Authority) | CZ |  | 02- Fire safety analyses | Page: 25 |  |  |  | 2.1.A.4 Main results / dominant events (licensee´s experience) Question: Were there fire events at the Temelin NPP that was taken into consideration in modifications (engineering or administrative) and/or had an effect on the fire safety assessment?
CZ-S-52 | HAEA (Hungarian Atomic Energy Authority) | CZ |  | 02- Fire safety analyses | Page: 25 |  |  |  | Acc. WENRA SV 6.2: “The extent of reliance on on-site or off-site fire brigades shall be shown to be adequate in the fire hazard analysis.” Question: How are the on-site or off-site fire departments/brigades taken into account in the fire safety analysis?
CZ-S-53 | Hungarian Atomic Energy Authority | CZ |  | 03.1 - Fire prevention | 57 |  |  |  | Are there internal regulations at the LVR-15 facility to limit and control the transport of combustible and flammable materials and substances into the facility? Are these activities and the amount logged, checked, etc.?
CZ-S-54 | Hungarian Atomic Energy Authority | CZ |  | 03.2 - Active fire protection | 106 |  |  |  | Are there regulations in force for the LVR-15 facility that require specific temporary measures to be taken for example during occasional flammable activities or work involving dust/smoke generation? If so, how are these requirements met?
CZ-S-55 | Hungarian Atomic Energy Authority | CZ |  | 03.3 - Passive fire protection | 124 |  |  |  | Could you provide details on the fire sectioning and applied passive fire protection solutions (e.g.: fire retardant coating on cables)?
CZ-S-56 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 1.1.2 | 9 |  |  |  | “From the candidate nuclear installations, the SÚJB selected those with the potential for significant radiological risks to the environment and the population caused or affected by fire, to enable a meaningful comparison of the level of fire protection provision and the feasibility and quality of the assessment.” -Why was the newer SFS Temelin selected for the assessment and not the older SFS Dukovany?
CZ-S-57 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 1.1.3 | 12 |  |  |  | “The LVR-15 is a tank-type light water research reactor housed in a non-pressurized stainless steel vessel under a shielding lid with forced cooling. The reactor uses IRT-4M type fuel with 19.7% 235U enrichment and an operating thermal power of up to 10 MW.” -What beyond-design-basis accidents are possible for this reactor? It should be taken into account that it uses fuel with relatively high enrichment and therefore the radiological consequences could be comparatively high.
CZ-S-58 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 1.2.2 | 16 |  |  |  | Are the current valid WENRA Safety Reference Levels for a) Existing Reactors, for b) Existing Research Reactors, for c) Waste and Spent Fuel Storage and for d) Decommissioning Safety included in the national regulations? And are they already applied in the safety assessment of all nuclear facilities, if not, when will they be applied?
CZ-S-59 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 1.2.2 | 17 |  |  |  | “Internal feedback system provides inspectors involved in inspections by information of operational events and the results of their investigations in their area of expertise. In addition to the inspection of the actual feedback process, inspectors review the progress and analysis of the checked events. “ -What are the main results of these inspections?
CZ-S-60 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 1.2.3 | 19 |  |  |  | “The scope of the state fire supervision enforcement: ….Identifying the causes of fires.” -What are the main causes of fire events?
CZ-S-61 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2.1 | 20 |  |  |  | Are beyond-design-basis fires for the NPPs possible? What would be the radiological consequences, if any?
CZ-S-62 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2.1.7.1 | 34 |  |  |  | “In accordance with the requirements of the SÚJB, a basic set of operational safety indicators is defined, including: -Unit availability factor - Fuel reliability - Number of INES events - Number and severity of failure events - Unplanned loss of power factor - Containment tightness - Number of fires in the NPP area ….” -Since when are these indicators determined? What are the results and trends of the indicators for the 6 reactors in the Czech Republic?
CZ-S-63 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2.1.A.3 | 25 |  |  |  | “The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 13.6% level.” -What are the CDF results for Temelin 1 and 2 according to the latest PSA? What is the date of the most recent calculation? What contribution is made by fire events to the frequency of beyond design-basis accidents or accidents involving the release of radioactive substances?
CZ-S-64 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2.1.A.4 | 25 |  |  |  | How many and which kind of events/failures per year of the fire protection equipment have been occurred?
CZ-S-65 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2.1.A.4 | 26 |  |  |  | “A. The measures to eliminate the most dangerous fire scenario in the area of sufficient forces and resources compared to the guaranteed 1st level of fire alarm for the given area confirms the necessity to establish the Fire Rescue Service Unit in the Temelín NPP (FRSU). B. The minimum member of this unit shall not be less than 12 personnel per shift continuously ready to respond to an emergency.” -This requirement applies to Temelin, is there a comparable requirement for Dukovany?
CZ-S-66 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2.1.B.3 | 30 |  |  |  | Dukovany NPP: “The contributions of internal fires to the overall risk of unit operation are generally of little importance. The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 20.3% level.” -What are the current CDF results for the 4 units of the Dukovany NPP? -When was the last PSA carried out? -What contribution is made by fire events to the frequency of beyond design-basis accidents or accidents involving the release of radioactive substances?
CZ-S-67 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2.1.B.4 | 31 |  |  |  | How many and which kind of events/failures per year of the fire protection equipment have occurred?
CZ-S-68 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2.2 | 36 |  |  |  | Are beyond-design-basis fires possible? What would be the radiological consequences, if any?
CZ-S-69 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2.2.6.2 | 40 |  |  |  | LVR-15: “The last documented fire was in the reactor hall in the cable line, which was extinguished without limiting the operability of safety-significant equipment and the affected portion of the cable line was repaired.”. -What was the reason for the last fire mentioned and when did it happen? How many fires have occurred since the start of operations?
CZ-S-70 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 2.4 | 40/41 |  |  |  | “The analysis of a deliberate attack by a large transport aircraft on a SFS falls into the category of extended design conditions and meets the requirements of a realistic approach. Application of a conservative approach in the form of "largest existing aircraft" is not required. The analyses performed indicate that the mechanical effects of the accident are not of such magnitude as to cause the spent fuel package leakage.” -What assumptions are made for this aircraft crash with regard to the type of aircraft, the fire temperature and the duration of the fire? What are the radiological results of this analysis? -Can radiological effects due to the thermal effects of the fire be completely ruled out? -Are the results for both SFS facilities in Dukovany the same?
CZ-S-71 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.1 | 44 |  |  |  | -What experiences have been made since the start of operation, when and where have fires occurred and what was the cause in each case?
CZ-S-72 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.1.A | 44 |  |  |  | A typical cause of internal fires in NPPs is a short circuit in an electrical component or due to ageing cable insulation. Have fires already occurred due to this cause? How are fires from this cause prevented?
CZ-S-73 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.1.A.3.2. | 47 |  |  |  | -Have all recommendations and suggestions from the last OSART mission been fully implemented for Temelin? How many recommendations have been given?
CZ-S-74 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.1.B | 48 |  |  |  | A typical cause of internal fires in NPPs is a short circuit in an electrical component or due to ageing cable insulation. Have fires already occurred due to this cause? How are fires from this cause prevented?
CZ-S-75 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.1.B | 49 |  |  |  | Dukovany “When it is not possible to locate redundant equipment and components of safety systems or safety-related systems in separate fire sections (containment, control room, emergency control room, cable space under control room, etc.), fire protection systems shall be designed to limit the spread of fire in these fire sections and to eliminate unacceptable effects of fire or the fire protection systems themselves on the redundant safety systems.” -Which redundant safety system equipment and components are not located in separate fire sections?
CZ-S-76 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.1.B.2 | 50 |  |  |  | Dukovany: “In all nuclear safety-relevant buildings, power cables and most low-current cables are of a design with increased resistance to the spread of fire, complying with IEC 332.3 category A, or IEC 331. c) In the case of special cables (optic cables, coaxial cables) which could not be manufactured to meet the test according to IEC 332.3 category A in order to ensure their functionality, their resistance to the spread of fire is ensured by covering their entire length in steel tubes.” -Which low-current cables are not of a design with increased resistance to the spread of fire, complying with IEC 332.3 category A, or IEC 331?
CZ-S-77 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.1.B.3.2 | 51 |  |  |  | Have all recommendations and suggestions from the last OSART mission been fully implemented for Dukovany? How many recommendations have been given?
CZ-S-78 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.2.A.2 | 65 |  |  |  | Are the fire extinguishing systems of Temelin designed to withstand earthquakes?
CZ-S-79 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.2.B.2 | 89 |  |  |  | Are the fire extinguishing systems of Dukovany designed to withstand earthquakes?
CZ-S-80 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.2.C.2 | 106 |  |  |  | Are the fire extinguishing systems designed to withstand earthquakes?
CZ-S-81 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.2.D.2 | 111 |  |  |  | Are the fire extinguishing systems designed to withstand earthquakes?
CZ-S-82 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.4 | 124 |  |  |  | Are the components of fire extinguishing systems, fire alarm systems and fire dampers in the aging management program included? If yes, since when? What are the results, how many ageing effects have occurred in these components? Are there any trends to be observed?
CZ-S-83 | Joint Project - Nuclear Risk & Public Control (AT) | CZ |  | 3.4 | 124 |  |  |  | How many incidents/failures of fire detection and alarm components, fire extinguishing systems, fire barriers and ventilation systems have occurred in the different nuclear facilities to date? Can trends be observed over the last two decades?
FI-S-84 | LT regulator | FI |  | 02- Fire safety analyses | page 26, B 2.1.6.2 |  |  |  | Were there any significant fire related events and lessons learned that led to improvements in equipment and/or practices?
FR-S-85 | Comité National de Protection contre les Rayonnements Ionisants (CNPRI) | FR |  | 03.5 - Regulator's assessment | 2 |  |  |  | What can be done to improve staff skills without having the necessary tools (detection devices)?
FR-S-86 | Comité National de protection contre les rayonnements ionisants | FR |  | 03.5 - Regulator's assessment | 10 |  |  |  | Permettez moi de faire partie
DE-S-87 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | DE |  | 01- General information | 8 |  |  |  | In Point 1.1.2.6 of the NAR “Installations under decommissioning” it is stated that “According to the Technical Specification for the TPR II /WEN 22/, installations under decommissioning with a considerable radiological risk due to fire are to be considered in particular. In Germany, these are particularly those installations that are not yet free of fuel elements. These are already covered by the selection made in paragraphs 1.1.2.1 and 1.1.2.2.” Furthermore in point 1.1.2.1 it is stated “As soon as fuel elements are no more present, the radiological risk from fire is no longer significant so that these installations don’t have to be further considered in this national report in line with the requirements of the TS /WEN 22/. Nevertheless, further details are given in various sections of this report.”Could Germany further elaborate on the rationale for not having explicitly included in the NAR the fire safety assessment for NPPs already defueled and under decommissioning?
HU-S-88 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2 | 30 |  |  |  | -Is an aircraft crash included in the external events considered for all nuclear facilities in Hungary?
HU-S-89 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 1.1.3 | 9 |  |  |  | BKR “Year of operational license expiring date: 15.12.2023” -Has the operating licence for the BKR been extended?
HU-S-90 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 1.3.1 | 13 |  |  |  | Experience feedback Nuclear Power Plants: -What experiences have been made since the start of operation, when and where have fires occurred and what was the cause in each case?
HU-S-91 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 1.3.4 | 21 |  |  |  | KKÁT: “Considered factors leading to occurrence of external fires:….. · During air traffic, fire event originated from aircraft crash onto the KKAT.” -What assumptions are made for this aircraft crash with regard to the type of aircraft, the fire temperature and the duration of the fire? -What are the radiological results of this analysis?
HU-S-92 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 1.4.1 | 23 |  |  |  | NPP: “A set of technical and administrative measures have been taken to prevent fires. It is a specific requirement, for example, that when furniture in the process-related rooms is being replaced, only pieces of furniture made of certified "flame retardant" materials may be purchased.” -What has been done so far? What percentage of furniture has already been replaced at Dukovany and Temelin?
HU-S-93 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 1.4.2 | 24 |  |  |  | BKR: “new requirement that is being introduced is that only superstructures or furniture made of ‘non-combustible’ materials may be procured when replacing installed equipment or furniture in the reactor hall;” -What has been done so far? What percentage of furniture has already been replaced at the BKR? Which equipment has to be replaced? What percentage of the equipment is already replaced?
HU-S-94 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.1 | 30 |  |  |  | Are beyond-design-basis fires possible? What would be the radiological consequences, if any?
HU-S-95 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.1.3 | 37/38 |  |  |  | “According to the calculation results, the expected value of the CDF resulting from fires that can be assumed to occur during power operation of the units at their rated capacity is: · for Unit 1: 2.30E-06/year, · for Unit 2: 1.93E-06/year, · for Unit 3: 3.01E-06/year, · for Unit 4: 4.71E-06/year.” -What are the current CDF results for the 4 units? -When was the last PSA carried out? -What contribution is made by fire events to the frequency of beyond design-basis accidents or accidents involving the release of radioactive substances?
HU-S-96 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.1.3 | 38 |  |  |  | “The differences between the results obtained for different units can be explained by differences in the spatial arrangement of system components, in particular by differences in cabling.” -Was it considered to change the spatial arrangement of the system components, in particular the different cabling in unit 4, in order to achieve a comparable and by a factor of 2.5 lower calculated probability than in unit 2?
HU-S-97 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.1.4 | 38 |  |  |  | “No major fire ever occurred in the Paks Nuclear Power Plant.” How many other fire events have been occurred?
HU-S-98 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.1.6.2 | 41 |  |  |  | How many and which kind of events/failures per year of the fire protection equipment have been occurred?
HU-S-99 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.1.7 | 41 |  |  |  | in the Czech Republic, in accordance with the requirements of the SÚJB, a basic set of operational safety indicators is defined, including: -Unit availability factor - Fuel reliability - Number of INES events - Number and severity of failure events - Unplanned loss of power factor - Containment tightness - Number of fires in the NPP area ….” -Are there comparable indicators defined in Hungary? And if yes, what are the results and trends of the indicators for the for Paks 1-4 ?
HU-S-100 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.2 | 44 |  |  |  | Are beyond-design-basis fires possible? What would be the radiological consequences, if any?
HU-S-101 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.2.2 | 45 |  |  |  | BKR: “The simultaneous occurrence of several independent fires and the combined effects are excluded from the assessment. However, the effects on the nuclear safety of the reactor induced by a particular fire are investigated.“ -Which kind of event combinations are considered in the FHA?
HU-S-102 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.2.6.2 | 51 |  |  |  | BKR: “However regardless of lack of severe fire cases it is necessary to improve the Safety Culture due to the complexity of the site and the staff.” -What measures have already been implemented and what measures are planned to improve the safety culture?
HU-S-103 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.2.7.1 | 52 |  |  |  | BKR: “Identified weaknesses can be considered as the following: · The responsibilities and authorities in the facility are underdeveloped and in many cases conflicting. …. This results in a situation when it is unclear who should remove unnecessary flammable materials, potential sources of fire, etc. · An additional weakness that was identified during the site visit is the lack of personnel specifically focusing on the changes in laws and regulations, which would ensure that both the fire risk analyses and the internal Fire Protection Regulation is kept up to date.” -When and how are these weaknesses solved or when and how they will be solved ?
HU-S-104 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.2.7.3 | 52 |  |  |  | BKR: “Conclusions drawn on the adequacy of the licensee’s fire safety analyses../The fire safety analysis itself was reviewed and was found partly satisfactory. The new version of the analysis has not yet been officially submitted, but is under internal review at the Licensee. The preliminary review of the new “not-yet-submitted” version of the document was found to be adequate based on the limited amount of time and access to the document, but final conclusions can only be drawn once the new version is submitted to the co-authorities.” -When the fire safety analysis has to be provided?
HU-S-105 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.4.3 | 57 |  |  |  | KKAT: “Except for cables located in switchboards and on cable trays, the technological system installed in the facility contains limited quantities of combustible material.” -What is the fire load of these cables?
HU-S-106 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 2.8 | 62 |  |  |  | “Regarding the fire risk assessment of the BME OR training reactor facility the issue of the lack of submitted and approved fire risk assessment is persistent, therefore in-depth regulatory review or evaluation of assessment cannot be carried out at this point, hence no regulatory conclusions can be drawn.” -When will this situation be over or when will fire risk assessment be provided and assessed? Has the supervisory authority considered suspending operations until that time?
HU-S-107 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.1 | 63 |  |  |  | A typical cause of internal fires in NPPs is a short circuit in an electrical component or due to ageing cable insulation. Have fires already occurred due to this cause? How are fires from this cause prevented?
HU-S-108 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.1.1 | 64 |  |  |  | -Which redundant safety system equipment and components are not located in separate fire sections?
HU-S-109 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.1.2.1 | 67 |  |  |  | NPP “The standard fire load parameters are constant values, but they may vary in cases where new cables are being installed or old cables are being removed. If an equipment is being replaced with one which contains more combustible materials, the fire load parameter changes are tracked the same way. In such cases the fire load changes are included in the design documentation for the planned modifications.” -Have cables or equipment been deliberately replaced in order to significantly reduce the fire load?
HU-S-110 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.1.3.2.1 | 71 |  |  |  | Have all recommendations and suggestions from the last OSART mission been fully implemented? How many recommendations have been given?
HU-S-111 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.1.3.3 | 72 |  |  |  | “The PAE’s operational life time has been extended by 20 years with the condition to carry out a comprehensive PSR after 10 year of extended operation. As of today further life time extension possibilities are under investigation. Consequently the subject of implementation is not actual.” -What is specifically meant by the last statement?
HU-S-112 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.2.2 | 85 |  |  |  | Are the fire extinguishing systems of all nuclear facilities considered here designed to withstand earthquakes?
HU-S-113 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.3.1 | 100 |  |  |  | Do the power cables in all buildings relevant to nuclear safety have an increased resistance to the spread of fire (e.g. in accordance with IEC 332.3 Category A or IEC 331 or higher)? Do the special cables (optical cables, coaxial cables), which could not be manufactured in such a way that they fulfil the test according to IEC 332.3 category A to ensure their functionality, have an unsheathing with steel tubes?
HU-S-114 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.3.1.2.1. | 106 |  |  |  | “Fire cells have been designed and implemented where cables from one safety system have been routed through a room belonging to another safety system in a fire-retardant manner as required.” -The cables of which safety systems pass through a room of another safety system.
HU-S-115 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.4 | 114 |  |  |  | How many incidents/failures of fire detection and alarm components, fire extinguishing systems, fire barriers and ventilation systems have occurred in the considered nuclear facilities to date? Can trends be observed over the last two decades?
HU-S-116 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.4 | 114 |  |  |  | Are the components of fire extinguishing systems, fire alarm systems and fire dampers in the aging management program included? If yes, since when? What are the results, how many ageing effects have occurred in these components? Are there any trends to be observed?
HU-S-117 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 3.5 | 116 |  |  |  | Is the safety culture evaluated with regard to fire protection in nuclear facilities? If so, how is this assessed in the respective facilities?
HU-S-118 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 4.1.2 | 119 |  |  |  | “In the case of research reactors it was identified both by the Licensees and the regulators that there is a persisting issue regarding the staffing of these facilities which pose a continuous obstacle on carrying out scheduled tasks on time. The issue arises from the size of the nuclear expert community and strict requirements on the qualifications of these experts, which significantly limits the number of available experts.” -How did the supervisory authority react to this situation? Has the supervisory authority considered suspending operations?
HU-S-119 | Joint Project - Nuclear Risk & Public Control (AT) | HU |  | 4.2 | 124 |  |  |  | “In general it was concluded that in the case of nuclear power plants the Hungarian regulations are practically fully in line with the WENRA RLs (although in some cases in a different structure).In the case of research reactors and interim spent fuel storages however several gaps were identified in the Hungarian regulations during and even prior the TPR II as part of a regulatory self-assessment.” -When will be the current valid WENRA Safety Reference Levels for the Existing Research Reactors and interim spent fuel storages included in the national regulations? And when do they have to be used in safety assessments?
IT-S-120 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | IT |  | 01- General information | 7 |  |  |  | In the table of “candidate” and “selected” installations the rationale for an installation to be “candidate” and “selected” is not given. For instance, one of the two BWR (Caorso or Garigliano), given their different technology, could be “selected” in addition to the “graphite” Latina and PWR Trino.
IT-S-121 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | IT |  | 01- General information | 8 |  |  |  | The table of “Key parameters per installation” reports relevant data only for “candidate” installations. For completeness and in regard of similarity, it could be advisable to report the corresponding data also for “represented” installations.
IT-S-122 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | IT |  | 03.3 - Passive fire protection; 03.4 - Licensee's experience | 91 |  |  |  | On the basis of what considerations is it considered adequate, from the point of view of fire extinguishing in the ESSOR ADECO spent fuel storage, the operation of the ventilation systems in the extraction function, during a fire event in the premises, even in presence of automatic HALON gas extinguishing systems? Is still the use of HALON allowed?
IT-S-123 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | IT |  | 03.4 - Licensee's experience | 91 |  |  |  | On the basis of what considerations is it considered adequate, from the point of view of fire extinguishing in the ESSOR ADECO spent fuel storage, the operation of the ventilation systems in the extraction function, during a fire event in the premises, even in presence of automatic HALON gas extinguishing systems? Is still the use of HALON allowed?
IT-S-124 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | IT |  | 03.4 - Licensee's experience | 87 |  |  |  | For older generation installations, for which it is expected to adopt different storage solutions for spent fuel or radioactive liquids, including flammable ones, in a relatively short time, could you clarify whether a maximum “waiting time” without carrying out safety improvements has been defined? The question applies to: ITREC - presence of disused (B.II.2.1.3) or in disagreement with the norms on electrical cables (B.II.3.1.2 pg. 93), ITREC, ESSOR B pool, AVOGADRO- lack of fire dampers (B.3.5 pg. 27), EUREX area 800 (C.V.3.3.2.1 pg. 151).
IT-S-125 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | IT |  | 03.4 - Licensee's experience | 86 |  |  |  | Have been acceptable timescales defined for the TAPIRO reactor and the AVOGADRO pool, to re-evaluate/improve the fire detection systems (A.3.1.4 pg. 25 – B.3.5 pg. 26) or, only for the TAPIRO reactor, where it is required to organize the staff training and to improve the procedures (3.6 pg. 31). Is the current status considered acceptable and on which bases?
IT-S-126 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | IT |  | 03.4 - Licensee's experience; 03.5 - Regulator's assessment | 135 |  |  |  | During phase 1 (C.III.1.4 pg. 32) of the EUREX D2 repository, ignition and consequent fire spread are more probable than during the subsequent phases and it is pursued the “minimization of the possibility that the fire can start, grow, and spread rapidly by adequate disposition of contaminated combustible materials, equipment and, where possible, by separating the causes of fire from flammable materials” (C.III.3.1.1.). In any case “a manual activation with 24 hours’ surveillance has been adopted” (C.III.2.1.6.2. pg, 134) by “intervention of the control room operator” (C.III.3.2.2.1 pg. 137). The question is whether during phase 1, where it is not possible to separate ignition sources from flammable material, some additional fire protection provisions and quicker interventions are programmed.
IT-S-127 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | IT |  | 03.4 - Licensee's experience; 03.5 - Regulator's assessment | 156 |  |  |  | There is a truncated sentence “The fire extinguishing system is a gaseous suppression type and use, as an extinguishing agent.” (C.VI.3.2.2.1.). Furthermore, the decision to make the activation of gas extinguishing systems manual in the 0PEC 2 also in areas at greatest risk does not seem entirely justified by the experience of spurious interventions in the past and reduces the success probability. (C.VI.2.1.6.2 pg. 154).
IT-S-128 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | IT |  | 03.4 - Licensee's experience; 03.5 - Regulator's assessment | 25 |  |  |  | Have been acceptable timescales defined for the TAPIRO reactor and the AVOGADRO pool, to re-evaluate/improve the fire detection systems (A.3.1.4 pg. 25 – B.3.5 pg. 26) or, only for the TAPIRO reactor, where it is required to organize the staff training and to improve the procedures (3.6 pg. 31). Is the current status considered acceptable and on which bases?
IT-S-129 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | IT |  | 03.5 - Regulator's assessment | 163 |  |  |  | For Latina decommissioning, could you elaborate in more detail about the unit of measurement and the methodology adopted to obtain “residual risk” in the presented table (par. D.I.2.1.3.) and if “fire loads” and corresponding “REI classification” in the same table are considered everywhere adequate? Could you also provide information on the schedule for “updating the fire detection systems of the plant” (par. D.I.2.1.4. pg. 164).
PL-S-130 | Joint Project - Nuclear Risk & Public Control (AT) | PL |  | 1.2 | 16 |  |  |  | Are the current valid WENRA Safety Reference Levels for Research Reactors included in the national regulations? And are they already applied in the safety assessment, if not, when will they be applied?
PL-S-131 | Joint Project - Nuclear Risk & Public Control (AT) | PL |  | 3.1 | 23 |  |  |  | -How many incidents/failures of fire detection and alarm components, fire extinguishing systems, fire barriers and ventilation systems have occurred in the considered nuclear facilities to date? --Can trends be observed over the last decades?
PL-S-132 | Joint Project - Nuclear Risk & Public Control (AT) | PL |  | 3.1 | 23 |  |  |  | Are the components of fire extinguishing systems, fire alarm systems and fire dampers in the ageing management program included? If yes, since when? What are the results, how many ageing effects have occurred in these components? Are there any trends to be observed?
PL-S-133 | Joint Project - Nuclear Risk & Public Control (AT) | PL |  | 3.1.3 | 24 |  |  |  | A typical cause of internal fires is a short circuit in an electrical component or due to ageing cable insulation. Have fires already occurred due to this cause? How are fires from this cause prevented?
PL-S-134 | Joint Project - Nuclear Risk & Public Control (AT) | PL |  | 3.5 | 40/41 |  |  |  | “The most important weaknesses of active fire protection were also identified: • lack of automatic extinguishing systems wherever there is a risk of fire that could threaten critical infrastructure for nuclear safety and radiological protection, and at the same time, the possible operation of automatic extinguishing systems would not affect the safety functions of SSCs (Structures, Systems, and Components), • the system of automatic fire detectors is unable to report the location of the fire, • lack of internal specialized fire brigade unit.” When will these major weaknesses be resolved?
PL-S-135 | Joint Project - Nuclear Risk & Public Control (AT) | PL |  | 3.5 | 41 |  |  |  | “The most important weakness of passive fire protection was also identified: • the construction building and reactor installations were designed using old standards and technical solutions. Some improvements are possible but they need modernization efforts.” Are these modernisation efforts being made? If so, when?
SI-S-136 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | SI |  | 01- General information | 136 |  |  |  | The definitions for fire area, zone or cell or reference standard should be specified. (par. 3.3.1. 1. Par. 3.1.2 pag. 114 - par. 2.5.10.1. pag. 112).
SI-S-137 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | SI |  | 01- General information | 8 |  |  |  | The exclusion of TRIGA Mark II research reactor (RR) from TPR because of low radiological risk should be better justified considering its location in Ljubljana in connection to the power level and to the past history of the plant fire system, as it is reported that relevant interventions have been undertaken following the 2010 fire event.
SI-S-138 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | SI |  | 02- Fire safety analyses | 3 APPENDIX |  |  |  | Table showing the most recent evolution in fire areas highlights that, in some areas, relevant safe shutdown functions are ensured by “alternative systems/equipment” or through “manual actions or operation changes”, which presumably require complex operators’ actions for supervision, systems alignment, local actions. It could be useful to clarify that success paths in those cases are characterized by acceptable success probabilities. In fact, “following several reviews/international missions, “Krško NPP introduced various plant changes, purchased additional mobile equipment .., enabling additional equipment to be connected to the existing Krško NPP’s systems .. and introduced different strategy for accidents mitigation” (par. 1.1.1.1 pg. 6). “Fire response procedure for the fire in those areas were comprehensive to give instructions to establish all safety functions mostly by a number of manual actions including some special system configuration” (par. 2.1.6.1. pg. 89).
SI-S-139 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | SI |  | 03.2 - Active fire protection | 46 |  |  |  | Since “Krško NPP Fire Protection System is not seismically qualified” (par. 2.1.2.5.2), limited success probabilities appear to characterize the manual interventions for possible fires following earthquakes due to the number of actions to be performed in those circumstances.
SI-S-140 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | SI |  | 03.2 - Active fire protection | 46 |  |  |  | Since “Krško NPP Fire Protection System is not seismically qualified” (par. 2.1.2.5.2), limited success probabilities appear to characterize the manual interventions for possible fires following earthquakes due to the number of actions to be performed in those circumstances.
SI-S-141 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | SI |  | 03.2 - Active fire protection | 124 |  |  |  | In the report there are some apparently contradictory statements, which do not allow to form a clear picture of the present situation. Examples on systems automation, are given below. “The area smoke, heat or flame detectors only perform a fire alarm function and they don't, by themselves, actuate any automatic fire extinguishing systems”. (par. 3.2.1.2) – “Fire detectors used to actuate fire suppression systems represent a more critically important component of a plant's Fire Protection Program than detectors that are installed solely for early fire warning and notification. Consequently, the minimum number of operable fire detectors must be greater for “activating” detectors”. (par. 3.2.1.3 pg. 126) – “Fire suppression is achieved by a combination of manual firefighting and automatic/semi-automatic fire extinguishing systems, that protect equipment, systems or areas as defined in FHA”. (par. 4.3. pg. 148).
SI-S-142 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | SI |  | 03.3 - Passive fire protection | 136 |  |  |  | The definitions for fire area, zone or cell or reference standard should be specified. (par. 3.3.1. 1. Par. 3.1.2 pag. 114 - par. 2.5.10.1. pag. 112).
CH-S-143 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | CH |  | 01- General information | II. |  |  |  | Reference is made to the fulfillment of WENRA SRL SV 6.2 which is not reported in the WENRA TS. It might be reported that WENRA SRL SV 6.2 relates to requirements on on-site or off-site fire brigades related to fire hazard analysis.
CH-S-144 | COMMISSION ON NPPs MANAGEMENT - ORDER OF ENGINEERS, ROME | CH |  | 02- Fire safety analyses | Pg. 44 |  |  |  | In ZWILAG building S “measures” have been taken that lead to estimated (by the licensee) low releases and to the tolerability of the lack of smoke and heat extraction system and extinguishing systems (2.4.4). In building H no fire detection and alarm systems were required and alternative/temporary provisions were “assessed as not relevant by the operator” (page 81). The current acceptability of such situations would require to be discussed in more detail.
CH-S-145 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS, ROME | CH |  | 03.1 - Fire prevention | 64 |  |  |  | Even for ZWILAG buildings K and V, several reasons are exposed for which ENSI “believes that a corresponding review of the fire protection concept is necessary” (3.1.4.1). The main bases for the actual adequacy of such present situation could be made explicit.
CH-S-146 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | CH |  | 03.2 - Active fire protection | 68 |  |  |  | In Goesgen and in Leibnstadt (3.2.1.1.) and, in general (4.3 pg. 118), fire detectors in “rooms with a high radiation load are excluded”, only manual buttons are installed at the entrance to escape and rescue routes. Could you clarify the reason and substantiate the alternative adequacy?
CH-S-147 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | CH |  | 03.2 - Active fire protection | 71 |  |  |  | It would be useful the provisions of analyses and arguments to better clarify acceptability of the situation in MULEBERG, where “connected peripherals such as manual and smoke detectors or room indicators etc. are electrically and seismically unclassified” (3.2.1.2).
CH-S-148 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | CH |  | 03.4 - Licensee's experience; 03.5 - Regulator's assessment | 62 |  |  |  | In several sections, starting from 3.1.4 (see also 3.2.5, 3.3.4, 3.5, 4.1, 4.2, 4.3, 4.4), many so called “national areas for improvements” are identified. No mention is made about possible initiatives in regard to implementation plan of all those improvements.
CH-S-149 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | CH |  | 03.5 - Regulator's assessment | 122 |  |  |  | The general approach and the adequate solutions to the problem of adaptation of new requirements to old installations should be adequately sought (4.4). For Beznau this problem is reported several times also at pages iii, 4,32, 87, referring in particular to the problem of separation of safety systems and stating that in some cases the adaptation is not possible. The specific solutions and their adequacy could be discussed in an available document, also in the perspective of the adoption of ENSI-G18 in 2024 (page 10 and 113).
CH-S-150 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | CH |  | 04 - Overall assessment and general conclusions | 86 |  |  |  | For Beznau and Gosgen, some measures have been adopted for possible fires external to the plant (pg. 29, 100). It might be appropriate to clarify whether systematic studies have been performed for possible fires in the forests bordering the plants.
CH-S-151 | COMMISSION NPPs MANAGEMENT, ORDER OF ENGINEERS ROME | CH |  | 04 - Overall assessment and general conclusions | 114 |  |  |  | A specific area for improvement for Gosgen is related to “the methods for determining fire occurrence frequencies and for handling fire-related short circuits” (4.2). Also this sentence raises the question whether the present defense from fires can be adequately estimated as completely acceptable.
TR-S-152 | HAEA (Hungarian Atomic Energy Authority) | TR |  | 01- General information | missing chapter 1.4 |  |  |  | 1.4. Defence in depth principle and its application missing chapter Question1: How is the defence in depth principle implemented for fire safety in the design phase of the Akkuyu NPP? Could you specifiy the regulations describing the related requirements? Question2: How is the defence in depth principle implemented in fire safety at ITU TRIGA facility? Could you specifiy the regulations describing the related requirements?
TR-S-153 | HAEA (Hungarian Atomic Energy Authority) | TR |  | 01- General information | missing chapter 1.3 |  |  |  | 1.3 Improvements in fire safety as a result of experience feedback missing chapter Questions2: What fire safety improvements have been implemented at the ITU TRIGA?
TR-S-154 | HAEA (Hungarian Atomic Energy Authority) | TR |  | 02- Fire safety analyses | Page: 12 |  |  |  | 2.2.3. Fire phenomena analyses: overview of models, data and consequences Question: How is the off-site fire department taken into account in the fire hazard analysis?
TR-S-155 | HAEA (Hungarian Atomic Energy Authority) | TR |  | 02- Fire safety analyses | Page: 12 |  |  |  | 2.2.2 Key assumptions and methodologies Question: Could you specify the worst-case scenario of the fire hazard analysis ?
TR-S-156 | HAEA (Hungarian Atomic Energy Authority) | TR |  | 02- Fire safety analyses | Page: 11 |  |  |  | 2.1.3. Fire phenomena analyses: overview of models, data and consequences Question: How are the on-site or off-site fire departments taken into account in the fire safety analysis of Akkuyu NPP? Acc. WENRA SV 6.2: “The extent of reliance on on-site or off-site fire brigades shall be shown to be adequate in the fire hazard analysis.”

## TPR team & EC
Question ID | Reviewer (TPR team or EC) | Country/NAR | Fire Protection Thematic (AFP, PFP, FSA - for experts' questions) | Chapter and relevant section of TS | Page no. in NAR (if specified) | Installation type (NPP, RR, SFS…) | Installation name | Question - installation specific (experts' questions) | Question - General (including generic/general experts' questions for type of installation) | Country's response | Cross reference to to another question-reply (Question ID) | Any remarks
AT-T-1 | TPR Team | AT |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
BE-T-2 | TPR Team | BE |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
BG-T-3 | EC | BG |  | 01-General information | N/A |  |  |  | What are the specific applications of the defence-in-depth principles in nuclear installations in Bulgaria?
BG-T-4 | TPR Team | BG |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
BG-T-5 | EC | BG |  | 02- Fire safety analyses | 28+ |  |  |  | What have been the main conclusion/results of the probabilistic and deterministic FHA concerning NPP power or control cable fire? What are the potential common cause failures due to the cable fire?
BG-T-6 | EC | BG |  | 02- Fire safety analyses | 47 |  |  |  | How were hazards of flammable gases and liquids considered in the fire safety analyes of the operating NPP units. What preventive/protective measures have been taken?
BG-T-7 | EC | BG |  | 03.1 - Fire prevention | 52 |  |  |  | Have you made / taken any fire safety improvements / technical measures based on internal/external operating experience?
BG-T-8 | EC | BG |  | 03.1 - Fire prevention | 61 |  |  |  | How is ensured fire resistance of the cables and cable ducts, routes, rooms etc.? How is prevented spreading of fire along power /control cables in cable ducts or rooms?
CZ-T-9 | EC | CZ |  | 01-General information | N/A |  |  |  | What fire safety improvements/measures have you done/taken based on internal/external operating experience, if any?
CZ-T-10 | TPR Team | CZ |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
CZ-T-11 | EC | CZ |  | 03.1 - Fire prevention | 45 |  |  |  | What specific cable design to prevent spreading fire over power and control cables has been used?
FI-T-12 | EC | FI |  | 01-General information | p.18 |  |  |  | It is stated that "After the new WENRA SRLs were published in 2021, a review was done between issue SV and YVL B.8. The SRLs were accounted for in Finnish regulations." As YVL was B.8 was issued in 2019, what is the meaning of 'accounted for'?
FI-T-13 | EC | FI |  | 01-General information | p.18 |  |  |  | It is said that the Finnish nuclear safety regulations are at least as stringent as the existing IAEA requirements". Noting that IAEA safety guides SSG-64 and SSG-77 have been re-issued in 2021 and 2022 respectively, which specific IAEA safety standards and safety guides covering fire protection are being referred to in that statement?
FI-T-14 | TPR Team | FI |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
FI-T-15 | EC | FI |  | 03.2 - Active fire protection | p. 44, 59, 72 |  |  |  | Obsolescence and the ability to obtain qualified replacement and spare parts are primary concerns in the nuclear industry. For the operating NPPs, particularly for OL1,2 and Loviisa 1,2, please explain the policy and implementation experience for obtaining and retaining a supply and replacement of essential spare parts and consumables such as sensors important for all the different types of fire and smoke detection equipment in use. What steps have been taken to ensure availability of replacement sensors/consumables in the expected lifetime of the NPPs?
FI-T-16 | EC | FI |  | 04 - Overall assessment and general conclusions | p.104 |  |  |  | European documents, e.g WENRA SRLs and international safety standards and guides from IAEA cover a broad range of topics in fire protection principally of NPPs, defining the functional requirements in terms of design, and for commissioning and operations phase, under the codes SSR-2/1 and SSR-2/2 respectively. In addition, there are safety guides (e.g. SSG-77 and SSG‑64) which provide recommendations on fire safety in design and safety assessment aspects, design of passive and active protection systems, fire risk analysis, and operational aspects such as fire prevention measures and operational aspects. In the light of operational experience feedback in Finland's NPPs and internationally, what do the licensees and regulatory authority consider as priority aresa for future revisions of the documents/standards and guides? What specific additional topics or issues could warrant consideration in future revisions of these European and international safety standards?
FR-T-17 | TPR Team | FR |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
DE-T-18 | EC | DE |  | 01-General information | 3 to 27 |  |  |  | The NAR provides at the pages an informative report with respect to the requirements.
DE-T-19 | TPR Team | DE |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
DE-T-20 | EC | DE |  | 02- Fire safety analyses | 35 to 37 |  |  |  | Several concrete examples of lessons learned from events and others are reported. This mentioning is to commend on this provision of information.
DE-T-21 | EC | DE |  | 02- Fire safety analyses | Page 38 |  |  |  | 2.1.7.1 "Overview of strengths and weaknesses identified by the regulator". Possible to provide some concrete examples of identified strengths and weaknesses?
DE-T-22 | EC | DE |  | 02- Fire safety analyses | Pages 38,39 |  |  |  | 2.1.7.2 " Lessons learned from inspection and assessment as part of the regulatory oversight". Possible to provide some concrete examples of lessons learned?
DE-T-23 | EC | DE |  | 02- Fire safety analyses | 45 to 48 |  |  |  | 2.2.6.2 "Lessons learned from events, reviews, fire safety related missions, etc." This comment to commend on the concrete examples provided.
HU-T-24 | TPR Team | HU |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
HU-T-25 | EC | HU |  | 02- Fire safety analyses |  |  |  |  | How were hazards of flammable gases and liquids considered in the fire safety analyes of the operating NPP units. What preventive/protective measures have been taken?
HU-T-26 | EC | HU |  | 04 - Overall assessment and general conclusions | 119-126 |  |  |  | How was/will be verified implementation of the corrective actions identified for the research reactors and the SF storage facilities?
IT-T-27 | EC | IT |  | 01-General information | 5 to 18 |  |  |  | At the referred pages, the NAR provides a good overview of the requested information, as Nuclear installation identification, national regulatory framework. With respect to 01.3, Improvements in fire safety as a result of experience feedback and 01.4, Defence in depth principle and its application, they are detailed for each installation in the Annexes. The section 1, General Information, provides adequate structure of the information with respect to the treated subjects.
IT-T-28 | EC | IT |  | 01-General information | 15 |  |  |  | Tne NAR refers at the page to the Ministerial Decree, DM 3 August 2015. which introduced a new engineering approach to fire safety, performance-based fire design. <<The application of the principles of fire safety engineering allows, similarly to other engineering disciplines, to define suitable solutions for achieving design goals by means of quantitative analysis.>> More information about this approach is provided in the page. This comment aims at bringing to the attention this approach as practice resulting from an improved approach.
IT-T-29 | TPR Team | IT |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
IT-T-30 | EC | IT |  | 02- Fire safety analyses | 18 to 24 |  |  |  | The NAR provides at the pages an accurate report on the "Regulator's assessment and conclusions on fire safety analyses with overview of strengths and weaknesses identifies by the regulator for each considered installation. The Lessons Learned from inspection and assessment as part of the regulatory Oversight are also provided, together with the Conclusions drawn on the adequacy of the licensee’s fire safety analyses. To be noted that: particular effort has been made to identify weaknesses and areas for improvement, which denotes that the NAR has been used as opportunity for further improvement. The identification of the weaknesses is in detail supported, for each installation, by the information provided in the Annexes,
IT-T-31 | EC | IT |  | 02- Fire safety analyses | 18 to 20 |  |  |  | Among the reported weaknesses, in several cases of Dedicated Spent Fuel Storage Facilities it is mentioned that the facility is quite old and the fire safety system was designed according to fire hazard analysis based on an older approach. However, information is provided that "A plan is however under implementation to transfer spent fuel".
IT-T-32 | EC | IT |  | 02- Fire safety analyses | page 22 |  |  |  | With respect to the "Waste storage facilities on the sites of nuclear installations", the same comment above applies: "The facilities are however quite old and the fire protection systems are obsolete. A plan to transfer waste into new storage facilities is ongoing".
IT-T-33 | EC | IT |  | 03.1 - Fire prevention | page 27 |  |  |  | To be highlighted as good practice the cooperation between the regulator and the local fire brigade, with beneficial effects on the fire prevention (<<The double check on fire prevention carried out by both the regulator and the local fire brigade led to a continuous re-evaluation of the prevention measures and systematic checks also by the operator with punctual records of all interventions carried out on fire prevention and protection measures>>)
IT-T-34 | EC | IT |  | 03.2 - Active fire protection | page 30 |  |  |  | The NAR commends on the availability of internal firefighting resources and its development. This is positively highlighted <<With regard of administrative and organisational fire protection issues, the firefighting approach is based on the availability of internal firefighting resources, with the important contribution of the local fire brigade command. In this regard, specific training programs and drills are conducted, also to enhance coordination between the personnel of the installation and the external response team, as well as the knowledge of installation and the existing hazards. The specific case of JRC Ispra site, characterized by an internal fire brigade structure, has to be positively highlighted.>>
LT-T-35 | TPR Team | LT |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
NL-T-36 | TPR Team | NL |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
PL-T-37 | EC | PL |  | 01-General information | 10 |  |  |  | The report refers that in the event of a fire in the MARIA RR reactor's "internal services, all services functioning within NCBJ, except for the reactor facility itself, and the entire technical structure of the facility can be utilized" while "if necessary, forces and resources from the Fire Brigade, Police, and other services, both from the Otwock county and the Mazowieckie Voivodeship, will be dispatched" What are the specific criteria for requesting support from the Fire Brigade?
PL-T-38 | EC | PL |  | 01-General information | 17 |  |  |  | Beyond the harmonisation with the EU legislation what other international standards does the licensee apply concerning fire protection?
PL-T-39 | TPR Team | PL |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
PL-T-40 | EC | PL |  | 02- Fire safety analyses | 21 |  |  |  | Area of improvement: What is the frequency of trainings for state and voluntary fire brigades?
PL-T-41 | EC | PL |  | 02- Fire safety analyses | 24 |  |  |  | What qualifications should the employees and external companies possess to carry out non-standard fire-hazardous work? How are these qualifications determined?
PL-T-42 | EC | PL |  | 03.2 - Active fire protection | 32 |  |  |  | How does the operator ensure proper coordination between the plant personnel and the offsite response group in the event of combined action in the RR area?
PL-T-43 | EC | PL |  | 03.2 - Active fire protection | 32 |  |  |  | Does the operator use any particular system for the accreditation of internal staff concerning fire fighting/extinguishing tasks?
PL-T-44 | EC | PL |  | 03.3 - Passive fire protection | 36 |  |  |  | During the refurbishment of the RR, were any improvements made to the by-design features of the building concerning the minimisation of radioactive releases due to fire events?
RO-T-45 | TPR Team | RO |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
RO-T-46 | EC | RO |  | 03.2 - Active fire protection | p.32, 49 |  |  |  | Obsolescence and the ability to obtain qualified replacement and spare parts are primary concerns in the nuclear industry. For the operating NPP Cernavoda 1, 2 and Triga Research reactor, please explain the policy and implementation experience for obtaining and retaining a supply and replacement of essential spare parts and consumables such as sensors important for all the different types of fire and smoke detection equipment in use. What steps have been taken to ensure availability of replacement sensors/consumables in the expected lifetime of the NPPs?
SK-T-47 | TPR Team | SK |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
SK-T-48 | EC | SK |  | 02- Fire safety analyses | 31 |  |  |  | How the fire hazard analysis for the Bohunice 3 and 4 NPP have considered the cable aging aspect for a risk of a cable fire (for example due to a cable insulation failure)
SK-T-49 | EC | SK |  | 03.1 - Fire prevention | 52 |  |  |  | What kind of fire-retarding cables have been used at the Mochovce 3 and 4 plants
SK-T-50 | EC | SK |  | 05 - Other | 130 |  |  |  | Which lessons learned from the fire safety inspection of NPP MO3&4 were/will be transferred to NPP EBO3&4 and MO1&2 plants, if any?
SI-T-51 | EC | SI |  | 01-General information | 16, 89 |  |  |  | The regulatory framework for Krško NPP includes a Regulatory Conformance Program were Krsko has to acomplish with the NRC rules. There is fire areas were Krsko does not comply with Appendix R (10 CFR 50), mainly in distance for redundant train separations.Page 89 of the NAR says "Fire response procedure for the fire in those areas were comprehensive to give instructions to establish all safety functions mostly by a number of manual actions including some special system configuration". Questions: Are these manual actions trained regularly? Are these manual actions implemented in the fire PSA?
SI-T-52 | TPR Team | SI |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
SI-T-53 | EC | SI |  | 04 - Overall assessment and general conclusions | 90 |  |  |  | Krsko NPP uses Fire PSA as an additional tool to the Fire deterministic analysis to increase fire safety. NAR mentions that Safety Upgrade Plan (SUP) was implemented as a consequence of response to Fukushima accident. It also mentioned that "This safety upgrade was very beneficial from the fire risk, as fire in MCR was a dominant sequence. It is still the most important fire sequence, but not over dominant, due to availability of the new Emergency Control Room" , but later is said that SUP is not yet implemented in the Fire PSA, could you please clarify if and how fire risk benefit has been calculated as a consequence of the modification in the Manin Control Room?
ES-T-54 | TPR Team | ES |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
SE-T-55 | TPR Team | SE |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
SE-T-56 | EC | SE |  | 02- Fire safety analyses | 28 |  |  |  | page. 28 "No combined sequences of events, for example fire resulting from an earthquake, have been included in the analysis. This is, however, required according to new regulations and is a future development planned for the safety analysis. " Question: When is planned to have combination of events incorporated to the fire hazard analysis? Would it be also included independent events (or just cause related events as in the case of fire provoqued by earthquake?
CH-T-57 | TPR Team | CH |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
TR-T-58 | TPR Team | TR |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
UA-T-59 | TPR Team | UA |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
UK-T-60 | TPR Team | UK |  | 01-General information | §1.2 |  |  |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)?
UK-T-61 | EC | UK |  | 03.2 - Active fire protection | p.177 et seq |  |  |  | Obsolescence and the ability to obtain qualified replacement and spare parts are primary concerns in the nuclear industry. For the operating NPPs in the UK, please explain the policy and implementation experience for obtaining and retaining a supply and replacement of essential spare parts and consumables such as sensors important for all the different types of fire and smoke detection equipment in use. What steps have been taken to ensure availability of replacement sensors/consumables in the expected lifetime of the NPPs?
UK-T-62 | EC | UK |  | 04 - Overall assessment and general conclusions | p.291-295 |  |  |  | European documents, e.g WENRA SRLs and international safety standards and guides from IAEA cover a broad range of topics for fire protection at NPPs, defining the functional requirements in terms of design, and for commissioning and operations phase, under the codes SSR-2/1 and SSR-2/2 respectively. In addition, there are safety guides (e.g. SSG-77 and SSG‑64) which provide recommendations on fire safety in design and safety assessment aspects, design of passive and active protection systems, fire risk analysis, and operational aspects such as fire prevention measures and operational aspects. In the light of operational experience feedback in UK's NPPs and other types of nuclear installations and internationally, what do the licensees and regulatory authority consider as priority aresa for future revisions of the documents/standards and guides? What specific additional installation types, topics or issues could warrant consideration in future revisions of these European and international safety standards?