## TPR EXPETS
Question ID | Reviewer (TPR experts - AFP, PFP, FSA) | Country/NAR | Fire Protection Thematic (for experts' questions) | Chapter and relevant section of TS (for experts' questions) | Installation type (NPP, RR, SFS…) | Installation name | Question - installation specific (experts' questions) | Question - General (including generic/general experts' questions for type of installation) | Country's response
CZ-E-304 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.1) | NPP | Temelin | Can you please provide information in how far and how the different plant operational states (POSs) are considered in the deterministic fire safety analysis (chapter 2.1.A.1, 2.1.A.2, 2.1.A.3)? |  | The fire is assumed in all plant operational states
CZ-E-305 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.1) | NPP | Temelin | p21 : Firefighting in bituminous areas : How is the risk from bitumen as fire load taken into account? (exothermic chemical reactions? 1997 Tokai Mura fire/explosion feedback?) P22 : Can you please explain what τe and k8 values are? |  | Measures are taken to prevent the occurrence of a fire, and in the event that a fire occurs, the fire is detected immediately (within 60 seconds) and the company's FRSU members arrive within 3 to 4 minutes of its notification. They will be equipped with appropriate fire extinguishers according to the firefighting documentation and can extinguish the fire immediately. Extinguishing is not considered in spaces with limited occupancy, where there are large dose rates - storage of high active radioactive waste. In such the fire burns out before unacceptable damage to building structures could occur (closed spaces without the possibility of fresh air intake). τe = equivalent fire duration in minutes, calculated in accordance to the Czech technical standard (ČSN). k8 = the fire resistance safety factor of the building structure depending on the number of floors and the construction system of the building
CZ-E-306 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.1) | NPP | Dukovany | New deterministic fire safety analysis of all safety significant buildings exist. It remains unclear how the operational states are incorporated in the above mentioned analysis [2.1.B.2.]. |  | The fire is assumed in all plant operational states. In 2022, the FHA actualization was processed, operating conditions are not included here, fire protection must be ensured in all operating states.
CZ-E-307 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.1) | NPP | Dukovany | p31 : The electrical Fire Detectors, where installed, is functional. Does this mean that the 3rd level of defence is not independent of the 2nd? Does this mean that the 3rd level of defence is not sufficient in the absence of detection? |  | The safety level is sufficient. Possible detector malfunction is signaled in control room as the control panel must signal to the operator at least three basic states: OPERATION, FAILURE, FIRE. Described on page 84 of NAR.
CZ-E-308 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience | NPP | Temelin NPP | page 35, section 2.1.7.3 topic 2/ Which the period of periodic inspections on fire protection? Could you provide some identified weakness or non-compliences during the inspection? |  | Fire protection inspections are carried out at regular intervals according to the requirements of the legislation, depending on the inclusion of the building degree of the fire risk. Inspection intervals are once, twice or four times a year, depending on the level of risk. In important objects, inspections are carried out 4 times a year.
CZ-E-309 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience | NPP | Temelin NPP |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified. | E309&311_ANSWER'!A1
CZ-E-310 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience | NPP | Dukovany | page 35, section 2.1.7.3 topic 2/ Which the period of periodic inspections on fire protection? Could you provide some identified weakness or non-compliences during the inspection? |  | Fire protection inspections are carried out at regular intervals according to the requirements of the legislation, depending on the inclusion of the building degree of the fire risk. Inspection intervals are once, twice or four times a year, depending on the level of risk. In important objects, inspections are carried out 4 times a year. In addition to regular annual inspections of the operability of fire safety equipment, the following are carried out on the equipment during operation: 1x per month - activity tests for switchboards and related equipment, 1x every 6 months - tests of the operation of automatic fire detectors and equipment controlled by EFD.
CZ-E-311 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience | NPP | Dukovany |  | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified. | E309&311_ANSWER'!A1
CZ-E-312 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.2) | Research reactor | Research reactor LVR 15 | To 1/ (pp. 36-40): Can you please address the scope of the analyses covering also shutdown states during outages more clearly (and not only implicitly)? |  | The shutdown state means that the rods are in the low end position and possible fire will not affect the change in its position even if the cabling to the drives and power supply is damaged - extraction of the rods is impossible. In case of cooling failure caused by fire during shutdown the followed water reheating and evaporation loss of water do not uncover core at least 3 days. In the event of a fire during the shutdown state, the scenario of a barrel with radioactive waste burning is being considered. This is assessed as not endangering the population.
CZ-E-313 | FSA | CZ | Fire safety analysis | Assumptions (TS 02.2) | Research reactor | Research reactor LVR 15 | To p.36, 1/: Could you specify, if the PSA, especially fire PSA performed for LVR-15? If yes, what are the main contributors (events) and dominant contributes (or sequences for each considered event), and are any measures (except for emergency planning zone issues) identified based on the results? |  | Internal fire scenarios were incorporated into LVR-15 PSA study in 2023. The quantification will be processed in the PSA update in 2024. IE fires are: in primary pump place, DG station, battery room, electrical distribution room, developed fire in control room, reactor hall, ventilation center and external network shutdown caused by fire.
CZ-E-314 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience | Research reactor | Research reactor LVR 15 | To 4/ (p. 40): b) The licensee mentions that the INSARR mission in 2020 revealed the need for fire hazard reduction (disposal of older technologies) and for comprehensive instructions for personnel response (emergency procedures and instructions) also in case of fire. Can you give some information on this? |  | INSARR-type missions always include a tour of the workplace - in the case of the LVR-15 reactor, as part of the tour, it was recommended to remove older (unused) equipment from the technology, not to store material in the technology (e.g. air conditioning filters, etc.) and thereby reduce both the amount of material and, possibly, risk of fire. . The INSARR mission pointed out and recommended a more comprehensive procedure for the operator should be prepared so that the response to the event is easier - that is, the document for the response of personnel was modified, which contains according to event type links to other subdocuments.
CZ-E-315 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience | Research reactor | Research reactor LVR 15 | , p.40, 2/ The information on regulatory oversight, and inspections on fire safety was covered is missing. How often the periodic inspections on fire safety are performed? Is there any significant insight into fire safety from this inspection? |  | In the area of regulatory inspections, an FRS of the Czech Republic inspection of the condition was carried out in 2022 - without negative findings; a five-year plan is typical for such inspections. The company FRSU carries out 2 inspections of the EPS and walk down of the reactor building, and 1 inspection of fire extinguishers and wall-mounted hydrants and dry pipes annually, and inspections of the building are carried out twice a year.
CZ-E-316 | FSA | CZ | Fire safety analysis | Licensee and regulatory experience | Research reactor | Research reactor LVR 15 |  | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified. | 1. All analyses were performed in accordance with Decree 329/2017 Coll. on design requirements. Deterministic analyses showed that no fuel cladding damage occurs for any of the scenarios. 2. a) In the Fire Safety Resolution of the building, the resistance of individual fire section is indicated, which prevent the spread of fires to other fire compartments. In the event of a fire, an operational card is prepared, which contains information relevant to the intervention. The company fire brigade (FRSU) does not have the status of a member of the professional fire brigade units, therefore it is not obliged to intervene in a fire. If the activity of the FRSU is refused, 2. b) As part of the evaluation of a fire as an initiating event, the fire is converted to another initiating event - typically a loss of electrical power (DBA and DEC). It is included in deterministic FHA and in future PSA (end of 2024). 2. c) The LVR-15 reactor does not yet have a fire PSA finished; it is considered as conservative. 2. d) The current data results in neither of the possible scenarios results in a loss of fuel cladding. 2. e) In deterministic analyses, the response of the system to an initialization event is addressed. In deterministic analyses, the failure sequence is not implemented - an order function is considered for safety systems. However consideration is also made as to whether safety critical components/functions satisfy the simple failure criterion - i.e., whether, for example, there is only one measurement sensor that is essential to the event management. The PSA defines the project model in a more comprehensive manner, automatically including in the PSA cuts those which do not meet the "SFC" (if there were any), including more simultaneous failures in higher order cuts. 2. f) The FRSU always departs when an EPS is reported, even in the event of a false alarm.
CZ-E-317 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | NPP | Temelin NPP | page 46/Section 3.1.A.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 46/Section 3.1.A.2/3/ Describe how management and control of hot work is carried out (e.g in case of maintenance, modification...)? page 46/Section 3.1.A.2/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered? |  | In the case of a planned intervention/modification in technology or in the building, this plan is assessed by the FP department, which will determine the fire safety conditions. In the case of temporary storage of fire-hazardous substances, the amount of fire-hazardous substances and the storage location must be approved by the FP department. The FP department further determines the conditions of storage and the marking of areas in which fire-hazardous substances are stored. Before starting work with an open fire, the work implementer must obtain a permit of the FP department, where the FP technician will determine the safety requirements that must be observed during the performance of the activity in place. In the case of work with an open flame in places where there are flammable or fire-hazardous substances, a firefighter is present. In other cases works with open fire are inspected at random. Explosion protection is stipulated by legislation, where so-called explosive zones are defined. On the basis of the provided expert assessment, the areas where the explosive concentration of the so-called Ex zone is possible are determined. ATEX 2014/34/EU, in the Czech legal system the directive has the nature of Government Regulation.
CZ-E-318 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | NPP | Temelin NPP |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications. | The permanent fire load is determined by the nature of the space (office, warehouse, operation, workshop, etc.) and any flammable building structures (e.g. windows, doors, floor) and is based on standards. The temporary fire load is determined by the working activity and its needs (repairs, replacements, etc.). As part of the operation, the permanent fire load is reduced (if there is a replacement of non-flammable equipment, non-flammable windows, doors and floors are installed...), the temporary fire load is subject to the approval of the FP department and is monitored and limited. Permanent fire load is documented in the design, temporary in the database of the FP department. The permanent fire load must not be increased, temporary only up to the limit (approved by the FP department) Any information is in the database of the FP department. Limits for permanent load are given by the design and internal procedure (page 50) temporary load is limited to max 1kgm-2. Fire load checks are part of the preventive inspections of the building, the frequency is determined by the "Fire Risk Assessment", corrective measures are carried out without delay. Hot works are managed by an internal methodology and are subject to approval by the FP department, which checks compliance with measures both during and after the work. Roles and responsibilities are regulated in the permit. Inspections are focused on fire prevention and compliance. Before starting, the FP department evaluates the place of work with an open fire and proposes adequate measures according to the type of work, the place of work and the conditions at the workplace. Subsequently, checks are carried out to ensure compliance with the conditions, and after the work is finished, there is a site security check and checks aimed at preventing the occurrence of fire. Hydrogen is stored in separate building, isolated tubes transport it into generator. For the possibility of hydrogen occurrence in reactor hall there are installed passive autocatalytic recombiners (22 pcs). No major changes or adjustments were made to the hydrogen management.
CZ-E-319 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | NPP | Dukovany | page 50/Section 3.1.B.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 50/Section 3.1.B.2/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered? |  | In the case of a planned intervention/modification in technology or in the building, this plan is assessed by the FP department, which will determine the fire safety conditions. In the case of temporary storage of fire-hazardous substances, the amount of fire-hazardous substances and the storage location must be approved by the FP department. The FP department further determines the conditions of storage and the marking of areas in which fire-hazardous substances are stored. Before starting work with an open fire, the work implementer must obtain a permit of the FP department, where the FP technician will determine the safety requirements that must be observed during the performance of the activity in place. In the case of work with an open flame in places where there are flammable or fire-hazardous substances, a firefighter is present. In other cases works with open fire are inspected at random. Explosion protection is stipulated by legislation, where so-called explosive zones are defined. On the basis of the provided expert assessment, the areas where the explosive concentration of the so-called Ex zone is possible are determined. ATEX 2014/34/EU, in the Czech legal system the directive has the nature of Government Regulation.
CZ-E-320 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | NPP | Dukovany |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications. | The permanent fire load is determined by the nature of the space (office, warehouse, operation, workshop, etc.) and any flammable building structures (e.g. windows, doors, floor) and is based on standards. The temporary fire load is determined by the working activity and its needs (repairs, replacements, etc.). As part of the operation, the permanent fire load is reduced (if there is a replacement of non-flammable equipment, non-flammable windows, doors and floors are installed...), the temporary fire load is subject to the approval of the FP department and is monitored and limited. Permanent fire load is documented in the design, temporary in the database of the FP department. The permanent fire load must not be increased, temporary only up to the limit (approved by the FP department) Any information is in the database of the FP department. Limits for permanent load are given by the design and internal procedure (page 46), temporary load is limited to max 1kgm-2 (EDU). Fire load checks are part of the FRSU preventive inspections of the building, the frequency is determined by the "Fire Risk Assessment", corrective measures are carried out without delay. Hot works are managed by an internal methodology and are subject to approval by the FP department, which checks compliance with measures both during and after the work. Roles and responsibilities are regulated in the permit. Inspections are focused on fire prevention and compliance. Before starting, the FO department evaluates the place of work with an open fire and proposes adequate measures according to the type of work, the place of work and the conditions at the workplace. Subsequently, checks are carried out to ensure compliance with the conditions, and after the work is finished, there is a site security check and checks aimed at preventing the occurrence of fire. Hydrogen is stored in separate building, isolated pipe routes transport it into generator. For the possibility of hydrogen occurrence in reactor hall there are installed passive autocatalytic recombiners (17 pcs).
CZ-E-321 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | NPP | Temelin NPP | page 112/Section 3.3.A.1.2/ 1/Describe how the plant is divided into fire compartments and fire cells? Please define the terms: fire compartment, fire sections, fire cell? page 112/Section 3.3.A.1.1/2/ Are the fire resistances for fire barriers (fire walls, fire doors, fire dampers) for 15 minutes acceptible? Are fire resistance of fire barriers in compliance with national fire standards? page 113/Section 3.3.A.1.3/2/ How it is ensured that the expected fire resistance and stability ratings are fulfilled? |  | Buildings are divided into fire sections and fire cells by the designer, who proceeds according to applicable legislation. Fire section – area of a building, separated from other parts of this building, or from neighboring buildings, fire separation structures or fire safety equipment; Fire cell – a partial part of the fire section secured in an alternative way so that in the event of a fire, the fire remains limited only to the place of its origin and there is no unacceptable damage to other parts of the fire section. The principle of fire cells is applied to ensure the fire safety of fire sections containing systems, structures and components with an impact on nuclear safety. The basic assessed unit from the point of view of fire safety of buildings. Legislation/technical standards set the fire resistance of barriers to 15 minutes in 1st. degree of fire safety. After the realization of the work, the compliance with design requirements is proven by Protocols on compliance, Declaration of product quality and assembly protocols.
CZ-E-322 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | NPP | Temelin NPP |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers? | The design deals with the division of buildings into fire sections, determines the fire resistance of individual structures, and determines the quantity, scope and location of individual fire safety devices. In the event of a change of use, the project is evaluated and measures are proposed to maintain or increase fire safety. The ventilation system is described in NAR.
CZ-E-323 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | NPP | Dukovany | page 118/Section 3.3.B.1.2/1/ Describe how the plant is divided into fire compartments and fire cells? Please define the terms: fire compartment, fire sections, fire cell? page 118/Section 3.3.B.1.2/2/ How it is ensured that the expected fire resistance and stability ratings are fulfilled? |  | Buildings are divided into fire sections and fire cells by the designer, who proceeds according to applicable legislation. Fire section – area of a building, separated from other parts of this building, or from neighboring buildings, fire separation structures or fire safety equipment; Fire cell – a partial part of the fire section secured in an alternative way so that in the event of a fire, the fire remains limited only to the place of its origin and there is no unacceptable damage to other parts of the fire section. The principle of fire cells is applied to ensure the fire safety of fire sections containing systems, structures and components with an impact on nuclear safety. The basic assessed unit from the point of view of fire safety of buildings. After the realization of the work, the compliance with design requirements is proved by Protocols on compliance, Declaration of product quality and assembly protocols.
CZ-E-324 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | NPP | Dukovany |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers? | The design deals with the division of buildings into fire sections, determines the fire resistance of individual structures, and determines the quantity, scope and location of individual fire safety devices. In the event of a change of use, the project is evaluated and measures are proposed to maintain or increase fire safety. The ventilation system is described in NAR.
CZ-E-325 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | NPP | Temelin NPP | /Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences? |  | The ventilation ensure that the fire does not spread through the ventilation distribution. In the event of a fire, the ventilation is automatically shut down, except for the areas of the bitumen line, where fire ventilation is proposed. In the PSA, after a fire rise in the fire section, the inoperability of the equipment is caused by the fire. In the event of a fire, the loss of ventilation is not taken into account in the PSA model.
CZ-E-326 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | NPP | Temelin NPP |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made? | The fire dampers regular inspection and maintenance set the manufacturer, it´s function is checked one per 12 month. In Temelín NPP there are not non-accessible dampers.
CZ-E-327 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | NPP | Dukovany | /Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences? |  | The ventilation ensure that the fire does not spread through the ventilation distribution. In the event of a fire, the ventilation is automatically shut down, except for the areas of the bitumen line, where fire ventilation is proposed. In the PSA, after a fire rise in the fire section, the inoperability of the equipment is caused by the fire. In the event of a fire, the loss of ventilation is not taken into account in the PSA model.
CZ-E-328 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | NPP | Dukovany |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made? | Fire dampers are tested once per 12 month.
CZ-E-329 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | NPP | Temelin NPP | Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements. page 124/Section 3.4/1/ Did you have OSART missions? What were lessons learnt from OSART missions? |  | During past 10 years there occurred 3 fires in Temelín NPP. Twice personal carelessness (2014 fire of sawdust particles ignited by red-hot nail while sawed wooden pallet in open space, 2019 fire of spilt diluent and smoke filled in FRSU building) and one fire cause was technical fault (2015 fire of hand-drier in medical center). The last OSART was in 2021. It has led to an improvement of training materials, increase of safety requirements in using heat appliances, addition of safety requirements when using flammable liquids.
CZ-E-330 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | NPP | Temelin NPP |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries). | NPP: Ageing management of fire passive and active SSC The fire protection equipment is included on the base of safety classification – safety class 3. Those include system stable sprinklers, selected fire dampers, EFD as defined. The detail on the ageing management system is fully described in previous NAR on TPR I. With regard to the complexity of the entire evaluation system and to ensure the required quality of the evaluation process of the systems and their equipment condition, common management documentation for both NPP is prepared. As part of the evaluation, LIVE data from a complex set of applications describing the operational history of the nuclear power plant across the professional focus is used. All fire protection equipment is subject to regular inspections procedures and checks. Any fire protection systems are subject to an annual operability check, and in case of unsatisfactory condition, they are repaired, modernized or replaced. Mapping and repair of original fire partitions, fire doors, fire dampers and fire piping. The evaluation of safety systems and safety-related systems takes place according to the established schedule. A HEALTH REPORT - Summary Report on the state of technological systems and components is prepared. OPEX According to the Czech legislation, every fire must be reported, the fire classification is carried out by a fire cause investigator who is a member of the FRS CR. Every fire is reported to the FRS of the Czech Republic, the exchange of experience about fires that have occurred takes place at conferences and at instructional methodical jobs between the commanders of FRSU (energy, automotive industry, chemical industry, airports, etc.) within the Czech Republic. There were no fires in our facilities that resulted in a significant improvement in FP. The Czech legislation is adjusted based on experience from domestic fires as well as world practice.
CZ-E-331 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | NPP | Dukovany | page 124/Section 3.4/1/ What were lessons learnt from OSART missions? Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements. |  | During past 10 years there occurred 2 fires in Dukovany NPP. In 2020 fire of fluorescent lamp resulted in replacement of lightings by equivalents. In 2023 fire in distribution box caused by technical failure. Preventive measure is in place - inspection of UPS and batteries by thermocameras and input of suction openings in operational cards.
CZ-E-332 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | NPP | Dukovany |  | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? | The fire protection equipment is included on the base of safety classification – safety class 3. Those include system stable sprinklers, selected fire dampers, EFD as defined. The detail on the ageing management system is fully described in previous NAR on TPR I. With regard to the complexity of the entire evaluation system and to ensure the required quality of the evaluation process of the systems and their equipment condition, common management documentation for both NPP is prepared. As part of the evaluation, LIVE data from a complex set of applications describing the operational history of the nuclear power plant across the professional focus is used. All fire protection equipment is subject to regular inspections procedures and checks. Any fire protection systems are subject to an annual operability check, and in case of unsatisfactory condition, they are repaired, modernized or replaced. Mapping and repair of original fire partitions, fire doors, fire dampers and fire piping. Fire water is checked by a leak test and functionality check (flow rate The evaluation of safety systems and safety-related systems takes place according to the established schedule. A HEALTH REPORT - Summary Report on the state of technological systems and components is prepared. Based on the annual assessment of the state of the stable extinguishing equipment (SES) and stable sprinkler equipment (SSE) during regular prescribed revisions, it has long been found out that there is a gradual deterioration of its technical condition. Lack of spare parts for pumps, valves or pump´s motors (qualified for safety class 3). Technical obsolesce of fire dampers. Lack of fire protection coating equivalent. Leakage in fire piping buried underground. Delay of SSE forbidden agent replacement. Replacement of steel fire pipes with polyethylene pipes; replacements for stable halon extinguishing equipment – regulated substance HALON 1301 for the approved equivalent of NOVEC 1230); replacement of fire-fighting coating product DICO by other products (Flammoplast KS1 and DEKORLACK SP2); replacement of fire partitions.
CZ-E-333 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Research reactor | Research reactor LVR 15 | Please provide more information on the practise of temporary fire load management. |  | Procedures for the evaluation of experiments and modifications are introduced to monitor these actions, where the description of the change is part of the documents for the evaluation of the safety commission, which member is also fire protection person. Following the assessment a procedure is subsequently determined for fire protection - supervision of work, change of documentation, fire prevention measures; conditions for carrying out activities etc.
CZ-E-334 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Research reactor | Research reactor LVR 15 | It is declared that a special process in the management system has been implemented. What special process is used at LVR 15? |  | The management system program is part of the operation documentation. Within it, activities/processes are defined that can/are affecting nuclear safety, radiation protection, technical safety, etc. Among such processes, fire protection was also determined, and the description of the process specifies, beyond the scope of the company's fire protection documentation, responsibilities for selected parts of the process.
CZ-E-335 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Research reactor | Research reactor LVR 15 |  | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications. | Management of fire loads LVR The permanent fire load is determined by the nature of the space (office, warehouse, operation, workshop, etc.) and any flammable building structures (e.g. windows, doors, floor) and is based on standards. The temporary fire load is determined by the operation and its needs (repairs, replacements, etc.). As part of the operation, the permanent fire load is reduced (if there is a replacement of non-flammable equipment, non-flammable windows, doors, floors are installed...), the temporary fire load is subject to the approval of the FP department and is monitored and limited. Permanent fire load is documented in the design, temporary in the database of the FP department. The permanent fire load must not be increased, temporary only up to the limit (approved by the FP department) Any information is in the database of the FP department. Limits for permanent load are given by the design and internal procedure (page 46, 50, 57) temporary load is limited to max 1kgm-2 (EDU). Fire load checks are part of the preventive inspections of the building, the frequency is determined by the "Fire Risk Assessment", corrective measures are carried out without delay. Management of ignition sources Hot works are governed by an internal methodology and are subject to approval by the FP department, which checks compliance with measures both during and after the work. Powers and responsibilities are regulated in the permit. Inspections are focused on fire prevention and compliance. Before starting, the FP department evaluates the place of work with an open fire and proposes adequate measures according to the type of work, the place of work and the conditions at the workplace. Subsequently, checks are carried out to ensure compliance with the conditions, and after the work is finished, there is a site security check and checks aimed at preventing the occurrence of fire. Hydrogen is stored in separate building, isolated tubes transport it into generator. For the possibility of hydrogen occurrence in reactor hall there are installed passive autocatalytic recombiners.
CZ-E-336 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | Research reactor | Research reactor LVR 15 | How are the fire classes for fire barriers defined? |  | The fire resistance of a structure is the time for which the structure is able to withstand the effects of fire without breaking its function - limit state of bearing capacity or stability R, integrity E, temperature on the unheated side I, heat flow density W and penetration of combustion products S. Fire sections are defined based on the Fire Safety Solution (FSS) documentation of the building. In FSS, individual fire sections are assigned by fire resistance letter with a number indicating fire resistance in minutes - 15, 30, 45, 60 a 90 minutes.
CZ-E-337 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | Research reactor | Research reactor LVR 16 |  | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers? | In the Fire Safety Resolution of the building, the resistance of individual fire section is indicated, which prevent the spread of fires to other fire compartments. Aiming for a gradual division of the building into fire sections with separation of materials with defined resistance See section 3.3.C2 of the NHZ, p. 122 Extension of the EFD system to more locations in the building/technology; higher division of buildings into fire sections; during renovations, establish qualification requirements and the corresponding qualification documents (fire-retardant materials); regular review of fire protection requirements - fire prevention and fire fighting; regular training of the operator's cooperation with the fire brigade units. The main constraints will be the financial conditions for the implementation of changes (construction modifications and technology replacement), alternatively only the possibility to minimize the fire load and higher frequency of condition inspections. Part of the implementation of changes is the necessary assessment process - this should include assessment against the FP documentation - typically the facility's Fire Safety Resolution when changes are made. Fire load influences the size and degree of fire safety of the fire section - determined by the relevant standards and is part of the Fire Safety Resolution of the building. Material damage caused by flooding can be expected during a (unplanned) start-up. In case of interruption, a minor delay in intervention can be expected due to the need to switch to an alternative source (another hydrant/Fire Brigade vehicle).
CZ-E-338 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | Research reactor | Research reactor LVR 15 | Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers? |  | The radioactive substances ventilation system is equipped with absolute filters - these are connected as the main ones. Iodine filters are connected to the circuit in the event that increased activity is identified in the ventilation circuits. The basic verification of fire dampers function is their inspection by the supplier at least once a year (identification of the damper, opening of the inspection hole and checking of closing and opening, the movement of the fire damper leaf, the visual check of corrosion presence and the integrity of the fire insulation from the fire separation structure, inspection of cabling, triggering mechanisms and cleaning). Specific actions are given by the manufacturer's documentation.
CZ-E-339 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | Research reactor | Research reactor LVR 16 |  | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made? | Due to the installation of fire dampers, automatic decommissioning can be expected. In the event of a fire-related accident, the ventilation system is fitted with fire dampers that are automatically closed when the inlet medium reaches 68°C. In the event of a fire, the building is to be disconnected from electrical power, including the ventilation system. Until the building is disconnected from the power supply, we will use alternative extinguishing agents, designed for extinguishing under voltage. Therefore, the ventilation system will not be functional, the firefighters will follow the rules of intervention with the risk of possible contamination of radioactive release. See section 3.3.C2 of the NHZ, p. 122 The fire dampers are subject to maintenance programs - carried out at least once a year (specified in ČSN 73 0872). No findings were found when inspecting seals or other means used to prevent the spread of a potential fire.
CZ-E-340 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | Research reactor | Research reactor LVR 15 |  | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries). | The occurrence of any fire protection related event is reported to the FRS CR, for the purposes of information keeping it is recorded into a database as an operational event and further investigated and the results discussed at safety committees. Any fire in the guarded area of a nuclear installation is reported to the SÚJB. Any experience is transferred within working groups (typically e.g. RROG - research reactor operation group). FRSU personnel are then members of other working groups. In the CEZ Group, a fire protection expert group has been established, where members meet twice a year and share their experience. In the event of a significant safety event, this information is shared within the group and corrective measures are taken. For workplaces with at least three employees where activities with increased or high fire hazards are carried out, it is obligatory to establish a preventive fire watch. These watches supervise compliance with fire protection regulations and, in the event of a fire, take the necessary measures to rescue persons at risk and take part in the firefighting process. A fire log book is also maintained to record inspections, workplace deficiencies and other information relating to fire safety.
CZ-E-341 | PFP | CZ | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications. | The permanent fire load is determined by the nature of the space (office, warehouse, operation, workshop, etc.) and any flammable building structures (e.g. windows, doors, floor) and is based on standards. The temporary fire load is determined by the working activity and its needs (repairs, replacements, etc.). As part of the operation, the permanent fire load is reduced (if there is a replacement of non-flammable equipment, non-flammable windows, doors, floors are installed...), the temporary fire load is subject to the approval of the FP department and is monitored and limited. Permanent fire load is documented in the design, temporary in the database of the FP department. The permanent fire load must not be increased, temporary only up to the limit (approved by the FP department) Any information is in the database of the FP department. Limits for permanent load are given by the design and internal procedure. Fire load checks are part of the preventive inspections of the building, the frequency is determined by the "Fire Risk Assessment", corrective measures are carried out without delay. Hot works, if any, are managed by an internal methodology and are subject to approval by the FP department, which checks compliance with measures both during and after the work. Roles and responsibilities are regulated in the permit. Inspections are focused on fire prevention and compliance. Before starting, the FP department evaluates the place of work with an open fire and proposes adequate measures according to the type of work, the place of work and the conditions at the workplace. Subsequently, checks are carried out to ensure compliance with the conditions, and after the work is finished, there is a site security check and checks aimed at preventing the occurrence of fire.
CZ-E-342 | PFP | CZ | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers? | The design deals with the division of buildings into fire sections, determines the fire resistance of individual structures, and determines the quantity, scope and location of individual fire safety devices. In the event of a change of use, the project is evaluated and measures are proposed to maintain or increase fire safety. The ventilation system is described in NAR.
CZ-E-343 | PFP | CZ | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made? | The period is 12 month.
CZ-E-344 | PFP | CZ | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries). | According to the Czech legislation, every fire must be reported, the fire classification is carried out by a fire cause investigator who is a member of the FRS CR. Every fire is reported to the FRS of the Czech Republic, the exchange of experience about fires that have occurred takes place at conferences and at instructional methodical jobs between the commanders of FRSU (energy, automotive industry, chemical industry, airports, etc.) within the Czech Republic. There were no fires in our facilities that resulted in a significant improvement in FP. The Czech legislation is adjusted based on experience from domestic fires as well as world practice.
CZ-E-345 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) | NPP | Temelin NPP |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems. | Earthquake resistance of fire protection systems in Temelín NPP have the System SSE and High Pressure Pipeline Distribution in the Reactor Building and semi-stable extinguishing of systems diesels. The requirement is that they maintain functionality even during a seismic event. After the replacement of CZ-10 system by SINTESO there are used only addressable detectors. Safety class 3 include system stable sprinklers, selected fire dampers, EFD as defined: EFD are placed in sections according to requirements of the design, technical standards (ČSN), special assessment results, insurance pool recommendation. Rooms with no importance, e.g. toilets, do not have detectors. EFD has certification based on ČSN EN 54, power supply of autonomous operation at least for 24 hours by batteries. In general, it can be stated that in objects with the presence of RA substances and equipment that is classified in safety class 2, the electric fire alarm system is classified in safety class 3.
CZ-E-346 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) | NPP | Temelin NPP | Page 60-65 Section 3.2.A.1 Topic 2 - No detail on level of system resilience, hazard tolerance or what EMIT is required and how it is controlled. |  | The electrical detection system is in compliance with the Czech technical standards (see Reference). In the protection of spaces important from the point of view of nuclear safety, the systems are seismic resistant.
CZ-E-347 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) | NPP | Temelin NPP | Page 61 of pdf, section 3.2.A.1.2, assumption 1. "Multi-criteria (combined) detector AlgoRex and SINTESO - new generation detector, working on the principle of measuring and comparing several different variables characteristic for fire (more than 5000 units installed)". Please, explain the main features, variables compared, design standards and other general information regarding this type of detectors. - Page 61 of pdf, section 3.2.A.1.2, assumption 1. "Video smoke detection system - uses a conventional CCTV camera connected to a central unit, analyses incoming images frame by frame and decides if they contain smoke". "This feature allows the system to detect smoke efficiently and quickly even when traditional detection techniques are ineffective (aspirating, linear and spot smoke detectors)". Please, explain the main features, design standards and other general information regarding this type of detectors. - Page 61 of pdf, section 3.2.A.1.2, assumption 1. In general, are SSC important to safety covered by fire detectors? If not, please explain. |  | The detail information is available on web page of SIEMENS company. The detectors and video detectors have certified compliance with the Czech technical standard ČSN EN54 (342710). Important SSC are guarded by fire detectors.
CZ-E-348 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) | NPP | Dukovany |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems. | The EFD switchboards at RB have seismic classification 1a. Switchboards of outdoor objects are not seismic resistant. The EFD system is fully addressable, each detector has its own unique address, which, when activated, is displayed on the control panel and in the superstructure (graphic) system. EPS detectors are placed in the premises based on: • Requirements of relevant CSN standards • Outputs from PSR, or requirements of the SÚJB/IAEA instructions • Recommendations of insurance companies • The operator's request • Designer's proposal. Rooms without fire load (with low accidental load) are usually without detectors. In the event of a loss of electrical network power, the EFD switchboard is powered by a backup energy source (batteries). Accumulators are usually part of the EFD switchboards (or auxiliary source) and the battery life is at least 24 hours EFD protecting spaces where the SSC of safety systems are located is classified in safety class 3. Other EPS protecting equipment with an impact on safety is classified as non-selected equipment
CZ-E-349 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) | NPP | Dukovany | No detail on level of system resilience, hazard tolerance or what EMIT is required and how it is controlled. (As for Temelin.) |  | The electrical detection system is in compliance with the Czech technical standards (see Reference). In the protection of spaces important from the point of view of nuclear safety, the systems are seismic resistant.
CZ-E-350 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) | NPP | Dukovany | Page 85 of pdf, section 3.2.B.1.2, assumption 1. In general, are SSC important to safety covered by fire detectors? If not, please explain. - Page 89 of pdf, section 3.2.B.1.3, assumption 4. Explain the procedures established for the examination, inspection, maintenance and testing of fire detection and alarm features. |  | Important SSC are guarded by fire detectors. Inspections are carried out according to decree no. 246/2001 Coll. i.e. system operability check and, for EFD systems, also activity tests during operation with a frequency of 1M (monthly check) and 6M (semiannual check). Checks are carried out within the scope of the system manufacturer's recommendations, or depending on operational experience, this period will be shortened. Part of the annual inspection of operability also includes the verification of the function of the follow-on equipment that the EFD controls (fire hydrants, ventilation, etc.).
CZ-E-351 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) | NPP | Temelin NPP |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy. | Earthquake resistance of fire protection systems in Temelín NPP: the Stable Sprinkling System and High Pressure Pipeline Distribution in the reactor building and PHZ of system DGS are seismically resistant. The requirement is that they maintain functionality even during a seismic event. Any failure of EFDS and Dampers must not endanger other seismic resistant equipment. There is no requirement for seismic resistance for the rest of extinguishing systems. Fire equipment is in safety class 3 (stable extinguishers of SSCs, selected fire dampers, EFDS). In the probabilistic risk assessment, fire water systems are included as a possible source that can cause internal flooding. Loss of water as a fire extinguishing agent are taken into account in the design of the system. Active extinguishing systems are connected to electrical power supply category II. (DG) or own batteries with 24 hours of autonomous operation. Stable extinguishing system is designed according to the project in places where there is a high fire load, important equipment, spaces where manual extinguishing is complicated (confined spaces, cable risers, oil management spaces). The FRSU goes out to every fire even in places with a stable extinguisher and, if necessary, extinguishes the fire manually.
CZ-E-352 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) | NPP | Temelin NPP | Page 65-81 Section 3.2.A.2 Topic 1- large amount of detail regarding the various suppression systems provided on site but it is not clear how it is determined whether the suppression provisions are adequate to extinguish a fire (where this is required) or what the safety classification or design standards against which these systems have been designed. Please could clarification be provided on these points? |  | Fire extinguishing systems are designed on the basis of a project, which is processed by an authorized person according to valid standards. Design documentation is prepared for individual systems, the part of which are calculations. Fire extinguishing systems are designed to extinguish a fire in a given area. The valid technical standards are listed in Reference in NAR.
CZ-E-353 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) | NPP | Temelin NPP | Page 65-81 Section 3.2.A.2 Topic 4 - No discussion of hazard effects of suppression systems and retention arrangements for fire fighting water. Please could clarification be provided on these points? |  | The dangerous effects of fire extinguishing systems are the same as everywhere else. Spaces that are protected by water stable extinguishing systems are connected to the industrial drainage system, and in case of extinguishing, the water flows into the industrial drainage system and then to the cleaning station.
CZ-E-354 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) | NPP | Temelin NPP | 1. Section 3.2.A.2.3. Requirements for fire resistance of power (6 and 0.4 kV) and control cables of safety systems and compliance of these cables with established requirements - see paras. (3.2.A.) 2. Section 3.2.A.3.1 Information on availability of safe emergency hydrogen discharge from the turbogenerator in the event of a problem with the sealing system. |  | The fire resistance of cables is documented by certificates from type or selection tests, or their use is individually assessed by designated experts in "group for engineering solutions". In the case of purchases of cables to the internal warehouse, the specified types are subject of verification tests (including fire tests). The entire hydrogen storage and transport system both Units, including the safe release of hydrogen, is described in internal procedure No. 264. Leakage of pressurized hydrogen from the machine around the rotor pins is prevented by radial rotor oil seals and a sealing oil system. CO2 is available for emergency emptying of the machine.
CZ-E-355 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) | NPP | Temelin NPP | Page 69 of pdf, section 3.2.A.2.2, assumption 1. "Foam Semi-Stable Extinguishers in Diesel Generating Stations: The equipment is designed to extinguish fires arising in the buildings of diesel generating stations. This equipment does not have its own extinguishing agent tank or its own extinguishing agent pump and works in synergy with mobile firefighting equipment". How long does it take to deploy the mobile firefighting equipment and start suppression activities? Is this special arrangement considered in the training program? Which is the water and foam capacity (volume and suppression time) of the mobile firefighting equipment? - Page 72 of pdf, section 3.2.A.2.2, assumption 2. Fire water supply system - seismic resistant: "Water source - the permanent fire water supply consists of a steel tank with a volume of 70 m3". Which is the suppression duration supposed to calculate this capacity? - Page 77 of pdf, section 3.2.A.2.3, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain. |  | After the arrival of the FRSU on the scene, the intervention starts within one minute and extinguishing takes place immediately. Firefighters of the FRSU regularly practice intervention on extinguishing DGS. Exercises are scheduled according to the training program. The capacity of water and foam is for 10 minutes of extinguishing plus three times the supply of extinguishing agent (water, foam). The water capacity is unlimited, foaming agent at 1% solution, currently FRSU has a stock of approx. 600,000 liters of extinguishing solution. Water is added to the tank from the technical water system, the water source is inexhaustible. The extinguishing time is calculated as 10 minutes. Flooding is not expected, the systems are flooded up to the valve station, and the pipeline is not flooded. Retention is through drainage system.
CZ-E-356 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) | NPP | Dukovany |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy. | Seismic resistance of individual fire extinguishing systems is described in dedicated chapters. The safety classification is mentioned in NAR – „system“ = safety classified (2 or 3), „non-system“ = without safety class. The fire water flooding in extinguished section is presumed and the water is drained to special sewerage. The emergency electrical supply is based on diesel generators and batteries. The last possibility is fire truck connection to the special inlets. Stable fire extinguishing equipment is designed according to the project in places where there is a high fire load, equipment is important, spaces where manual extinguishing is complicated (confined spaces, cable risers, oil management spaces) in spaces where, thanks to the designed SHZ, the designer can reduce the fire risk and thereby reducing the fire resistance of building structures and others. Main principles of SES use: protection of important equipment - cable management, oil management, complicated manual extinguishing - cable risers. In the area of cable risers, the availability of manual extinguishing was taken into account.
CZ-E-357 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) | NPP | Dukovany | As for Temelin. |  | Fire extinguishing systems are designed on the basis of a project, which is processed by an authorized person according to valid standards. Design documentation is prepared for individual systems, the part of which are calculations. Fire extinguishing systems are designed to extinguish a fire in a given area. The valid technical standards are listed in Reference in NAR.
CZ-E-358 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) | NPP | Dukovany | Page 90 of pdf, section 3.2.B.2.2, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown or any similar provision? - Page 96 of pdf, section 3.2.B.2.2, assumption 1. Are there fixed suppression systems based on foam? - Page 99 of pdf, section 3.2.B.2.3, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain. - Page 101 of pdf, section 3.2.B.2.4, assumption 3. Explain the procedures established for the examination, inspection, maintenance and testing of extinguishing systems. |  | In the protection of spaces important from the point of view of nuclear safety, the systems are seismic resistant. Dukovany NPP do not use foam extinguishers. There is an industrial sewer in the areas protected by the water stable extinguishers, in the event of a start-up, the water flows through this sewer and is collected and cleaned. Inspections are carried out according to decree no. 246/2001 Coll. i.e. system operability check. Checks are carried out within the scope of the system manufacturer's recommendations, operating procedures or depending on operational experience, this period will be shortened.
CZ-E-359 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) | NPP | Dukovany | 1. Section 3.2.A.2.3 Requirements for fire resistance of power (6 and 0.4 kV) and control cables of safety systems and compliance of these cables with established requirements - see paras (3.2.A.) 2. Section 3.2.A.3.1. Information on availability of safe emergency hydrogen discharge from the turbogenerator in the event of a problem with the sealing system. |  | The fire resistance of cables is documented by certificates from type or selection tests, or their use is individually assessed by a group for engineering solutions. In the case of purchases of cables to the internal warehouse, the specified types are subject of verification tests (including fire tests). The entire hydrogen storage and transport system both Units, including the safe release of hydrogen, is described in internal procedure No. 264. Leakage of pressurized hydrogen from the machine around the rotor pins is prevented by radial rotor oil seals and a sealing oil system. CO2 is available for emergency emptying of the machine.
CZ-E-360 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP | Temelin NPP |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. | The FRS CR is located in Týn nad Vltavou, the distance is 7 km from NPP. The duration of an intervention inside the reactor hall in non-working hours is the same as during working hours - 4 minutes from notification to arrival at the scene and 3 minutes for combat deployment inside the building. The nearest FRS has 8 firefighters+1 commander (in 3 shifts totally 25 persons). The FRS has ability to intervene in and off site of NPP. The fire alarm plan defines the FRS to intervene in dedicated area. If the case of fire magnitude exceeds the FRSU sufficient number of forces and resources to extinguish the fire, the hail of the state FRS CR is automatically applied based on permanent connection to the FRS CR operational center. The arrival time of the first Temelín FRSU team from the alarm announcement is a maximum of 4 minutes. The company FRSU has 3 outgoing teams, which means that another team can go out to the fire at the same time or according to the requirements of the intervention commander. The state FRS CR is able to respond to a fire within 15-20 minutes, depending on the driving distance. Arrival times are checked as part of cooperation in joint interventions and exercises. Temelín NPP FRSU is in site. Page 83 Equipment is on Pg. 84. The FRSU is provided with the necessary protective equipment (protective clothing, radiate heating clothing, overpressure clothing for liquidation of chemical incidents). The NPP firefighters are professional staff with no other duties except fire suppression and rescue.
CZ-E-361 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP | Temelin NPP | Page 81 - 84 Section 3.2.A.3 Topic 5 - no detail provided of fire drills and exercises. Please could clarification be provided on this point? |  | The FRSU's exercises are based on the annual training program, as a rule, each shift performs two exercises per month. Furthermore, once a month, an exercise is organized in a selected construction object with the aim of evacuating people. Minimum once a year is organized a cooperation exercise with FRS CR.
CZ-E-362 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP | Temelin NPP | Page 81 - 84 Section 3.2.A.3 Topic 3 - no detail provided on EMIT of fire protection measures. Please could clarification be provided on this point? |  | Earthquake mitigation was subject to special assessment EU "Stress Tests” in 2012 resulted in Action Plan (published on web page). Many measures after the Fukushima event were implemented also in fire protection measures – upgrading the FRSU station, additional equipment and mobile operating equipment, increasing the number of firefighters, diverse additional and mobile equipment technology for the company fire brigade (Diverse EFW System), hydrogen recombiners. There are actively used external and internal feedback, which assess the influence of external and internal events on the fire protection process.
CZ-E-363 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP | Temelin NPP | 1. There is no detailed information on the NPP's strategy regarding improvement of the active fire protection, including modernization of the fire protection system. Please provide missing information. 2. Section 3.2.A.3 The information on the organization of safe staff work performance related to fire-hazardous activities is missing. Please provide missing information. |  | In 2003, the NPP Temelín fire safety improvement study was prepared, which established the requirements for increasing fire safety in individual areas and the conditions under which these improvements can be made and recommended the order of their implementation. The document was a basis for strategic decisions in connection with the gradual increase in fire safety in the power plant. Other suggestions for improving fire safety include the recommendations of insurance companies (nuclear pool, EMANI), the needs of the independent FP administration department, and recommendations from the PSR. As mentioned in the Chapter 1.2.1 (Pg. 16) Act No. 262/2006 Coll., the Labor Code, stipulates the employer's obligation to carry out regular training in the field of occupational health and safety. Details of employee training in fire protection stipulate Section 23 of Decree No. 246/2001 Coll. - the obligation to repeat the fire training every 2 years. All NPP employees are regularly trained once a year in the rules of fire protection, where there is information on the safe behavior of employees.
CZ-E-364 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP | Temelin NPP | Page 81 - 84 Topic 1 Section 3.2.A.3 - no detail provided on whether the internal fire brigade would need to call on the external fire brigade. If so, what are the criteria and how are the external fire brigade contacted? Please could clarification be provided on these points? |  | The intervention of an external FRS is based on the extent of the fire, according to the regional Fire Alarm Plan. The regional fire alarm plan determines FP units for individual district of the region. The units are activated through the regional operating center of the FRS region.
CZ-E-365 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP | Temelin NPP | Page 81 of pdf, section 3.2.A.3, assumption 4. "The firefighters perform repressive activities in four shifts, each with 18 firefighters + 1 driver". Explain the training, organisation, minimum knowledge and physical conditions of the fire brigade. - Page 81 of pdf, section 3.2.A.3, assumption 1. "The maximum time of arrival of the FRSU to the most important buildings of the nuclear power plant (MPU) is 4 minutes from the occurrence of a fire that is detected by EFD". Please, give evidence of the time of arrival from real events and drills. - Page 83 of pdf, section 3.2.A.3.2, assumption 1. Drills and exercises are not described. Please explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade, content and main lessons learnt. - Page 83 of pdf, section 3.2.A.3.2, assumption 2. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 83 of pdf, section 3.2.A.3.2, assumption 2. Explain the coordination between the onsite fire brigade and the offsite response group. - Page 83 of pdf, section 3.2.A.3.2, assumption 2. Explain the written procedures in place defining responsibility and actions of staff in responding to any fire in the installation. |  | The training of the FRSU is organized according to issued annual training plan of the FRS of the Czech Republic by the Ministry of the Interior. Subsequently, this training plan is applied to the annual training and training plan of the NPP. Physical fitness and the limits for successful completion of physical tests is established in departmental instruction. Physical tests are reviewed once a year. Theoretical and practical knowledge is given by training programs with its examination once a year. On the basis of intervention reports, which is one of the mandatory documents of the FRSU, the individual times of the unit's arrival at the building can be documented. The time of announcement, departure and arrival is controlled by uniform time (NTP). Every year, each of the 4 shifts must perform at least 24 tactical exercises on a selected building object and 3 exercises on the topic of evacuating a building object. An intervention report was drawn up from each exercise. These exercises are given by the Instruction of the head of the fire protection unit. According to the DAM training schedules, all exercises of stress tests management are performed every 3 years. Firefighting documentation for all building objects and intervention cards are prepared, where interventions on important objects and systems in the NPP are described. There is a description of the structure, the system, the determination of the technique for extinguishing the fire, a suitable extinguishing agent, the protection of the responding firefighters, a description of the possible risks during the intervention, recommendations for the intervention commander. Communication is set up and regularly checked through operational centers where the first exchange of information takes place. Subsequently, the FRSU communicate using radio stations on a common communication channel. The units are equipped with the same means of communication. Employees of the power plant and leaders of suppliers are regularly trained in fire protection once a year. Regular exercises in which objects are evacuated are in place. Fire points are located in buildings, on which instructions are described on how to behave in the event of a fire and when evacuating people from the given building.
CZ-E-366 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP | Dukovany |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. | The nearest professional FRS of the Vysočina region is in the village of Hrotovice (7 km - calculated travel time max. 10 min. - considered at a speed of 45 km/h). In the event of an intervention, the FRSU is not blocked by the administration. The entrance to the buildings, including the reactor building, is through escape routes. Always with the approval of shift engineer and after ascertaining the current radiation situation at central dosimetry control. Each firefighter is then equipped with a dosimeter. After the end of the intervention, a standard output including dosimetry control is performed. The necessary time for combat development in accordance with the combat and training regulations is 2 to 10 minutes depending on the specific location and complexity of the combat development (rescue of a person, stretcher, fire, intervention in pressure suits, danger of explosion, etc.). The minimum number of 4 firefighters in Hrotovice is required. They are able to go out with two vehicles at the same time in the number of 1+1. Average or maximum driving times are not set, according to the applicable legislation, the calculated time is used (7km - calculated driving time max. 10 min. - considered at a speed of 45 km/h), however the modernized technology already has a standard driving speed to hit 60km/h. According to the legislation, the time limit is 7 minutes - only driving time and combat development. The actual time from the start of the intervention since the announcement of the alarm is around 5 minutes. The organization of the FRSU Dukovany NPP unit is set so that both teams leave at the same time. FRSU is described on page 101-103 There are no additional activities that could affect the availability of firefighters; all team is professional.
CZ-E-367 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP | Dukovany | As for Temelin. |  | The FRSU's exercises are based on the annual training program, as a rule, each shift performs two exercises per month. Furthermore, once a month, an exercise is organized in a selected construction object with the aim of evacuating people. Minimum once a year is organized a cooperation exercise with FRS CR.
CZ-E-368 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP | Dukovany | Page 102 of pdf, section 3.2.B.3, assumption 4. "The 70 firefighters perform repressive activities in four shifts, each with 12 firefighters on the day shift and 11 firefighters on the night shift divided into 3 fire teams". Explain the training, organisation, minimum knowledge and physical conditions of the fire brigade. - Page 102 of pdf, section 3.2.B.3, assumption 1. "The maximum time of arrival of the FRSU to the most important buildings of the nuclear power plant (MPU) is 4 minutes from the occurrence of a fire that is detected by EFD". Please, give evidence of the time of arrival from real events and drills. - Page 104 of pdf, section 3.2.B.3.2, assumption 1. Drills and exercises are not described. Please explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade, content and main lessons learnt. - Page 104 of pdf, section 3.2.B.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 104 of pdf, section 3.2.B.3.2, assumption 2. Explain the coordination between the onsite fire brigade and the offsite response group. - Page 104 of pdf, section 3.2.B.3.2, assumption 2. Explain the written procedures in place defining responsibility and actions of staff in responding to any fire in the installation. |  | The training plan of the FRSU of Dukovany NPP is in accordance with the professional training (including physical training) and is supplemented by topics that are specific to NPP (special equipment, individual NPP buildings, specific activities, DAM exercises, etc.). The resulting number of hours of professional training more than doubles the set minimum (80 hours) given by national legislation. The training plan for the given calendar year is sent to the Regional FRS of the Vysočina region. Regular verification of the knowledge of FRSU employees takes place once a year (including physical tests), and then there is regular verification of knowledge for individual functions as part of the qualification for the performance of a function in the Training and Education Facility of the FRS CR (period once every 5 years). The reaction time of FRSU intervention is measured an is between 2 to 4 minutes (proven by SÚJB). Practices and exercises are carried out practically every day as part of the established professional training plan. This is mainly training according to combat and exercise regulations, DAM exercises and intervention exercises in individual buildings. There are operative cards in case of intervention for all rooms where EFD/SES is installed. These cards contain information and procedures in case of intervention. Firefighting documentation, including the graphic part, is also processed for selected objects. The coordination of the intervening units is in accordance with the training and Battle Order of the FRS units. The units proceed in the same way for all Integrates Rescue Service interventions. Thus, an intervention commander is determined, who manages the firefighting and rescue work. The coordination and transmission of other units, possibly other components, is carried out by the Vysočina Region FRS Operations Center in cooperation with the NPP FRSU Operations Center (outbound system GINA, DIGITAL RDST, ANALOG RDST, by telephone). At the point of transmission of instructions, the intervention commander ensures, in the case of major incidents, the sector commander/section commander. If necessary, it is possible to use the national emergency cooperation channels of radio traffic. The established written procedures are mainly individual operating regulations in case of fire. Procedures describe how operating personnel should proceed in the event of a fire.
CZ-E-369 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP | Dukovany | 1. There is no detailed information on the NPP's strategy regarding improvement of the active fire protection, including modernization of the fire protection system. Please provide missing information. 2. Section 3.2.A.3 The information on the organization of safe staff work performance related to fire-hazardous activities is missing. Please provide missing information. |  | All fire protection systems are subject to an annual operability check, and in case of unsatisfactory condition, they are repaired, modernized or replaced. Detail are in NAR on page 85. NPP have developed a methodology and basic rules of procedure for fire-hazardous work. These works require a permit from the NPP FP department, which sets the conditions for a given type of fire-hazardous work, determines the fire patrol and supervision of these works and the period of supervision after the work is completed.
CZ-E-370 | AFP | CZ | Active fire protection | Licensee and regulatory experience | NPP | Temelin NPP |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs. | There is no such a experience. Regular checks in accordance with the requirements of the equipment manufacturer and in accordance with legislation are required. After the titanium pipe fire on July 2, 2015 at the Paluel nuclear power plant - France, this event was presented at the training of managers, with the fact that when working with an open flame, an appropriate technological procedure must be chosen and appropriate safety measures must be ensured - rigorous control workplace, workplace fencing, etc. A suitable type of fire extinguisher must be available on site to ensure first intervention.
CZ-E-371 | AFP | CZ | Active fire protection | Licensee and regulatory experience | NPP | Temelin NPP | Page 125 of pdf, section 3.6, and all the assumptions. Strengths and weaknesses are not clearly mentioned in the NAR, can you confirm that there are no strengths / weaknesses or otherwise mention them if there are any? |  | Described on page 28
CZ-E-372 | AFP | CZ | Active fire protection | Licensee and regulatory experience | NPP | Dukovany |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs. | Based on operational experience, the cleaning period of flame detectors on outdoor transformers was adjusted to the 3 month period. For EFD intake units, part of the half-yearly inspection includes filter cleaning as well. The probability of fire in the PSA is calculated according to generic data that is based on international documents.
CZ-E-373 | AFP | CZ | Active fire protection | Licensee and regulatory experience | NPP | Dukovany | Page 125 of pdf, section 3.6, and all the assumptions. Strengths are not clearly mentioned in the NAR, can you confirm that there are no strengths or otherwise mention them if there are any? - Page 125 of pdf, section 3.6, and all the assumptions. Weaknesses are not clearly mentioned in the NAR, can you confirm that there are no weaknesses or otherwise mention them if there are any? |  | Described on page 33
CZ-E-374 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) | Research reactor | Research reactor LVR 15 |  | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? | The EFD system is not classified with a requirement for seismic resistance. The EFD is designed according to ČSN 73 0875 and ČSN 34 2710 in the scope of the Fire Safety Solution. EFD system has sensors with an address. Solved within the framework of the construction's Fire Safety Solution. Typically, they are not in places where due to the method of EPS detection a relevant response of the system cannot be expected - hall with high ceilings, rooms with significant draught - in these places the placement of EFD on the ceiling does not provide the necessary information and an alternative location (e.g. cable trays) or a surveillance procedure (cameras) is chosen. The control panels have a backup power supply for 24 hours
CZ-E-375 | AFP | CZ | Active fire protection | Fire suppression (TS 3.2.2) | Research reactor | Research reactor LVR 15 |  | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy. | The safety classification is mentioned in NAR on page 15 “fire safety systems are in SC 3. The fire water flooding in extinguished section is presumed and the water is drained to special sewerage. The emergency electrical supply is based on diesel generators and batteries. The last possibility is fire truck connection to the special inlets. Stable extinguishing equipment is designed according to the project in places where there is a high fire load, equipment is important, spaces where manual extinguishing is complicated (confined spaces, cable risers, oil management spaces).
CZ-E-376 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Research reactor | Research reactor LVR 15 |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. | FRS of the Czech Republic in Neratovice is in distance 20 km. Required response time is 92 minutes. Calculation from Fire Fighting documentation, approved by the Fire Department of the Central Bohemia Region From the moment of fire detection to the start of actual firefighting is 7 minutes. The minimum staffing of the nearest off-site FRS is 1+5 persons. The FRSU is set at 1+3 persons - in the event of larger incidents, external help is called in parallel. According to the assessment of the management group and the intervention leader on the ability to handle the situation with the current cast/shift. It is done every time a fire is detected. The time needed between the fire alarm declaration and the presence of the first response unit on the scene is 5 minutes. The second response is required in 25 minutes. The actual times measured during recent unannounced exercises and drills are as expected. To be determined in the Fire Fighting document. See 3.2.C.3.p. 108 Firefighters are required to leave within 2 minutes of an alarm being declared for any activity.
CZ-E-377 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Research reactor | Research reactor LVR 15 | Composition of the "shift" dedicated to firefighting. p 125 : "Thanks to the presence of the Fire Rescue Service Unit directly on the site" : it is not clear for the status of this team: public or private ? |  | This is the Fire and Rescue Service of the company ÚJV Řež, a. s. – private. The minimum shift composition is 4 persons. See Pg. 14 Article 49 of Atomic Act specifies the obligation to ensure the prevention, detection, elimination and suppression of fires and explosions and the limitation of their impact on safety and to provide a unit of the company's Fire Rescue Service in accordance with the Fire Protection Act.
CZ-E-378 | AFP | CZ | Active fire protection | Licensee and regulatory experience | Research reactor | Research reactor LVR 15 |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors. | Within the operation of the EFD, sometimes, based on false alarms, the type of sensor is changed, e.g. optical-smoke for thermal, etc. in accordance with the Fire Safety Solution. Based on the experience from the evacuation drills, automatic opening of sliding doors in the administration building depending on the EFD signal has been added. The LVR-15 reactor facility was not affected by a significant fire. Regular exercises at least once every 2 years are a source of experience. Exercises include follow-up analysis and determination of measures: some areas has been equipped with additional portable fire extinguishers During evacuation, an connection to a member of the Fire and Rescue Service unit was tested, where it is possible to ensure the presence of the equipment operator at the workplace for the most necessary actions in a limited period of time. Restricted use identification cards to exit the building during a fire. The FRSU in cooperation with external units is able to provide protection of the reactor from forest fire by remote transport of water from the river based on the experience from the exercise.
CZ-E-379 | AFP | CZ | Active fire protection | Fire detection and alarm (TS 3.2.1) | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? | Described on page 110 - 111 & 124 of NAR.
CZ-E-380 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). | The FRS CR is located in Týn nad Vltavou, the distance is 7 km from NPP. The duration of an intervention inside the reactor hall in non-working hours is the same as during working hours - 4 minutes from notification to arrival at the scene and 3 minutes for combat deployment inside the building. The nearest FRS has 8 firefighters+1 commander (in 3 shifts totally 25 persons). The FRS has ability to intervene in and off site of NPP. The fire alarm plan defines the FRS to intervene in dedicated area. If the case of fire magnitude exceeds the FRSU sufficient number of forces and resources to extinguish the fire, the hail of the state FRS CR is automatically applied based on permanent connection to the FRS CR operational center. The arrival time of the first Temelín FRSU team from the alarm announcement is a maximum of 4 minutes. The company FRSU has 3 outgoing teams, which means that another team can go out to the fire at the same time or according to the requirements of the intervention commander. The FRS CR is able to respond to a fire within 15-20 minutes, depending on the driving distance. Arrival times are checked as part of cooperation in joint interventions and exercises. Temelín NPP FRSU is in site. Page 83 Equipment is on Pg. 84. The FRSU is provided with the necessary protective equipment (protective clothing, radiate heating clothing, overpressure clothing for liquidation of chemical incidents). There are no additional activities that could affect the availability of firefighters; all team is professional.
CZ-E-381 | AFP | CZ | Active fire protection | Licensee and regulatory experience | Spent fuel storage - dry | NPP Temelin Dry Spent Fuel Storage |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. | Temelín NPP: 68 failures were recorded on the EPS system for the year 2023. In 2023, 10 failures were recorded on the fire water system. In 2023, 19 malfunctions were recorded in the ventilation system. That includes also SFS systems.
CZ-E-382 | AFP | CZ | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Spent fuel storage - wet | Spent Fuel Storage facility |  | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). | The FRS CR is located in Týn nad Vltavou, the distance is 7 km from NPP. The duration of an intervention inside the reactor hall in non-working hours is the same as during working hours - 4 minutes from notification to arrival at the scene and 3 minutes for combat deployment inside the building. The nearest FRS has 8 firefighters+1 commander (in 3 shifts totally 25 persons). The FRS has ability to intervene in and off site of NPP. The fire alarm plan defines the FRS to intervene in dedicated area. If the case of fire magnitude exceeds the FRSU sufficient number of forces and resources to extinguish the fire, the hail of the state FRS CR is automatically applied based on permanent connection to the FRS CR operational center. The arrival time of the first Temelín FRSU team from the alarm announcement is a maximum of 4 minutes. The company FRSU has 3 outgoing teams, which means that another team can go out to the fire at the same time or according to the requirements of the intervention commander. The FRS CR is able to respond to a fire within 15-20 minutes, depending on the driving distance. Arrival times are checked as part of cooperation in joint interventions and exercises. Temelín NPP FRSU is in site. Page 83 Equipment is on Pg. 84. The FRSU is provided with the necessary protective equipment (protective clothing, radiate heating clothing, overpressure clothing for liquidation of chemical incidents). There are no additional activities that could affect the availability of firefighters; all team is professional.
CZ-E-383 | AFP | CZ | Active fire protection | Licensee and regulatory experience | Spent fuel storage - wet | Spent Fuel Storage facility |  | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. | Same as NPP.

## COUNTRIES
Question ID | Reviewer (Country authorities) | Country/NAR | Fire Protection Thematic | Page no. in NAR (if specified) | Question - General (including generic/general experts' questions for type of installation) | Country's response | Cross reference to to another question-reply (Question ID) | Any remarks
CZ-C-85 | Austria | CZ | 01-General information | 19 | As stated in 1.2.3. FRS performs inspections of nuclear power plants on an annual basis, always on one selected building. FRS has performed a comprehensive inspection of all nuclear power plant buildings in 2013 at Temelín NPP. However, one of the conclusions was that due to the scope and documentation requirements of such an action and the resulting inadmissible duration of the entire inspection process, the feedback effect of the inspection process completely disappears. Thus, the FRS followed the path of annual inspections of one selected building from the list of risk buildings determined by deterministic analysis. How many buildings are declared significant? How are those inspected? Are there any other inspections (e.g. conditions of fire detection of fire extinguishing systems and components)? How often are they inspected? | At the Temelín NPP, 22 buildings are declared as important. Inspections of these buildings are carried out in accordance with the requirements of state legislation, namely according to the determination of fire risk, usually 4 times a year by FRSU. The FRS of CR inspect one of those separately. Fire safety equipment is checked by FRSU according to the requirements of the equipment manufacturer and legislation, an operability test must be carried out at least once every 12 months. The manufacturer of the device can also specify a shorter inspection period.
CZ-C-86 | Austria | CZ | 02- Fire safety analyses | 20 | Regarding "Audit No. 5", which examined the design of significant nuclear power plant buildings in relation to the terms between fire hazards and safe shutdown of the nuclear reactor according to the criteria defined in US 10CFR50, Appendix R and NUREG-8000, Part 9.5.1 (1995). How do you define significant buildings? | Important buildings are defined according to the fire risk, the content of security systems and the content of safety important equipment and radiation protection areas. Algorithm for fire safety assessment of NPP buildings is on page 22 of NAR.
CZ-C-87 | Austria | CZ | 02- Fire safety analyses | 21 | Regarding the study prepared by Nuclear Research Institute Řež, Energoprojekt Praha for the purposes of the Topical Peer-Review "Fire Protection" division many areas were covered but some of the most important areas for Nuclear Safety are not mentioned (e.g. MCR, cable spreading rooms, etc.). Please elaborate on the reasons for not mentioning these areas. | In this study, evaluated were areas where there was need for increased fire safety. Areas that met the required safety parameters and where no room for further improvement was found were not evaluated in this study.
CZ-C-88 | Austria | CZ | 02- Fire safety analyses | 24 | In 2011, a "Technical Assistance" document was prepared to examine the suitability and addition of Electrical Fire Detectors (EFD) in selected areas of the reactor and auxiliary buildings. A fire risk analysis was made for each room and, where values were exceeded for rooms without fire risk, the actual values were verified on site. Could you explain which rooms were covered here and what does “where values were exceeded for rooms without fire risk” mean? On which basis was the status “without fire risk” determined and what was e.g. the probability of fire ignition for those rooms? | Fire sections and spaces without fire risk are defined in the Czech technical standard (ČSN) and those are spaces in which the maximum fire load is less than 7.5 kg/m2 and are bounded by non-combustible structures. There is very little or no fire load in these spaces and there are no sources of initiation.
CZ-C-89 | Austria | CZ | 02- Fire safety analyses |  | It is stated that power cables and most low-current cables have enhanced resistance to the spread of fire, complying with IEC 332.3 category A, or IEC 331 tests, in all nuclear safety-important buildings. Were all original cables replaced in a course of pre-start up modernization at Temelin? | The decision to use only cables with increased resistance to the spread of flame according to IEC 332.3A and, in the case of safety cables, additionally according to IEC 331 in the buildings of the main production unit was made even before the start of cables implementation during construction stage.
CZ-C-90 | Austria | CZ | 02- Fire safety analyses | 25 | It is stated that documentation is actualized as required by the Fire Protection Act. This document approves the South Bohemian Regional Fire Rescue Service. The latest version of the fire risk assessment of the 1st reactor turbine hall has approval issued on 18 April 2016. What is the frequency of the updates as per applicable regulations? How of the is the fire risk assessment for all buildings updated? | The fire risk assessment is checked once a year, and if there have been changes in the building that affect the updating of the document, the documentation is revised.
CZ-C-91 | Austria | CZ | 02- Fire safety analyses | 30 | The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 20.3% level. This is a rather high contribution from internal fires, possibly indicating a safety challenge in this area. On which total CDF is 20.3% fire related? | CDF/year of all internal initiating events = 3,42E-06. CDF/year of fire internal events = 7,05E-07. IE groups are: Internal fires leading to the LOCA; Internal fires leading to the loss of secondary circuit; Internal fires leading to the LOCA; Internal fires leading to the loss of electrical power supply.
CZ-C-92 | Austria | CZ | 02- Fire safety analyses | 31 | The contributions of internal fires to the overall risk of unit operation are generally of little importance. The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 20.3% level. What about MCR and cable spreading areas? | Internal fire hazard analyzes include all fire section that contain equipment important to nuclear safety or related equipment, including MCR and cable areas. The fire in MCR is one if initiating events calculated in PSA.
CZ-C-93 | Austria | CZ | 02- Fire safety analyses | 33 | In this section, it is mentioned that the water SE, which protects the cable compartments, is obsolete. At present, the Dukovany NPP has developed a requirement for the selection of the most suitable method of securing the cable compartments by the SE. A working group has been set up to evaluate the different options. Since fire in the cable spreading areas is likely the dominant risk factor, when will this be completed and why was it not done before? | The water system is functional, but its innovation was not approved. The internal procedure is not finished as management of such a big modification is subject to legal conditions.
CZ-C-94 | Austria | CZ | 02- Fire safety analyses | 33 | Conference on fire protection and nuclear safety. Fire protection specialists obtain information on the latest trends in the field of fire safety. The information can be used to comment on new actions, or specialists recommend the implementation of these innovations a NPP. GOOD PRACTICE | Employees of the FP department participate in several conferences, seminars, and fire protection workshops every year. The last one was held in České Budějovice on 9-10 April 2024. In June 2024 is planned specialized conference on FP of NPP.
CZ-C-95 | Austria | CZ | 02- Fire safety analyses | 35 | “The introduction of the elements of cooperation and real distress cannot be replaced by any training for the members of the Fire Rescue Service.” Please clarify what is meant by this statement. | The level of stress and collective and personal responsibility and perception of danger in a real intervention is completely different from any training. This is a fact that affects the behavior of each individual, albeit to varying degrees. For the commander, the behavior of the subordinates during the actual intervention is an important indicator of the abilities of the team members.
CZ-C-96 | Austria | CZ | 02- Fire safety analyses | 35 | In regards to the inspection activities performed by the SÚJB and the Fire Rescue Service results. What is the frequency and scope of the inspections? | Fire inspections at the NPP are usually carried out once every 3 years by the Regional FRS. From the results of these inspections it can be stated that within the scope of the inspection points the obligations set out in Act No. 133/10985 Coll., on Fire Protection, as amended, were fulfilled. The NPP FRSU performs “day-by-day” inspections of all NPP buildings. SÚJB has Standard Annual Inspection Plan, which includes 4+2 inspection of reactor unit ventilation systems and every other year the fulfilment of implementation of fire protection system assurance of dedicated NPP.
CZ-C-97 | Austria | CZ | 02- Fire safety analyses | 36 | On this page it is mentioned that temperatures of several 1 000 °C are reached during the combustion of chemical gases and vapors. Several thousand degrees sounds rather high. | In the reactor building there are present combustible gases with high ignition temperature or combustible liquids e.g. diesel fuel. The structural systems are made of non-combustible material type DP1 (they do not increase the fire intensity during the required fire resistance period). For cable penetrations from fire sections, they are at least EW 30 DP1 and the fire resistance of structures is at least EI 60 DP1. Combustion takes place in a controlled manner within safety limits and the possible temperature is taken into account in approval of such a work.
CZ-C-98 | Austria | CZ | 02- Fire safety analyses | 39 | It is mentioned that the next fire exercise is planned for 2023. Did the mentioned fire exercise already take place and what are the outcomes? Are any exersices planned that would focus on safety significant sequences (for systems of the RR itself) rather than on the sources? | Fire exercise organized in cooperation with the company FRS and a group of volunteer firefighters was performed by the end of 2023. The theme was „simulated operation of the LVR-15 reactor at power; during operation, a warning signal of a reduced flow through the cooling trains was issued“. Subsequently, due to the drop in cooling flow, the reactor was shut down in an emergency. The operator performs a status check, shift personnel announce potential fire in pump station and FRSU is activated. After the end of the HZS intervention, handing over the operator's workplace and carrying out the decontamination of the interveners; after ensuring monitoring, further necessary decontamination of premises.
CZ-C-99 | Austria | CZ | 02- Fire safety analyses | 40 | In this section, it is mentioned that the LVR-15 reactor has not been affected by a significant fire since the 1989 reconstruction and the last documented fire was in the reactor hall in the cable line, which was extinguished. How many fires have there been in the LVR-15 reactor facility in total? | The event was the burning in cable duct. As mentioned only that one during 35 years of operation.
CZ-C-100 | Austria | CZ | 03.1 - Fire prevention | 43 | It is mentioned that in the USSR, the basic requirements for fire safety were based on production categories only. Could you please explain what “Production Category” means? What is the relation of “Production Category” to “Safety Class”? | This is a division of objects into production and non-production, and conditions are set based on the evaluation. At present the FHA is made according to the Czech legislation. There is no relationship between the production category and the safety class.
CZ-C-101 | Austria | CZ | 03.1 - Fire prevention | 47 | Here it is noted that non-conformities detected are at a very low level (2022: 73/942). This does not sound low; it is 8% of the inspection. Could you please comment on the findings? | All mentioned findings are category 4 - findings of low relevance. A root cause analysis is not required and it is not necessary to involve multiple departments to resolve it. These are deficiencies, potential noncompliance, near misses. The examples are on page 47 „usually caused by human factors (e.g. improper storage of combustible materials, closing of fire doors) and are promptly corrected“.
CZ-C-102 | Austria | CZ | 03.1 - Fire prevention | 72 | The permanent fire water supply consists of a steel tank with a volume of 70 m3. On which basis was it determined that a 70 m3 tank volume would be sufficient for e.g. seismically induced fire extinguishing, in case the resupply is damaged by the same seismic event? | The volume of the tank was determined by a project prepared by an authorized person in the FP field and is classified as selected equipment safety class 3 and is designed in seismic resistance category 1b.
CZ-C-103 | Austria | CZ | 03.2 - Active fire protection | 78 | It is stated that protected piping is not required for the supply system tubes, which filters outdoor air containing radioactive aerosols for the control room when necessary, and does not need to be used for fire sectioning for the following reasons. The system is only operational when the outdoor air is contaminated with radioactive substances. This seems to imply that an event with a release of radioactivity (e.g. radioactivity in ambient) and a simultaneous fire are deterministically excluded. On which basis was such an exclusion justified? | In the FHA, a fire is not considered to occur simultaneously with non-fire related failures in safety systems, plant accidents, or the most severe natural phenomena, except the loss of off-site power (IAEA TECDOC-1977, VIENNA, 2021).
CZ-C-104 | Austria | CZ | 03.2 - Active fire protection | 79 | The report mentions that the parallel installation of different divisions of cable routes of the secured power supply systems in compartments without separation by construction with fire resistance of at least 90 minutes is assessed and evaluated in detail in special documentation "engineering solutions". In how many cases does such a situation of multiple redundancies in one fire compartment occur? What are typical “engineering solutions” to assure power supply to redundant trains in a case of fire in such rooms? | In total there are registered 245 cases where there is more than one divisional cable route in one section (room), requiring assessment. In these cases (concurrence of cable routes/cables belonging to several divisions), the following is assessed: • Functions of the cables participating in the concurrency • Design of cables • Transmitted power of the cables participating in the concurrency • Disposition (distances, geometry) of individual routes/cables participating in the concurrency • Installed technology in places of concurrency
CZ-C-105 | Austria | CZ | 03.2 - Active fire protection | 81 | Temporary measures to ensure the required fire safety are applied e.g. during shutdowns of fire safety equipment, repairs, modifications and maintenance. How often are such temporary measures activated on average (per unit and per years)? | Abnormal/temporary safety measures are set by the FRSU for approx. 20 times per year
CZ-C-106 | Austria | CZ | 03.2 - Active fire protection | 103 | In the report it is stated that the fire resistance of the pipe penetrations through the fire separating structures prove a certificate according to the approved test methodology from 1995. Has the test methodology for penetration been upgraded since 1995? As for the plant life extension, how does the life extension affect the penetrations and their testing in the sense of the fire resistance? How are those penetrations inspected in the course of life extension? | Currently, the operability check of fire partitions is assessed according to Act No. 133/1985 Coll. (a major amendment to the fire law took place in 2000) and Decree No. 246/2001 Coll. and according to the manufacturer's instructions. The ageing inspection is subject to AMP. BTW documents created in 1995 are subject to amendments in the view of legislation changes.
CZ-C-107 | Austria | CZ | 03.3 - Passive fire protection | 106 | It is stated that the Vltava River is used as the main source of firewater in the reactor hall with a total water supply of 14.000 liters. Is there any firewater tank available at the site? What does the 14000-liter volume for the reactor hall refer to? | The page 106 refers to LVR 15. The use of water in firefighting is limited as much as possible, inert substances are preferred - carbon dioxide, powder, CAFS - dry foam. Water only in extremely necessary cases and in small quantities (mist, splinter stream). The Vltava River is used as the main source of firewater in the area. According to the methodology for extinguishing fires, an extinguishing time of 10 minutes is considered, 14,000 liters is the amount supplied by all streams for a period of 10 minutes. The supply of fire water is inexhaustible thanks to the water source.
CZ-C-108 | Austria | CZ | 03.3 - Passive fire protection | 116 | The fire resistance of the penetration seals installed in critical areas is 90 minutes. Does this apply to both the piping and electrical (cables) penetration? How do you define “critical areas”, and how many critical areas are defined in each NPP unit? | Penetrations of pipeline routes through fire-dividing structures are fire-sealed with fire resistance complying with the requirements of ČSN. The fire resistance of the sealing of pipe penetrations in important spaces is 90 minutes and the sealing construction is designed to allow pipes dilatation. The fire resistance of hermetic grommets installed at the boundary of the containment is 90 minutes. It applies to all distributions and applies to all "important" objects calculated in FHA methodology. Dukovany NPP has 24, Temelín NPP 22 important objects
CZ-C-109 | Austria | CZ | 03.3 - Passive fire protection | 120 | In the report, it is mentioned that flammable air filters are designed in such a way that they cannot leak radioactive substances above the specified limits in the event of a fire. The filter is automatically separated from the rest of the channel by closing the air dampers. Are those dampers gas-tight ones? If so, to which over-pressure are those designed? E.g. for the main charcoal filter in the MCR clean-up system? | The filters are airtight and are rated for an overpressure of 6 kPa, based on national legislation.
CZ-C-110 | Austria | CZ | 03.3 - Passive fire protection | 120 | It is noted that part of the dampers are designed so that when a temperature of 130°C is reached, the damper blade is "baked" - sealed in the pipe. Which dampers are designed to have such a feature? | The dampers at the partitions which separate safety systems.
CZ-C-111 | Austria | CZ | 03.3 - Passive fire protection | 121 | The originally undivided reactor building is being divided into fire sections subsequently during use; the division is not complete and finished. What exactly is unfinished and when will it be finished? | The information was valid to the required date June 2022. The division of fire sections is finished as of 2024. Planned actions include revising the Fire Solution document and equipping some areas with Electrical Fire Detectors (EFD) to increase safety in fire protection (plan for 2024). Subsequently, the new EFD will be added to the existing documentation of the object.
CZ-C-112 | Germany | CZ | 02- Fire safety analyses | Regarding Temelin NPP, p. 21 | The NAR states on p. 21: "In 2011, a "Technical Assistance" document was prepared to examine the suitability and addition of Electrical Fire Detectors (EFD) in selected areas of the reactor and auxiliary buildings. A fire risk analysis was made for each room and, where values were exceeded for rooms without fire risk, the actual values were verified on site." Could you provide information on the criteria used for the analysis? Is there a minimum risk for fire detectors to be installed in the areas of the reactor and the auxiliary buildings? | The criteria for the analysis were the fire load values in the individual assessed rooms. The EFD system must be designed in fire sections in buildings listed in the technical standards or ČSN 730875.
CZ-C-113 | Germany | CZ | 02- Fire safety analyses | Regarding Temelin NPP, p. 22 | On p. 22, Algorithm for fire safety assessment Could you explain the meaning of the "coefficient of fire safety, k8"? How is the "equivalent fire duration" calculated? | The equivalent duration of the fire is calculated according to the ČSN, the equation includes parameters: fire load, ventilation, effect of fire safety devices, area of the fire section and head of the room of the fire section. k8 = the fire resistance safety factor of the building structure depending on the number of floors and the construction system of the building
CZ-C-114 | Germany | CZ | 02- Fire safety analyses | Regarding Temelin NPP, p. 28 | On p. 28, Sect. "2.1.A.6.2. Lessons learned from events, reviews, fire safety related missions", the sources for lessons learned are explained; however, examples for lessons learned are missing. Could you please provide examples? | Retrofitting of engine rooms - addition of fire extinguishing, increase of fire resistance of the perimeter wall, replacement of fire pumps. Minimization of oil leaks – over-sealing of fittings, slope/downgrade of draining pans.
CZ-C-115 | Germany | CZ | 02- Fire safety analyses | Regarding all installations, different pages, staring on p. 20 | The phrase "fire section" is used many times all over the NAR for different facilities. A definition could not be found. It is correctly understood that "fire section" could either mean "fire compartment" or "fire cell"? A clarification and distinction between "fire compartment" and "fire cell" would be appreciated. | The mixture of words "section" and "compartment" is basically caused by incorrect SW translation form Czech to English. The term "fire section" could either mean "fire compartment" in the internationally adopted vocabulary. Compartment itself is mostly a "part of a building" which need not be only "fire section". Fire cell is only used in sections with redundant equipment which can´t be effectively separated by structure.
CZ-C-116 | Germany | CZ | 02- Fire safety analyses | Regarding Dukovany NPP, p. 30 | On p. 30 of the NAR, regarding special cables like optic cables, coaxial cables "which could not be manufactured to meet the test according to IEC 332.3 category A in order to ensure their functionality, their resistance to the spread of fire is ensured by covering their entire length in steel tubes". How and against what type of scenario is this solution qualified? | The functionality of the affected cables is ensured by placing them in a non-flame-spreading plastic pipe, ensuring that the fire does not spread.
CZ-C-117 | Germany | CZ | 02- Fire safety analyses | Regarding Dukovany NPP, p. 33 | On p. 33, Sect. "2.1.B.6.2. Lessons learned from events, reviews, fire safety related missions", the sources for lessons learned are explained; however, examples for lessons learned are missing. Could you please provide examples? | Expansion of the EFD system, substitution of SES (e.g. Halon for NOVEC), spraying fire protection coating on steel structures.
CZ-C-118 | Germany | CZ | 02- Fire safety analyses | Regarding LVR 15, pp. 36-40 | The scope of the analyses covering also shutdown states during outages should be more clearly (and not only implicitly) addressed. | The shutdown state means that the rods are in the low end position and possible fire will not affect the change in its position even if the cabling to the drives and power supply is damaged - extraction of the rods is impossible. In case of cooling failure caused by fire during shutdown the followed water reheating and evaporation loss of water do not uncover core at least 3 days. In the event of a fire during the shutdown state, the scenario of a barrel with radioactive waste burning is being considered. This is assessed as not endangering the population.
CZ-C-119 | Germany | CZ | 02- Fire safety analyses | Regarding LVR 15, pp. 36-40 | Information on how the presence of permanent and temporary fire loads is considered and addressed in the fire safety analyses is missing. | The „permanent“ fire load affects the size and degree of fire safety of the fire section as given by the relevant technical standards and it is part of the Fire Solution of the building. The temporary fire load is subject to specific assessment case by case.
CZ-C-120 | Germany | CZ | 02- Fire safety analyses | Regarding LVR 15, pp. 36-40 | What is the reason for not considering the radiation hazard of a release from burning radioactive waste in the fire safety analysis? | Analysis of a burning barrel with RAW is part of the safety analysis and estimates unknown content. The radiation in the air is supposed to be same as during operation. Taking into account these the dose is under limits.
CZ-C-121 | Germany | CZ | 02- Fire safety analyses | Regarding LVR 15, pp. 36-40 | Detailed information on how the direct and indirect fire effects are assessed and which methods and data are used is missing. | In deterministic evaluation, fire is converted into events symptomatically as power loss - for these scenarios, a number of parameters are evaluated by computer programs - the most important of which is the temperature on the fuel surface and its comparison with the acceptance criteria.
CZ-C-122 | Germany | CZ | 02- Fire safety analyses | Regarding all installations, pp. 36-43 | Information on consideration of plant modifications in updates of the safety reviews and how they are addressed is missing. | Procedures for the evaluation of experiments and modifications are introduced to monitor these actions, where the description of the change is part of the documents for the evaluation of the safety commission, which member is also fire protection person. Following the assessment a procedure is subsequently determined for fire protection - supervision of work, change of documentation, fire prevention measures; conditions for carrying out activities etc.
CZ-C-123 | Germany | CZ | 02- Fire safety analyses | Regarding all installations, pp. 36-43 | Information in how far and how information from the operating experience regarding deterioration of fire protection features at the Czech installations reported in the NAR and from fire events at other nuclear installations applicable to the installations reported is applied in the fire safety analyses should be provided. | Considering the fact that research nuclear facilities are often unique in design - even in the case of facilities that were originally typical (such as reactors of the VVR-S type), direct transferability is often not possible due to changes during operation - experience is transferred in within working groups (typically e.g. RROG – Research Reactor Operation Group). Fire fighters are subsequently members of other groups for sharing experience within FRSs. LVR 15 operator take experience according to the ČEZ group (occurrence of events at nuclear-energy facilities) + fire protection conferences - according to set topics
CZ-C-124 | Germany | CZ | 02- Fire safety analyses | Regarding LVR 15, pp. 36-40 | The INSARR mission in 2020 revealed the need for fire hazard reduction (disposal of older technologies) and for comprehensive instructions for personnel response (emergency procedures and emergency instructions) also in case of fire. This statement needs some basic information for justification. | INSARR-type missions always include a tour of the workplace - in the case of the LVR-15 reactor, as part of the tour, it was recommended to remove older (unused) equipment from the technology, not to store material in the technology (e.g. air conditioning filters, etc.) and thereby reduce both the amount of material and, possibly, risk of fire. . The INSARR mission pointed out and recommended a more comprehensive procedure for the operator should be prepared so that the response to the event is easier - that is, the document for the response of personnel was modified, which contains according to event type links to other subdocuments.
CZ-C-125 | Germany | CZ | 02- Fire safety analyses | 36 | A PSA study is mentioned for LVR-15. Did you perform a full scope Probabilistic Safety Analysis (including Fire Analysis) for this research reactor? Could Czech Republic please provide information on the probabilistic analysis and the major findings? | Internal fire scenarios were incorporated into LVR-15 PSA study in 2023. The quantification will be processed in the PSA update in 2024.
CZ-C-126 | Germany | CZ | 02- Fire safety analyses | 40 | The inclusion of the internal FRSU in the region's alarm plans and the possibility of the unit's departure to the nearby surroundings to cooperate with the Regional FRS is identified as a good practice. Could Czech Republic please provide more information on the means and procedures at LVR-15 to guarantee the smooth cooperation between the FRSU and FRS? | The inclusion of the internal FRSU of the Research Instute Řež in the region's alarm plans is impossible due to limited number of personnel in site (4). There are organized common exercises with state FRS and also voluntary FRS of the village.
CZ-C-127 | Germany | CZ | 03.1 - Fire prevention | Regarding Temelin NPP, p. 42 | In the NAR on p. 42, under Chapter 3, 3A - Temelin it is mentioned that weak points were found in a 2003 study. However, the weaknesses were not mentioned. It was only reported that "None of these "weak points" relate to the potential impact of fire on nuclear safety." The weak points should be mentioned in some detail in order to allow the community to learn from each other. | Extinguishing in the bitumen area; Addition of a warning device for the presence of CO2 in the area equipped with Stable extinguishes; System of extinguishing turbogenerator and turbine powered feed water, pipe channels; Oil capture and collection system; Cooling system of load-bearing roof structures and equipment for heat removal, Increasing the fire resistance of the perimeter shell, including doors on in turbine hall and in the transformer area; Internal fire water supply in containment; Replacement of CO2 extinguisher agent with another type; Replacement of foam semi-stable fire extinguisher; stable fire extinguish in the simulator area; Extinguishing in warehouses; Semi stable and stable fire extinguish in electro control room; Suctioning the Pyrocool fire extinguisher into the stable sprinkler device in the oil storage areas in reactor building.
CZ-C-128 | Germany | CZ | 03.1 - Fire prevention | 44 | It is stated that the company's FRSU has a contract with Nuclear Research Institute Řež PLC. Is FRSU an internal fire department of LVR-15? Could Czech Republic please provide more information on the structure of fire fighting and involved parties? | FRSU has the status of a professional firefighting unit, the founder of which is ÚJV Řež, a. s. Firefighters work in FRSU as their profession. It is included in the Administration and Operation section, in the Security and Protection department.
CZ-C-129 | Germany | CZ | 03.1 - Fire prevention | Regarding Dukovany NPP, p. 51 | On p. 51, section "3.1.B.3.2. Lessons learned from events, fire safety related mission evaluations" the way findings are generated and treated is explained, but the findings itself are not reported. Could you please give some examples for findings? | Missing EFD detectors, low period for removal of oiled cleaning textiles.
CZ-C-130 | Germany | CZ | 03.1 - Fire prevention | Regarding Temelin and Dukovany NPPs, p. 80 | Could you add the fire specific characteristics of the turbine oil used? | Turbine oil MOL Turbine 32 K, Flash point (COC) (EN ISO 2592): temp. 220°C, not explosive, practically insoluble in water.
CZ-C-131 | Germany | CZ | 03.1 - Fire prevention | Regarding LVR 15 | What is the regulatory basis for conducting firefighting drills at least one per two years? | Legislation in the field of radiation emergency management requires regular (min. 1 x 2 years) exercises for relevant events referred to as radiation incidents - in the case of LVR-15 documentation, fires are also identified as sources of radiation incidents.
CZ-C-132 | Germany | CZ | 03.2 - Active fire protection | Regarding Temelin NPP | The frequently used "semi-stable" extinguishing equipment should be defined. It is understood so far as a piping system for fire extinguishing agents which need manual support. Could you comment and define? | A semi-stable extinguishing device (SSE) is a fire safety device that is firmly built into a protected building and has its own distributor of mobile equipment, to which firefighters with mobile fire equipment can be easily connected. There is air in the entire distribution of a semi-stable fire extinguisher.
CZ-C-133 | Germany | CZ | 03.2 - Active fire protection | Regarding both NPPs | The flow capacity of the fire water systems should be explained and for what scenario it is designed (e.g. the largest fire extinguishing system plus x water hoses). | The water system is designed to supply firewater to the stable extinguishing, sprinkling and cooling extinguishers to protect selected compartments of the reactor building that house safety system equipment and components. The system also supplies the internal high-pressure firewater distribution system for manual firefighting in the reactor building.
CZ-C-134 | Germany | CZ | 03.2 - Active fire protection | Regarding LVR 15 | There are no fixed fire extinguishing systems at LVR 15. What is the basis for justification? | The technical standard ČSN 73 0804 defines conditions for stable extinguishers based on fire load in section and its position in the building. The LVR 15 building does not fit to any of definition and is though excluded.
CZ-C-135 | Germany | CZ | 03.3 - Passive fire protection | Regarding Temelin and Dukovany NPPs, pp. 112 - 117 | On p. 112 (p. 117) of the NAR the actual fire resistance is reported to range from 15 to 240 min for walls and ceilings and from 15 to 90 min for doors and hatches. For fire dampers and fire seals (for pipework, cables) no actual fire resistance is given. How was the given fire resistance rating determined? Please provide information on the required fire resistance rating of fire barriers and their elements and the justification for that. Is the required fire resistance given by calculations or by prescriptive requirements? | Fire resistance is determined by the project, in which calculations are mainly used, but normative requirements are also used based on the value in the table, which is related to the degree of fire safety. The degree of fire safety depends on the structural system of the building, the fire load and the height of the building. The actual fire resistance must not be lower than that specified in the project.
CZ-C-136 | Germany | CZ | 03.3 - Passive fire protection | Regarding Temelin NPP, p. 115 | From p. 115 it can be read that fire dampers were only installed in the place of "penetrations of ventilation equipment smaller than 0.04 m2" depending on certain criteria. How is the max 0.04 m2 opening area is justified? The criteria mentioned for closing penetrations smaller than 0.04 m2 with dampers do not include structural protection of redundant trains. How is this considered? | This requirement is set in ČSN 730872 (air ventilation equipment with natural and forced air flow).
CZ-C-137 | Germany | CZ | 03.3 - Passive fire protection | Regarding LVR 15, pp. 123 | In the NAR it is written on p. 123 regarding fires close to the pump house: "A fire in any of these spaces can disable the cooling function for the prescribed 30 minutes." Could you explain why in case of such event the cooling function is restored after 30 min? | The limit of 30 minutes is taken as the minimum cooling time that must be ensured after shutdown. Thus, the events are assessed as to whether they are capable of causing a situation where cooling for 30 minutes will not be possible.
CZ-C-138 | Germany | CZ | 03.4 - Licensee's experience | Regarding all installations, pp. 124-125 | The two licensee's experience chapters are very unspecific and may be extended by examples. | Experience of the permit holder with the implementation of the fire protection concept is not based on examples as the concept is described in dedicated chapters. Specific examples are given in other chapters, in particular the expansion of fire safety devices and the increase of the level of fire protection.
CZ-C-139 | Finland | CZ | 03.2 - Active fire protection | 94 | Has another extinguishing agent been considered instead of CO2? | In the case of Temelín NPP when replacing CO2, the preparation for the replacement is for inert gas. In Dukovany NPP it is required by the design.
CZ-C-140 | Finland | CZ | 03.2 - Active fire protection | 79, 101 | How is the flooding induced by actuation of fire extinguishing systems considered? | Spaces that are protected by water-stable fire extinguishing systems are connected to the industrial drainage system, and in case of extinguishing, the water flows into the industrial drainage system and then to the cleaning water station. In the PSA, after a fire breaks out in the fire section, the inoperability of the equipment is caused by the fire. In in the PSA model, the inoperability of the equipment is not "duplicated" by flooding caused by the activation of the extinguishing equipment.
CZ-C-141 | Finland | CZ | 03.3 - Passive fire protection | 119-120 | Do fire dampers have the same fire resistance requirement as the penetrated fire-separating structure? | All fire dampers have a fire resistance of 90 minutes
CZ-C-142 | Finland | CZ | 03.3 - Passive fire protection | 120 | What is the structural separation between turbine hall and reactor buildings? Are there any systems important to safety located inside the turbine hall? | The reactor building is structurally separated from the turbine hall where also systems important for safety are incorporated in Temelín NPP. The reactor building is separated from the turbine hall by another object - horizontal shelf in Dukovany NPP.
CZ-C-143 | Poland | CZ | 02- Fire safety analyses | 40 | Was the potential aspects of gas generation from waste or spent fuel considered in the safety analyses? | From the point of view of fire protection, they were not evaluated. SFS has natural ventilation in storage part and forced ventilation in the rest of the building.
CZ-C-144 | Poland | CZ | 02- Fire safety analyses | 56 | Was the cliff-edge effect taken into consideration in the fire safety analyses? | As part of the deterministic analyses, the fire scenarios are converted to events associated with the power failure of individual devices up to the level of the scenario for DEC - complete loss of power. All scenarios will be included in PSA study in 2024.
CZ-C-145 | Slovakia | CZ | 01-General information | page 17; chapter 1.2.2 and throughout the report | 50 - SG - D2 rev.1 was valid from 1992 to 2004 and is now invalid. In 2004 it was superseded by NS-G.1.7. Since 2021 NS-G-1.7 has been superseded by SSG-64. SSG - 64 and SSG - 77 are safety standards currently in force for fire safety.The report needs to be assessed in the context of currently applicable safety standards and corrected as necessary. | The binding legal Czech documents are the Acts, the Decrees and the Government´s Orders published in Collection of Laws, together with the Czech Technical Standards (ČSN), if listed in the law. The NAR is prepared on that base. IAEA SSG are adopted in the Czech regulatory framework as recommendations, typically as SÚJB Nuclear Safety Guides (listed in chapter 1). The NAR mention the IAEA safety guide 50-SG-D2 as used for the fire protection of Dukovany and Temelín original assessment.
CZ-C-146 | Slovakia | CZ | 03.2 - Active fire protection | page 25; chapter 2.1.A.4 | In the case of an oil leakage between the 1st and 2nd section of the low-pressure of a steam turbine, one of the worst outcomes is an oil leakage into the insulation, which is not listed in the report. Only an oil leakage from a +15m to a -8.20m floor is indicated. | The FHA describes the most complex variant of the fire, in which the fire spreads in the building from the +15 m floor to the -8.2 m floor, and FRSU must use special extinguishing agents and procedures to extinguish it. Oil leakage into the insulation was not evaluated as the most complex variant of a fire in the building.
CZ-C-147 | Slovakia | CZ | 03.2 - Active fire protection | page 39; chapter 2.2.6.1 | Is Halotron allowed to be used as a fire extinguishing medium in the Czech Republic? If it is banned, is there a replacement and a recycling process ready, or underway? | In general, technological and highly demanding ecological requirements are currently met by such extinguishing agents that are made by mixing several chemical individuals and their resulting quality are usually better than these of the individual components. This group also includes new extinguishing agents of American origin, HALOTRON I and HALOTRON II, products of AMERICANPACIFICCORP. The recycling process is regulated by Ministry for Environment

## STAKEHOLDERS
Question ID | Reviewer (Country authorities; organisation name, etc) | Country/NAR | Chapter and relevant section of TS | Page no. in NAR (if specified) | Question - General (including generic/general experts' questions for type of installation) | Country's response | Cross reference to to another question-reply (Question ID) | Any remarks
CZ-S-42 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2 | 20 | “The assessment presented in the Operational Safety Analysis Report includes a set of postulated initiating events, which take into account the nature of the event, the type of occurrence and the frequency of the event occurrence. Initiating events include internal and external fire events.” -Is an aircraft crash included in the external events considered for all nuclear facilities in the Czech Republic? | The aircraft crash is included in the external events considered for all nuclear facilities in the Czech Republic
CZ-S-43 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 4 | 126 | Is the safety culture evaluated with regard to fire protection in nuclear facilities? If so, how is this assessed in the respective facilities? | Fire or its effect on operation and consequences are a typical operational event according to Decree No. 21/2017 Coll. that defines the events that must be reported to the SÚJB and a fire in the installation is included. The Decree requires an analysis of the event causes based on investigation and, in general, for operational events, the impact on nuclear safety culture. Such an assessment performs the operating company and subsequently any event is assessed by special SÚJB inspection.
CZ-S-44 | HAEA (Hungarian Atomic Energy Authority) | CZ | 01- General information | Page 8. | How are the commonly shared resources (e.g., onsite fire brigade, common drills, etc.) shared between the installations? | There is regular communication between the Temelín and Dukovany sites, and both inform each other about unusual events with impacts on fire protection. Fire fighters are members of specialized groups for sharing experience within Czech FRS and participate in fire protection conferences - according to set topics. Operators take experience according to the ČEZ group; LVR 15 also consider occurrence of events at nuclear-energy facilities.
CZ-S-45 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 01- General information | 1 | The "Joint Project - Nuclear Risk & Public Control" submitted today a long list of questions for CZ, HU, BG and PL via the survey support form. Sorry but it was not possible to put our questions in your form. I kindly ask you to verify that you received our list and will consider it in the consultation. Thank you! | ANSWERS FOLLOW
CZ-S-46 | HAEA (Hungarian Atomic Energy Authority) | CZ | 02- Fire safety analyses | Page: 36 | 2.2.3. Fire phenomena analyses: overview of models, data and consequences Question: How are the on-site or off-site fire departments/brigades taken into account in the fire safety analysis. | Fire risk is taken into account: permanent and accidental fire load, structural system – flammable, non-flammable and mixed, height of the building, area of fire section, ventilation parameter, size of fire-opened areas, presence of fire safety devices EFD, stable extinguishers, devices for smoke and heat outlet, by the presence of the FRSU.
CZ-S-47 | HAEA (Hungarian Atomic Energy Authority) | CZ | 02- Fire safety analyses | Page: 32 | 2.1.B.5. Periodic review and management of changes Question: What regulation/regulations set the requirements for Fire PSA and Deterministic Fire Hazard Analysis? | General requirements are defined by Atomic act and Decree No. 162/2017 Coll. on safety assessment. The requirements for fire PSA are further set in the evaluation of external hazards (external hazards), which are listed in the SÚJB Safety Guide BN-JB 2.5 - probabilistic safety assessment and in use is also IAEA SSG-3 - Development and Application of Level 1 Probabilistic Safety Assessment for Nuclear Power Plants.
CZ-S-48 | HAEA (Hungarian Atomic Energy Authority) | CZ | 02- Fire safety analyses | Page: 31 | 2.1.B.4 Main results / dominant events (licensee´s experience) Question: Were there major fire events at the Dukovany NPP that was taken into consideration in modifications (engineering or administrative) and/or had an effect on the fire safety assessment? | During the operation of the Dukovany NPP, there was only one significant fire, which happened in 1994 – the transformer station fire. On the basis of this fire, EFD and SSE were built on all transformers, individual transformers were fire separated from the surrounding area.
CZ-S-49 | HAEA (Hungarian Atomic Energy Authority) | CZ | 02- Fire safety analyses | Page: 30 | 2.1.B.3. Fire phenomena analyses: overview of models, data and consequences Acc. WENRA SV 6.2: “The extent of reliance on on-site or off-site fire brigades shall be shown to be adequate in the fire hazard analysis.” Question: How are the on-site or off-site fire departments/brigades taken into account in the fire safety analysis? | Fire risk is taken into account: permanent and accidental fire load, structural system – flammable, non-flammable and mixed, height of the building, area of fire section, ventilation parameter, size of fire-opened areas, presence of fire safety devices EFD, stable extinguishers, devices for smoke and heat outlet, by the presence of the FRSU. The fire risk assessment evaluates possible events and compares the forces and resources of the FRSU. In case of insufficiency of forces and resources, measures are proposed to fulfill them. Fire brigades outside the power plant area are only taken into account in case of effective deployment.
CZ-S-50 | HAEA (Hungarian Atomic Energy Authority) | CZ | 02- Fire safety analyses | Page: 26 | 2.1.A.5. Periodic review and management of changes Question: What regulation/regulations set the requirements for Fire PSA and Deterministic Fire Hazard Analysis? | General requirements are defined by Atomic act and Decree No. 162/2017 Coll. on safety assessment. The requirements for fire PSA are further set in the evaluation of external hazards (external hazards), which are listed in the SÚJB Safety Guide BN-JB 2.5 - probabilistic safety assessment and in use is also IAEA SSG-3 - Development and Application of Level 1 Probabilistic Safety Assessment for Nuclear Power Plants.
CZ-S-51 | HAEA (Hungarian Atomic Energy Authority) | CZ | 02- Fire safety analyses | Page: 25 | 2.1.A.4 Main results / dominant events (licensee´s experience) Question: Were there fire events at the Temelin NPP that was taken into consideration in modifications (engineering or administrative) and/or had an effect on the fire safety assessment? | Yes – retrofitting of engine rooms: TG and TBN extinguishing, increasing the fire resistance of the engine room walls, modernization of the CO2 extinguishing system of the oil management.
CZ-S-52 | HAEA (Hungarian Atomic Energy Authority) | CZ | 02- Fire safety analyses | Page: 25 | Acc. WENRA SV 6.2: “The extent of reliance on on-site or off-site fire brigades shall be shown to be adequate in the fire hazard analysis.” Question: How are the on-site or off-site fire departments/brigades taken into account in the fire safety analysis? | Fire risk is taken into account: permanent and accidental fire load, structural system – flammable, non-flammable and mixed, height of the building, area of fire section, ventilation parameter, size of fire-opened areas, presence of fire safety devices EFD, stable extinguishers, devices for smoke and heat outlet, by the presence of the FRSU.
CZ-S-53 | Hungarian Atomic Energy Authority | CZ | 03.1 - Fire prevention | 57 | Are there internal regulations at the LVR-15 facility to limit and control the transport of combustible and flammable materials and substances into the facility? Are these activities and the amount logged, checked, etc.? | Directive OSM 18 is used for the registration of dangerous substances, including flammables. A shared table is created for keeping information on the current amount of hazardous substances. Every year the lists are checked and the purchase of new substances is part of the approval procedure for the purchase of chemical substances. The FRSU is involved in the approval process. Transportation of dangerous substances is part of process management and is subject to registration/approval.
CZ-S-54 | Hungarian Atomic Energy Authority | CZ | 03.2 - Active fire protection | 106 | Are there regulations in force for the LVR-15 facility that require specific temporary measures to be taken for example during occasional flammable activities or work involving dust/smoke generation? If so, how are these requirements met? | Plans and analyzes are prepared for buildings - Fire Safety Solutions for buildings. It describes in detail preventive fire measures such as escape exits, resistance of building structures, determination and scope of fire technology and other safety and technical information including fire load analyses. According to the assessment of temporary fire load, a procedure is subsequently determined - supervision of work/change; change of documentation; fire prevention measures; conditions for carrying out activities etc. Procedures for evaluating experiments and modifications are in place to monitor these actions.
CZ-S-55 | Hungarian Atomic Energy Authority | CZ | 03.3 - Passive fire protection | 124 | Could you provide details on the fire sectioning and applied passive fire protection solutions (e.g.: fire retardant coating on cables)? | Buildings are divided into fire sections and fire cells by the design. Fire section – area of a building, separated from other parts of this building, or from neighboring buildings, fire separation structures or fire safety equipment - is the basic assessed unit from the point of view of fire safety of buildings. Passive fire protection - the aim of this protection is to stop or slow down the spread of fire in the building by closing and sealing openings and passages through which this spread can occur (non-combustible fire walls, fire penetrations, fire coatings, etc.) Cables with reduced reaction to fire and limitation of flame spread are used in SFS, therefore coatings are not used here
CZ-S-56 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 1.1.2 | 9 | “From the candidate nuclear installations, the SÚJB selected those with the potential for significant radiological risks to the environment and the population caused or affected by fire, to enable a meaningful comparison of the level of fire protection provision and the feasibility and quality of the assessment.” -Why was the newer SFS Temelin selected for the assessment and not the older SFS Dukovany? | The legal requirements and design/construction essential features are the same, regardless the time of construction of dry SFS. The same permit holder ČEZ, a. s., equal requirements, measures and procedures. The SFS has been described in NAR however it is not individual nuclear installation as it is localized in the site of NPP.
CZ-S-57 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 1.1.3 | 12 | “The LVR-15 is a tank-type light water research reactor housed in a non-pressurized stainless steel vessel under a shielding lid with forced cooling. The reactor uses IRT-4M type fuel with 19.7% 235U enrichment and an operating thermal power of up to 10 MW.” -What beyond-design-basis accidents are possible for this reactor? It should be taken into account that it uses fuel with relatively high enrichment and therefore the radiological consequences could be comparatively high. | For the DEC events, the complete loss of working sources of electric power supply, the step input of reactivity of 0.7 β, the loss of the coolant of the primary circuit due to leakage through the hole with cross-sections of 4 cm2 and 8 cm2 and the loss of the final heat sink without pumps of the primary circuit are selected as initialization events. Furthermore, there is the loss of coolant of the primary circuit due to the detachment of the horizontal channel and the complete blocking of one fuel assembly. The use of uranium enrichment of approx. 20 percent does not represent an increased risk - the radiological consequences are determined by the inventory of radioactive substances in the fuel and this is rather proportional to both the total amount of fuel and the level of burnout. Due to operation under atmospheric pressure (open vessel) there is no risk of phase transformation of the coolant during a LOCA type event etc.
CZ-S-58 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 1.2.2 | 16 | Are the current valid WENRA Safety Reference Levels for a) Existing Reactors, for b) Existing Research Reactors, for c) Waste and Spent Fuel Storage and for d) Decommissioning Safety included in the national regulations? And are they already applied in the safety assessment of all nuclear facilities, if not, when will they be applied? | Any WENRA valid SRL is included in the Czech legislation. WENRA SRLs for NPPs and RRs (if relevant) are appropriately implemented in the Czech „nuclear legislation“ since 2017.
CZ-S-59 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 1.2.2 | 17 | “Internal feedback system provides inspectors involved in inspections by information of operational events and the results of their investigations in their area of expertise. In addition to the inspection of the actual feedback process, inspectors review the progress and analysis of the checked events. “ -What are the main results of these inspections? | Inspections focused on internal feed-back system are performed quarterly at both NPP (8 inspections per year). The investigation and analyses of selected operational events are reviewed. It can be summarized that in several cases the SÚJB requires further investigation of the event and root causes or the addition of corrective measures. In rare cases, a new analysis of the operational event is required.
CZ-S-60 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 1.2.3 | 19 | “The scope of the state fire supervision enforcement: ….Identifying the causes of fires.” -What are the main causes of fire events? | In the Czech Republic, according to the statistics of the FRS CR, the most common causes of fires are carelessness and technical failure. The main cause of the fire in Dukovany NPP (5 during the entire period of operation of almost 40 years) was a technical fault.
CZ-S-61 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2.1 | 20 | Are beyond-design-basis fires for the NPPs possible? What would be the radiological consequences, if any? | PSA does not differentiate between project and beyond-design-basis fires. The PSA output is the frequency of individual scenarios leading to a leak. In FHA the most complicated fire is assessed.
CZ-S-62 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2.1.7.1 | 34 | “In accordance with the requirements of the SÚJB, a basic set of operational safety indicators is defined, including: -Unit availability factor - Fuel reliability - Number of INES events - Number and severity of failure events - Unplanned loss of power factor - Containment tightness - Number of fires in the NPP area ….” -Since when are these indicators determined? What are the results and trends of the indicators for the 6 reactors in the Czech Republic? | The first set of Safety Performance Indicators was created and the first evaluated year was 1991. The following knowledge and experience gained from regular evaluations resulted in a revision of the file. The annual evaluation is published on SÚJB web page in the Czech language.
CZ-S-63 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2.1.A.3 | 25 | “The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 13.6% level.” -What are the CDF results for Temelin 1 and 2 according to the latest PSA? What is the date of the most recent calculation? What contribution is made by fire events to the frequency of beyond design-basis accidents or accidents involving the release of radioactive substances? | The contribution of internal threats, and thus also the contribution of internal fires, to the overall risk is evaluated annually and reported in the Operational Safety Analysis Report (PrBZ). For 2022, the contribution from internal fires to FDF (Fuel Damage Frequency) was 12.95%.
CZ-S-64 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2.1.A.4 | 25 | How many and which kind of events/failures per year of the fire protection equipment have been occurred? | Temelín NPP: 68 failures were recorded on the EPS system, 10 failures were recorded on the fire water system and 19 malfunctions were recorded in the air-conditioning system in 2023. Due to the scale of these systems and the number of components, there are one per thousand failures.
CZ-S-65 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2.1.A.4 | 26 | “A. The measures to eliminate the most dangerous fire scenario in the area of sufficient forces and resources compared to the guaranteed 1st level of fire alarm for the given area confirms the necessity to establish the Fire Rescue Service Unit in the Temelín NPP (FRSU). B. The minimum member of this unit shall not be less than 12 personnel per shift continuously ready to respond to an emergency.” -This requirement applies to Temelin, is there a comparable requirement for Dukovany? | The number of members of the FRSU is given by the "Assessment of fire risk" and, as stated in other chapters, the minimum number is 12 on the day shift and 11 on the night shift in Dukovany NPP.
CZ-S-66 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2.1.B.3 | 30 | Dukovany NPP: “The contributions of internal fires to the overall risk of unit operation are generally of little importance. The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 20.3% level.” -What are the current CDF results for the 4 units of the Dukovany NPP? -When was the last PSA carried out? -What contribution is made by fire events to the frequency of beyond design-basis accidents or accidents involving the release of radioactive substances? | The PSA model is updated regularly as part of the Living PSA, the risk assessment is carried out continuously, and once a year the summary results are presented in Chapter 19 of the Safety Analysis Report. The mentioned value is the share of internal events caused by fires in the total value of Core Damage Frequency = 3,42E-06. Contribution to LERF value is 5,8% (2,4E-08).
CZ-S-67 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2.1.B.4 | 31 | How many and which kind of events/failures per year of the fire protection equipment have occurred? | The SÚJB record in database approximately 3 fire protection related event per year per NPP - fire protection equipment malfunctions majority of which is false activation.
CZ-S-68 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2.2 | 36 | Are beyond-design-basis fires possible? What would be the radiological consequences, if any? | The FHA describes the most complex variant of the fire
CZ-S-69 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2.2.6.2 | 40 | LVR-15: “The last documented fire was in the reactor hall in the cable line, which was extinguished without limiting the operability of safety-significant equipment and the affected portion of the cable line was repaired.”. -What was the reason for the last fire mentioned and when did it happen? How many fires have occurred since the start of operations? | The fire in the cable bridge was in a location outside of safety-relevant components - the event occurred on an older part of the cable line in the hall (not made in a non-fire-spreading design). There are no further records of fires in reactor technology.
CZ-S-70 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 2.4 | 40/41 | “The analysis of a deliberate attack by a large transport aircraft on a SFS falls into the category of extended design conditions and meets the requirements of a realistic approach. Application of a conservative approach in the form of "largest existing aircraft" is not required. The analyses performed indicate that the mechanical effects of the accident are not of such magnitude as to cause the spent fuel package leakage.” -What assumptions are made for this aircraft crash with regard to the type of aircraft, the fire temperature and the duration of the fire? What are the radiological results of this analysis? -Can radiological effects due to the thermal effects of the fire be completely ruled out? -Are the results for both SFS facilities in Dukovany the same? | The NPP´s PSA does not consider a deliberate attack by an airliner, only an accidental crash. The construction of SF transport and storage package is subject to special type approval and tests which are in accordance with Decree No. 379/2016 Col. The Decree implements all requirements of EU Directives valid in this area, international transportation rules (UN, RID) or IAEA Safety Standards Series No. SSR-6.
CZ-S-71 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.1 | 44 | -What experiences have been made since the start of operation, when and where have fires occurred and what was the cause in each case? | Since start of operation (in 2001) 9 fires occurred in Temelín NPP, majority was technical failure or personnel carelessness.
CZ-S-72 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.1.A | 44 | A typical cause of internal fires in NPPs is a short circuit in an electrical component or due to ageing cable insulation. Have fires already occurred due to this cause? How are fires from this cause prevented? | Only self-extinguishing cables with increased resistance to flame propagation (ČSN EN 60332-1, ČSN EN IEC 60332-3-22) are allowed to be used in the objects of the main production unit (in listed objects). Safety cables shall comply with ČSN IEC 60331. Cable penetrations through fire separation structures are fireproof sealed.
CZ-S-73 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.1.A.3.2. | 47 | -Have all recommendations and suggestions from the last OSART mission been fully implemented for Temelin? How many recommendations have been given? | 8 recommendation were issued by OSART mission and all are implemented.
CZ-S-74 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.1.B | 48 | A typical cause of internal fires in NPPs is a short circuit in an electrical component or due to ageing cable insulation. Have fires already occurred due to this cause? How are fires from this cause prevented? | Only self-extinguishing cables with increased resistance to flame propagation (ČSN EN 60332-1, ČSN EN IEC 60332-3-22) are allowed to be used in the objects of the main production unit (in listed objects). Safety cables shall comply with ČSN IEC 60331. Cable penetrations through fire separation structures are fireproof sealed.
CZ-S-75 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.1.B | 49 | Dukovany “When it is not possible to locate redundant equipment and components of safety systems or safety-related systems in separate fire sections (containment, control room, emergency control room, cable space under control room, etc.), fire protection systems shall be designed to limit the spread of fire in these fire sections and to eliminate unacceptable effects of fire or the fire protection systems themselves on the redundant safety systems.” -Which redundant safety system equipment and components are not located in separate fire sections? | From the point of view of safety systems, it is mainly the outlet of pipeline routes. Within the hermetic space, the fire separation of the individual divisions is carried out using fire cells. The cable ducts in the hermetic space are separated from it by fire separation structures. A stable fire extinguisher is located in the areas with the greatest fire risk
CZ-S-76 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.1.B.2 | 50 | Dukovany: “In all nuclear safety-relevant buildings, power cables and most low-current cables are of a design with increased resistance to the spread of fire, complying with IEC 332.3 category A, or IEC 331. c) In the case of special cables (optic cables, coaxial cables) which could not be manufactured to meet the test according to IEC 332.3 category A in order to ensure their functionality, their resistance to the spread of fire is ensured by covering their entire length in steel tubes.” -Which low-current cables are not of a design with increased resistance to the spread of fire, complying with IEC 332.3 category A, or IEC 331? | Mainly cables from construction phase (thermometers, pressure gauges, cabling from I&C stands), telephone, radio, company radio, accurate time, data network cabling. Optical, coaxial cables of computer network.
CZ-S-77 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.1.B.3.2 | 51 | Have all recommendations and suggestions from the last OSART mission been fully implemented for Dukovany? How many recommendations have been given? | The last OSART mission was held in Dukovany NPP in 2013 and issued no recommendation related to fire protection.
CZ-S-78 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.2.A.2 | 65 | Are the fire extinguishing systems of Temelin designed to withstand earthquakes? | In main operational units are seismic resistant extinguishers. Seismic-resistant is stable sprinklers systems and distribution of high-pressure pipelines in the reactor building and PHZ of system diesels. The requirement is that they maintain functionality even during a seismic event.
CZ-S-79 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.2.B.2 | 89 | Are the fire extinguishing systems of Dukovany designed to withstand earthquakes? | Safety important equipment is protected by stable extinguishing equipment with seismic resistance.
CZ-S-80 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.2.C.2 | 106 | Are the fire extinguishing systems designed to withstand earthquakes? | Firefighting equipment and EFD are not seismically qualified.
CZ-S-81 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.2.D.2 | 111 | Are the fire extinguishing systems designed to withstand earthquakes? | Based on FHA there are no stable extinguishing systems in the SFS. The building has a hydrant distribution of fire water, which is not seismic resistant.
CZ-S-82 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.4 | 124 | Are the components of fire extinguishing systems, fire alarm systems and fire dampers in the aging management program included? If yes, since when? What are the results, how many ageing effects have occurred in these components? Are there any trends to be observed? | The requirements of Aging Management Program (AMP) for research reactors were introduced by legislation in 2016. The program includes the EFD in buildings, fire dampers and fire water distribution of the building. For these devices, the AMP defines condition monitoring methods, acceptance criteria (activity/functionality test form and required result) + selected preventive measures to minimize aging. In 2019, the central switchboard, located in the FRSU building, was replaced; in 2020, the main hydrant water supply (service) was reconstructed and part of the horizontal distribution lines up to the supply to the reactor hall were reconstructed; in process is gradual replacement of selected parts based on regular tests and condition inspections results.
CZ-S-83 | Joint Project - Nuclear Risk & Public Control (AT) | CZ | 3.4 | 124 | How many incidents/failures of fire detection and alarm components, fire extinguishing systems, fire barriers and ventilation systems have occurred in the different nuclear facilities to date? Can trends be observed over the last two decades? | The vast majority of EFD malfunctions are diagnosed by the system online (defects of detectors, input modules, etc.) System failure (affecting downstream equipment) did not occur. Non compliances in mechanical parts of extinguishing systems are detected in walk downs or functional testing (related with system ageing) were detected: e.g. in 2022 recorded 70, in 2023 recorded 35 in Dukovany NPP.

## TPR BOARD
Question ID | Reviewer (TPR team or EC) | Country/NAR | Chapter and relevant section of TS | Page no. in NAR (if specified) | Question - General (including generic/general experts' questions for type of installation) | Country's response | Cross reference to to another question-reply (Question ID) | Any remarks
CZ-T-9 | EC | CZ | 01-General information | N/A | What fire safety improvements/measures have you done/taken based on internal/external operating experience, if any? | Many measures after the Fukushima event were implemented also in fire protection measures – upgrading the FRSU station, additional equipment and mobile operating equipment, increasing the number of firefighters, diverse additional and mobile equipment technology for the company fire brigade (Diverse EFW System) or hydrogen recombiners. There are actively used external and internal feedback, in which is assessed the influence of external and internal events on the fire protection process.
CZ-T-10 | TPR Team | CZ | 01-General information | §1.2 | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)? | WENRA SRLs for NPPs and RRs (if relevant) are appropriately implemented in the Czech „nuclear legislation“ since 2017. WENRA SRLs are not published in the Czech Legal Code as binding.
CZ-T-11 | EC | CZ | 03.1 - Fire prevention | 45 | What specific cable design to prevent spreading fire over power and control cables has been used? | Only self-extinguishing cables with increased resistance to flame propagation (ČSN EN 60332-1, ČSN EN IEC 60332-3-22) are allowed to be used in the objects of the main production unit (in listed objects). Safety cables shall comply with ČSN IEC 60331. Cable penetrations through fire separation structures are fireproof sealed.

## E309&311_ANSWER
1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these.
Screening criteria used in the fire analysis describes NAR in chapter 2.
2. Defense in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise:
a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)?
b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire?
c) Under these considerations, do you consider your Fire PSA conservative or realistic?
d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered?
e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way?
f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events.
g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events?
h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA.
a) In the analysis, it is assumed that the systems are functional and the FP units are operational.
In the deterministic analysis, the burnout of the fire section is calculated, with the fact that the fire must not spread from the affected fire section.
b) PSA considers, in most cases, the failure of all components in the affected fire section. Only for a few fire sections, the PSA model is more detailed and considers different probabilities of component failure in the affected fire section.
In the deterministic analysis, the burnout of the fire section is calculated, with the fact that the fire must not spread from the affected fire section.
c) PSA is conservative.
d) From the point of view of PSA, one of the basic inputs is the frequency of fire occurrence in the given fire section. The frequencies were determined on the basis of knowledge of the given fire sections, equipment in the fire section, fire load, etc. From the point of view of PSA, it does not matter if the fire was caused by a so-called simple fault.
In the deterministic analysis, a simple disturbance is considered. The most complex variant of fire in the building is expected.
e) In the PSA, false activation of signals during a fire, the so-called hot short, is considered, the fire section were assessed as for it. However, the model does not specifically include the false activation of extinguishing systems. Should a false start of an extinguisher cause an equipment inoperability or an initiating event, this will be reflected in the PSA when the PSA data is regularly updated.
The deterministic analysis does not account for false activation of signals and false activity of fire SCCs.
f) In the deterministic analysis, a combination of fires is not considered, but only one fire in the building.
g) A simple failure is expected. A subsequent fire is dealt with in the same way as the initial one.
h) PSA include all NPP states. Fire and its extinguishing is calculated in every unit mode.
3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources.
a) Provide details on the rationale followed.
b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified?
c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated?
a) This is a project solution according to ČSN.
b) The criteria are based on the Czech legislation and related binding technical standards – ČSN the majority of which is unified with European standards (EN).
c) This applies to all enclosed spaces. In the Czech standards, a ventilation parameter is calculated, which takes into account the ventilation of the space.
4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis?
If mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified."
Legislation and standardized requirements determine which cables are included in the fire load and which are not. If the cables are protected by fire coatings and these coatings are serviceable (fire prevention measures), they are not included in the fire load.
5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion?
Temporary combustibles and ignition sources were not included in the analysis as this is managed and registered by the Fire Protection Department – approval is necessary.
6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated.
In fire analyses, it is assumed that the fire that occurs in the fire section will not spread anywhere, which means that the structure, closures, penetrations, dampers and other fire safety equipment is designed to withstand the effects of the fire. Furthermore, it is expected that the equipment in the fire section will be destroyed. Therefore, redundant systems are placed in separate fire sections.
7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses?
Such fires are included in Fire Risk Assessment.
8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade.
The calculation of intervention time is included in Fire Risk Assessment.
9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable.
Protective measures are taken to prevent the occurrence of a fire, and if a fire does occur, the fire is detected immediately (within 60 seconds) and the FRSU workers arrive within 3 to 4 minutes of its notification. They will be equipped with appropriate extinguishers according to the firefighting documentation and can extinguish the fire immediately. Extinguishing is not considered in spaces with limited occupancy, where there are large dose rates - storage of highly active radioactive waste, where the fire burns out before unacceptable damage to building structures could occur (closed spaces without the possibility of fresh air intake).
10. Analytical methods:
a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description.
b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out.
c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects?
d) How are you facing to this (understanding of the corresponding studies by the stakeholders)?
a) Fire analyzes are always analyzed and calculated according to the fire load of each fire section. The values in the table are normative (ČSN).
b) Sensitivity and uncertainty are not reported in fire analyses.
c) Design solution is made strictly according to the Czech legislation and fire protection standards (ČSN).
d) The requirement „safety first“ is on the top level and it is valid as well in fire safety.
11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analyzed –and, as far as available, also from other nuclear installations– is considered in the fire analysis.
Fire analyzes are always analyzed and calculated according to the fire load of each fire section. The values in the table are normative (ČSN).
12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country?
Beyond design fire is not estimated.
13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about:
a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed.
b) Please provide results for the fire contribution to CDF / LRF / LERF.
c) The process carried out to update the fire analysis and the reasons for that.
d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified.
e) The use of the fire analyses by the regulator.
f) The influence of international reviews on the Fire Safety Analysis.
This is described in chapter 2 of NAR.
14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly
Not identified. Fire protection requirements are strictly regulated as prescribed.

## ALL CZECH
Question ID | Reviewer (TPR experts - AFP, PFP, FSA) | Fire Protection Thematic (for experts' questions) | Chapter and relevant section of TS (for experts' questions) | Installation name | Question - installation specific (experts' questions) | Country's response
CZ-E-304 | FSA | Fire safety analysis | Assumptions (TS 02.1) | Temelin | Can you please provide information in how far and how the different plant operational states (POSs) are considered in the deterministic fire safety analysis (chapter 2.1.A.1, 2.1.A.2, 2.1.A.3)? | The fire is assumed in all plant operational states
CZ-E-305 | FSA | Fire safety analysis | Assumptions (TS 02.1) | Temelin | p21 : Firefighting in bituminous areas : How is the risk from bitumen as fire load taken into account? (exothermic chemical reactions? 1997 Tokai Mura fire/explosion feedback?) P22 : Can you please explain what τe and k8 values are? | Measures are taken to prevent the occurrence of a fire, and in the event that a fire occurs, the fire is detected immediately (within 60 seconds) and the company's FRSU members arrive within 3 to 4 minutes of its notification. They will be equipped with appropriate fire extinguishers according to the firefighting documentation and can extinguish the fire immediately. Extinguishing is not considered in spaces with limited occupancy, where there are large dose rates - storage of high active radioactive waste. In such the fire burns out before unacceptable damage to building structures could occur (closed spaces without the possibility of fresh air intake). τe = equivalent fire duration in minutes, calculated in accordance to the Czech technical standard (ČSN). k8 = the fire resistance safety factor of the building structure depending on the number of floors and the construction system of the building
CZ-E-306 | FSA | Fire safety analysis | Assumptions (TS 02.1) | Dukovany | New deterministic fire safety analysis of all safety significant buildings exist. It remains unclear how the operational states are incorporated in the above mentioned analysis [2.1.B.2.]. | The fire is assumed in all plant operational states. In 2022, the FHA actualization was processed, operating conditions are not included here, fire protection must be ensured in all operating states.
CZ-E-307 | FSA | Fire safety analysis | Assumptions (TS 02.1) | Dukovany | p31 : The electrical Fire Detectors, where installed, is functional. Does this mean that the 3rd level of defence is not independent of the 2nd? Does this mean that the 3rd level of defence is not sufficient in the absence of detection? | The safety level is sufficient. Possible detector malfunction is signaled in control room as the control panel must signal to the operator at least three basic states: OPERATION, FAILURE, FIRE. Described on page 84 of NAR.
CZ-E-308 | FSA | Fire safety analysis | Licensee and regulatory experience | Temelin NPP | page 35, section 2.1.7.3 topic 2/ Which the period of periodic inspections on fire protection? Could you provide some identified weakness or non-compliences during the inspection? | Fire protection inspections are carried out at regular intervals according to the requirements of the legislation, depending on the inclusion of the building degree of the fire risk. Inspection intervals are once, twice or four times a year, depending on the level of risk. In important objects, inspections are carried out 4 times a year.
CZ-E-309 | FSA | Fire safety analysis | Licensee and regulatory experience | Temelin NPP | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified. | E309&311_ANSWER'!A1
CZ-E-310 | FSA | Fire safety analysis | Licensee and regulatory experience | Dukovany | page 35, section 2.1.7.3 topic 2/ Which the period of periodic inspections on fire protection? Could you provide some identified weakness or non-compliences during the inspection? | Fire protection inspections are carried out at regular intervals according to the requirements of the legislation, depending on the inclusion of the building degree of the fire risk. Inspection intervals are once, twice or four times a year, depending on the level of risk. In important objects, inspections are carried out 4 times a year. In addition to regular annual inspections of the operability of fire safety equipment, the following are carried out on the equipment during operation: 1x per month - activity tests for switchboards and related equipment, 1x every 6 months - tests of the operation of automatic fire detectors and equipment controlled by EFD.
CZ-E-311 | FSA | Fire safety analysis | Licensee and regulatory experience | Dukovany | [generic/general]: 1. Screening criteria used in the fire analysis for those NPP that have not explicitly identified these. 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the fire analysis for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA conservative or realistic? d) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? e) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the analyses? In what way? f) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. g) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards – such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding – considered? What are the qualification requirements ensuring their required function during and after these events? h) Consideration of the different Plant Operational States (POSs) and/or operating status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Qualification of cables: As far as qualified cables (typically FRNC) are available, in how far are they taken into account as fire load and fire source? How is the qualification of those cables been considered in the fire analysis and for what objective? In how far are protected cables (e.g., protected by protective coatings) considered as contributors to fire propagation in the fire analysis? 5. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 6. Direct fire effects: Are direct fire effects (either by smoke, pressure, temperature, soot, etc) onto SSCs important to safety considered in the fire analysis (including reliability of human actions, fire pressure effects on fire doors, fire overpressure effects on cascade flow and pressure gradients of the dynamic confinement system, …)? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 7. Electrical fires: Have electrically induced fires (including fires by high-energy arcing faults, HEAF) been considered in the fire analyses? 8. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 9. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 10. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 11. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 12. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for nuclear power plants in your country? 13. Results of the Fire Safety Analyses, revisions and actions: Please provide details about: a) A more elaborated description of the results of the analysis since for some plants the description is not very detailed. b) Please provide results for the fire contribution to CDF / LRF / LERF. c) The process carried out to update the fire analysis and the reasons for that. d) The procedure and responsibilities to design and establish compensatory measures when non-conformities or weaknesses have been identified. e) The use of the fire analyses by the regulator. f) The influence of international reviews on the Fire Safety Analysis. 14. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified. | E309&311_ANSWER'!A1
CZ-E-312 | FSA | Fire safety analysis | Assumptions (TS 02.2) | Research reactor LVR 15 | To 1/ (pp. 36-40): Can you please address the scope of the analyses covering also shutdown states during outages more clearly (and not only implicitly)? | The shutdown state means that the rods are in the low end position and possible fire will not affect the change in its position even if the cabling to the drives and power supply is damaged - extraction of the rods is impossible. In case of cooling failure caused by fire during shutdown the followed water reheating and evaporation loss of water do not uncover core at least 3 days. In the event of a fire during the shutdown state, the scenario of a barrel with radioactive waste burning is being considered. This is assessed as not endangering the population.
CZ-E-313 | FSA | Fire safety analysis | Assumptions (TS 02.2) | Research reactor LVR 15 | To p.36, 1/: Could you specify, if the PSA, especially fire PSA performed for LVR-15? If yes, what are the main contributors (events) and dominant contributes (or sequences for each considered event), and are any measures (except for emergency planning zone issues) identified based on the results? | Internal fire scenarios were incorporated into LVR-15 PSA study in 2023. The quantification will be processed in the PSA update in 2024. IE fires are: in primary pump place, DG station, battery room, electrical distribution room, developed fire in control room, reactor hall, ventilation center and external network shutdown caused by fire.
CZ-E-314 | FSA | Fire safety analysis | Licensee and regulatory experience | Research reactor LVR 15 | To 4/ (p. 40): b) The licensee mentions that the INSARR mission in 2020 revealed the need for fire hazard reduction (disposal of older technologies) and for comprehensive instructions for personnel response (emergency procedures and instructions) also in case of fire. Can you give some information on this? | INSARR-type missions always include a tour of the workplace - in the case of the LVR-15 reactor, as part of the tour, it was recommended to remove older (unused) equipment from the technology, not to store material in the technology (e.g. air conditioning filters, etc.) and thereby reduce both the amount of material and, possibly, risk of fire. . The INSARR mission pointed out and recommended a more comprehensive procedure for the operator should be prepared so that the response to the event is easier - that is, the document for the response of personnel was modified, which contains according to event type links to other subdocuments.
CZ-E-315 | FSA | Fire safety analysis | Licensee and regulatory experience | Research reactor LVR 15 | , p.40, 2/ The information on regulatory oversight, and inspections on fire safety was covered is missing. How often the periodic inspections on fire safety are performed? Is there any significant insight into fire safety from this inspection? | In the area of regulatory inspections, an FRS of the Czech Republic inspection of the condition was carried out in 2022 - without negative findings; a five-year plan is typical for such inspections. The company FRSU carries out 2 inspections of the EPS and walk down of the reactor building, and 1 inspection of fire extinguishers and wall-mounted hydrants and dry pipes annually, and inspections of the building are carried out twice a year.
CZ-E-316 | FSA | Fire safety analysis | Licensee and regulatory experience | Research reactor LVR 15 | [generic/general]: 1. Fire safety objectives: Not clearly stated. In particular, clarification is requested regarding the purpose of the deterministic fire risk assessment: has it been carried out with the purpose of protecting the lives of operators or of preventing nuclear accidents? 2. Defence in Depth (DiD): Regarding the level of fire DiD and the assumptions in the Fire Safety Analyses (FSA) the following questions arise: a) Has the failure of the fire protection means (features such as structures, systems and equipment, but also human failures in active fire protection) been taken into account in the FSA for the safety demonstration of the fire protection structures, systems and components (SSCs)? b) Both in the deterministic and probabilistic FSA, under which assumptions is this failure considered: full burnout in the fire area and failure of all SSC therein, functions of failure probability for the different SSCs, no damage due to the fire? c) Under these considerations, do you consider your Fire PSA (if applicable) conservative or realistic? d) Could you provide (in case a Fire PSA is performed) results in terms of CDF / LRF / LERF? e) Is the single failure criterion considered in the fire analysis? If it is, on which regulatory basis and how is it considered? f) Are the spurious actuation of signals by a fire and the false operation of fire protection SCCs considered in the fire analyses? In what way? g) Provide information on which combinations of fires and other events have been included in the fire analysis with their justification. Please refer to Appendix I of the IAEA SSG-64 to address possible combinations of events. h) With regard to these combinations of fires with other events in the analysis, is the failure of the fire protection features (for detection or suppression) caused by combined hazards –such as earthquake and consequential fire or a fire occurring coincidentally with a long-lasting external flooding– considered? What are the qualification requirements ensuring their required function during and after these events? i) Consideration of the different Plant Operational States (POSs) or of the operative status and modes in the deterministic FSA. 3. Fire resistance/fire hazard rating: The fire resistance rating of fire compartments, or fire hazard level, is often determined based on the fire load density (MJ/m²) in every fire area or compartment accounting for both permanent and transient fire loads and potential ignition sources. a) Provide details on the rationale followed. b) Fire load criteria values may differ amongst facilities and countries depending on the regulatory framework. How are these respective criteria justified? c) Are they justified knowing that fires in nuclear facilities are generally under-ventilated? 4. Transient combustibles and ignition sources: In how far and how have transient combustibles and ignition sources (by e.g. hot works) been included in the fire analysis and what are the hypotheses related to their inclusion? 5. Direct fire effects: Are direct fire effects (by smoke, pressure, temperature, soot, etc.) onto SSC important to safety considered in the fire analysis? Some detailed information about the regulatory requirements applicable and the way such effects are taken into account regarding design/conception/construction/modifications would be appreciated. 6. Fire Brigade: How have the response times of the fire brigade (onsite, offsite brigades) been taken into account in the fire analysis? This question is more relevant in those installations that do not have a dedicated onsite fire brigade. 7. Radiological consequences of fires: Please provide more details about the methods of addressing the radiological consequences of the fires in the fire analysis and the radiological criteria of acceptance and the corresponding threshold values applicable. 8. Analytical methods: a) For the installations that do not provide enough detail on the tools and models used in the fire analysis, please provide a more detailed description. b) In cases where computational tools have been used within fire safety analyses, provide information on the sensitivity and uncertainty analyses carried out. c) The use of calculation tools is growing. What are your review processes to identify the needs and advantages/disadvantages of adopting such tools? What are the outcomes of these prospects? d) How are you facing to this (understanding of the corresponding studies by the stakeholders)? 9. Management of temporary modifications and their impact on fire safety: A lot of temporary modifications are implemented at research reactors for performing experiments. These temporary modifications for experiments may increase fire loads in compartments, limit access to compartments or buildings, or even impact sequences of fire events if any. Could you please specify: a) Are, and how are the modifications (including those for incorporation of new experimental devices, launching new laboratories, etc.) considered in the fire safety analysis and the periodic safety review (PSR) updates? b) Is any fire safety analysis/assessment of temporary modification for experiments conducted before implementation (to assess the impact on the fire safety of the reactor)? c) Updates of the FSA and PSR: criteria and periodicity for their review. d) Sources to derive new modifications: FSA and PSR and their updates, operating experience, new regulation, etc. 10. Operating Experience: Provide a detailed description on if and how the operating experience from both (i) fires and (ii) other events (whether reportable or not) with degradation or failure of fire protection features in the installation analysed –and, as far as available, also from other nuclear installations– is considered in the fire analysis. 11. Additional analyses: Following the accident at the Fukushima NPP, stress tests were defined for European NPP. Has there been followed a similar approach regarding beyond-design-basis fire events for research reactors in your country? Please provide details. 12. Strengths/weaknesses: In cases that no strengths and weaknesses have been explicitly mentioned in the NAR, please confirm that neither strengths nor weaknesses have been identified. | 1. All analyses were performed in accordance with Decree 329/2017 Coll. on design requirements. Deterministic analyses showed that no fuel cladding damage occurs for any of the scenarios. 2. a) In the Fire Safety Resolution of the building, the resistance of individual fire section is indicated, which prevent the spread of fires to other fire compartments. In the event of a fire, an operational card is prepared, which contains information relevant to the intervention. The company fire brigade (FRSU) does not have the status of a member of the professional fire brigade units, therefore it is not obliged to intervene in a fire. If the activity of the FRSU is refused, 2. b) As part of the evaluation of a fire as an initiating event, the fire is converted to another initiating event - typically a loss of electrical power (DBA and DEC). It is included in deterministic FHA and in future PSA (end of 2024). 2. c) The LVR-15 reactor does not yet have a fire PSA finished; it is considered as conservative. 2. d) The current data results in neither of the possible scenarios results in a loss of fuel cladding. 2. e) In deterministic analyses, the response of the system to an initialization event is addressed. In deterministic analyses, the failure sequence is not implemented - an order function is considered for safety systems. However consideration is also made as to whether safety critical components/functions satisfy the simple failure criterion - i.e., whether, for example, there is only one measurement sensor that is essential to the event management. The PSA defines the project model in a more comprehensive manner, automatically including in the PSA cuts those which do not meet the "SFC" (if there were any), including more simultaneous failures in higher order cuts. 2. f) The FRSU always departs when an EPS is reported, even in the event of a false alarm.
CZ-E-317 | PFP | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Temelin NPP | page 46/Section 3.1.A.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 46/Section 3.1.A.2/3/ Describe how management and control of hot work is carried out (e.g in case of maintenance, modification...)? page 46/Section 3.1.A.2/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered? | In the case of a planned intervention/modification in technology or in the building, this plan is assessed by the FP department, which will determine the fire safety conditions. In the case of temporary storage of fire-hazardous substances, the amount of fire-hazardous substances and the storage location must be approved by the FP department. The FP department further determines the conditions of storage and the marking of areas in which fire-hazardous substances are stored. Before starting work with an open fire, the work implementer must obtain a permit of the FP department, where the FP technician will determine the safety requirements that must be observed during the performance of the activity in place. In the case of work with an open flame in places where there are flammable or fire-hazardous substances, a firefighter is present. In other cases works with open fire are inspected at random. Explosion protection is stipulated by legislation, where so-called explosive zones are defined. On the basis of the provided expert assessment, the areas where the explosive concentration of the so-called Ex zone is possible are determined. ATEX 2014/34/EU, in the Czech legal system the directive has the nature of Government Regulation.
CZ-E-318 | PFP | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Temelin NPP | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications. | The permanent fire load is determined by the nature of the space (office, warehouse, operation, workshop, etc.) and any flammable building structures (e.g. windows, doors, floor) and is based on standards. The temporary fire load is determined by the working activity and its needs (repairs, replacements, etc.). As part of the operation, the permanent fire load is reduced (if there is a replacement of non-flammable equipment, non-flammable windows, doors and floors are installed...), the temporary fire load is subject to the approval of the FP department and is monitored and limited. Permanent fire load is documented in the design, temporary in the database of the FP department. The permanent fire load must not be increased, temporary only up to the limit (approved by the FP department) Any information is in the database of the FP department. Limits for permanent load are given by the design and internal procedure (page 50) temporary load is limited to max 1kgm-2. Fire load checks are part of the preventive inspections of the building, the frequency is determined by the "Fire Risk Assessment", corrective measures are carried out without delay. Hot works are managed by an internal methodology and are subject to approval by the FP department, which checks compliance with measures both during and after the work. Roles and responsibilities are regulated in the permit. Inspections are focused on fire prevention and compliance. Before starting, the FP department evaluates the place of work with an open fire and proposes adequate measures according to the type of work, the place of work and the conditions at the workplace. Subsequently, checks are carried out to ensure compliance with the conditions, and after the work is finished, there is a site security check and checks aimed at preventing the occurrence of fire. Hydrogen is stored in separate building, isolated tubes transport it into generator. For the possibility of hydrogen occurrence in reactor hall there are installed passive autocatalytic recombiners (22 pcs). No major changes or adjustments were made to the hydrogen management.
CZ-E-319 | PFP | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Dukovany | page 50/Section 3.1.B.2/3/ Describe control and the minimization of ignition sources: chemicals reaction, explosive atmosferes (ATEX), high energy arcing fault (HEAF), hot spots, hot gas, overheating or failure of electrical or mechanical SSC, wrong human behavior? page 50/Section 3.1.B.2/3/ How is explosion protection (Ex zone, Ex equipment...) in connection with ATEX directives considered? | In the case of a planned intervention/modification in technology or in the building, this plan is assessed by the FP department, which will determine the fire safety conditions. In the case of temporary storage of fire-hazardous substances, the amount of fire-hazardous substances and the storage location must be approved by the FP department. The FP department further determines the conditions of storage and the marking of areas in which fire-hazardous substances are stored. Before starting work with an open fire, the work implementer must obtain a permit of the FP department, where the FP technician will determine the safety requirements that must be observed during the performance of the activity in place. In the case of work with an open flame in places where there are flammable or fire-hazardous substances, a firefighter is present. In other cases works with open fire are inspected at random. Explosion protection is stipulated by legislation, where so-called explosive zones are defined. On the basis of the provided expert assessment, the areas where the explosive concentration of the so-called Ex zone is possible are determined. ATEX 2014/34/EU, in the Czech legal system the directive has the nature of Government Regulation.
CZ-E-320 | PFP | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Dukovany | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications. | The permanent fire load is determined by the nature of the space (office, warehouse, operation, workshop, etc.) and any flammable building structures (e.g. windows, doors, floor) and is based on standards. The temporary fire load is determined by the working activity and its needs (repairs, replacements, etc.). As part of the operation, the permanent fire load is reduced (if there is a replacement of non-flammable equipment, non-flammable windows, doors and floors are installed...), the temporary fire load is subject to the approval of the FP department and is monitored and limited. Permanent fire load is documented in the design, temporary in the database of the FP department. The permanent fire load must not be increased, temporary only up to the limit (approved by the FP department) Any information is in the database of the FP department. Limits for permanent load are given by the design and internal procedure (page 46), temporary load is limited to max 1kgm-2 (EDU). Fire load checks are part of the FRSU preventive inspections of the building, the frequency is determined by the "Fire Risk Assessment", corrective measures are carried out without delay. Hot works are managed by an internal methodology and are subject to approval by the FP department, which checks compliance with measures both during and after the work. Roles and responsibilities are regulated in the permit. Inspections are focused on fire prevention and compliance. Before starting, the FO department evaluates the place of work with an open fire and proposes adequate measures according to the type of work, the place of work and the conditions at the workplace. Subsequently, checks are carried out to ensure compliance with the conditions, and after the work is finished, there is a site security check and checks aimed at preventing the occurrence of fire. Hydrogen is stored in separate building, isolated pipe routes transport it into generator. For the possibility of hydrogen occurrence in reactor hall there are installed passive autocatalytic recombiners (17 pcs).
CZ-E-321 | PFP | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | Temelin NPP | page 112/Section 3.3.A.1.2/ 1/Describe how the plant is divided into fire compartments and fire cells? Please define the terms: fire compartment, fire sections, fire cell? page 112/Section 3.3.A.1.1/2/ Are the fire resistances for fire barriers (fire walls, fire doors, fire dampers) for 15 minutes acceptible? Are fire resistance of fire barriers in compliance with national fire standards? page 113/Section 3.3.A.1.3/2/ How it is ensured that the expected fire resistance and stability ratings are fulfilled? | Buildings are divided into fire sections and fire cells by the designer, who proceeds according to applicable legislation. Fire section – area of a building, separated from other parts of this building, or from neighboring buildings, fire separation structures or fire safety equipment; Fire cell – a partial part of the fire section secured in an alternative way so that in the event of a fire, the fire remains limited only to the place of its origin and there is no unacceptable damage to other parts of the fire section. The principle of fire cells is applied to ensure the fire safety of fire sections containing systems, structures and components with an impact on nuclear safety. The basic assessed unit from the point of view of fire safety of buildings. Legislation/technical standards set the fire resistance of barriers to 15 minutes in 1st. degree of fire safety. After the realization of the work, the compliance with design requirements is proven by Protocols on compliance, Declaration of product quality and assembly protocols.
CZ-E-322 | PFP | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | Temelin NPP | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers? | The project deals with the division of buildings into fire sections, determines the fire resistance of individual structures, and determines the quantity, scope and location of individual fire safety devices. In the event of a change of use, the project is evaluated and measures are proposed to maintain or increase fire safety. The ventilation system is described in NAR.
CZ-E-323 | PFP | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | Dukovany | page 118/Section 3.3.B.1.2/1/ Describe how the plant is divided into fire compartments and fire cells? Please define the terms: fire compartment, fire sections, fire cell? page 118/Section 3.3.B.1.2/2/ How it is ensured that the expected fire resistance and stability ratings are fulfilled? | Buildings are divided into fire sections and fire cells by the designer, who proceeds according to applicable legislation. Fire section – area of a building, separated from other parts of this building, or from neighboring buildings, fire separation structures or fire safety equipment; Fire cell – a partial part of the fire section secured in an alternative way so that in the event of a fire, the fire remains limited only to the place of its origin and there is no unacceptable damage to other parts of the fire section. The principle of fire cells is applied to ensure the fire safety of fire sections containing systems, structures and components with an impact on nuclear safety. The basic assessed unit from the point of view of fire safety of buildings. After the realization of the work, the compliance with design requirements is proved by Protocols on compliance, Declaration of product quality and assembly protocols.
CZ-E-324 | PFP | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | Dukovany | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers? | The design deals with the division of buildings into fire sections, determines the fire resistance of individual structures, and determines the quantity, scope and location of individual fire safety devices. In the event of a change of use, the project is evaluated and measures are proposed to maintain or increase fire safety. The ventilation system is described in NAR.
CZ-E-325 | PFP | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | Temelin NPP | /Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences? | The ventilation ensure that the fire does not spread through the ventilation distribution. In the event of a fire, the ventilation is automatically shut down, except for the areas of the bitumen line, where fire ventilation is proposed. In the PSA, after a fire rise in the fire section, the inoperability of the equipment is caused by the fire. In the event of a fire, the loss of ventilation is not taken into account in the PSA model.
CZ-E-326 | PFP | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | Temelin NPP | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made? | The fire dampers regular inspection and maintenance set the manufacturer, it´s function is checked one per 12 month. In Temelín NPP there are non-accessible dampers.
CZ-E-327 | PFP | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | Dukovany | /Section 3.3.2.1/2/Describe how the loss of ventilation (because of fire) influence the operability of SSC important to safety? Describe scenarios in which the ventilation can be lost and what are consequences? | The ventilation ensure that the fire does not spread through the ventilation distribution. In the event of a fire, the ventilation is automatically shut down, except for the areas of the bitumen line, where fire ventilation is proposed. In the PSA, after a fire rise in the fire section, the inoperability of the equipment is caused by the fire. In the event of a fire, the loss of ventilation is not taken into account in the PSA model.
CZ-E-328 | PFP | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | Dukovany | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made? | Fire dampers are tested once per 12 month.
CZ-E-329 | PFP | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | Temelin NPP | Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements. page 124/Section 3.4/1/ Did you have OSART missions? What were lessons learnt from OSART missions? | During past 10 years there occurred 3 fires in Temelín NPP. Twice personal carelessness (2014 fire of sawdust particles ignited by red-hot nail while sawed wooden pallet in open space, 2019 fire of spilt diluent and smoke filled in FRSU building) and one fire cause was technical fault (2015 fire of hand-drier in medical center). The last OSART was in 2021. It has led to an improvement of training materials, increase of safety requirements in using heat appliances, addition of safety requirements when using flammable liquids.
CZ-E-330 | PFP | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | Temelin NPP | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? Which kind of deficiencies of active and passive FP SSCs in scope of aging management program were identified in last 10 years? Describe how these deficiencies were corrected (e.g. what kind of replacement, improvement or modifications? o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries). | NPP: Ageing management of fire passive and active SSC The fire protection equipment is included on the base of safety classification – safety class 3. Those include system stable sprinklers, selected fire dampers, EFD as defined. The detail on the ageing management system is fully described in previous NAR on TPR I. With regard to the complexity of the entire evaluation system and to ensure the required quality of the evaluation process of the systems and their equipment condition, common management documentation for both NPP is prepared. As part of the evaluation, LIVE data from a complex set of applications describing the operational history of the nuclear power plant across the professional focus is used. All fire protection equipment is subject to regular inspections procedures and checks. Any fire protection systems are subject to an annual operability check, and in case of unsatisfactory condition, they are repaired, modernized or replaced. Mapping and repair of original fire partitions, fire doors, fire dampers and fire piping. The evaluation of safety systems and safety-related systems takes place according to the established schedule. A HEALTH REPORT - Summary Report on the state of technological systems and components is prepared. OPEX According to the Czech legislation, every fire must be reported, the fire classification is carried out by a fire cause investigator who is a member of the FRS CR. Every fire is reported to the FRS of the Czech Republic, the exchange of experience about fires that have occurred takes place at conferences and at instructional methodical jobs between the commanders of FRSU (energy, automotive industry, chemical industry, airports, etc.) within the Czech Republic. There were no fires in our facilities that resulted in a significant improvement in FP. The Czech legislation is adjusted based on experience from domestic fires as well as world practice.
CZ-E-331 | PFP | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | Dukovany | page 124/Section 3.4/1/ What were lessons learnt from OSART missions? Please provide information about significant fire events and the derived operating experience of at least the last ten years. The information for each event should contain: description of the event, causes, consequences and improvements. | During past 10 years there occurred 2 fires in Dukovany NPP. In 2020 fire of fluorescent lamp resulted in replacement of lightings by equivalents. In 2023 fire in distribution box caused by technical failure. Preventive measure is in place - inspection of UPS and batteries by thermocameras and input of suction openings in operational cards.
CZ-E-332 | PFP | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | Dukovany | [generic] o NPP: Ageing management of fire passive and active SSC Describe which fire active and passive SSCs are covered by the aging management program. Describe in general the preventive actions to minimize and control ageing degradation on fire protection. Describe specifically how the aging management program covers/considers fire barriers, fire extinguishing system and the firewater distribution network. Describe in general the monitoring and trending of ageing effects on FP SSC? | The fire protection equipment is included on the base of safety classification – safety class 3. Those include system stable sprinklers, selected fire dampers, EFD as defined. The detail on the ageing management system is fully described in previous NAR on TPR I. With regard to the complexity of the entire evaluation system and to ensure the required quality of the evaluation process of the systems and their equipment condition, common management documentation for both NPP is prepared. As part of the evaluation, LIVE data from a complex set of applications describing the operational history of the nuclear power plant across the professional focus is used. All fire protection equipment is subject to regular inspections procedures and checks. Any fire protection systems are subject to an annual operability check, and in case of unsatisfactory condition, they are repaired, modernized or replaced. Mapping and repair of original fire partitions, fire doors, fire dampers and fire piping. Fire water is checked by a leak test and functionality check (flow rate The evaluation of safety systems and safety-related systems takes place according to the established schedule. A HEALTH REPORT - Summary Report on the state of technological systems and components is prepared. Based on the annual assessment of the state of the stable extinguishing equipment (SES) and stable sprinkler equipment (SSE) during regular prescribed revisions, it has long been found out that there is a gradual deterioration of its technical condition. Lack of spare parts for pumps, valves or pump´s motors (qualified for safety class 3). Technical obsolesce of fire dampers. Lack of fire protection coating equivalent. Leakage in fire piping buried underground. Delay of SSE forbidden agent replacement. Replacement of steel fire pipes with polyethylene pipes; replacements for stable halon extinguishing equipment – regulated substance HALON 1301 for the approved equivalent of NOVEC 1230); replacement of fire-fighting coating product DICO by other products (Flammoplast KS1 and DEKORLACK SP2); replacement of fire partitions.
CZ-E-333 | PFP | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Research reactor LVR 15 | Please provide more information on the practise of temporary fire load management. | Procedures for the evaluation of experiments and modifications are introduced to monitor these actions, where the description of the change is part of the documents for the evaluation of the safety commission, which member is also fire protection person. Following the assessment a procedure is subsequently determined for fire protection - supervision of work, change of documentation, fire prevention measures; conditions for carrying out activities etc.
CZ-E-334 | PFP | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Research reactor LVR 15 | It is declared that a special process in the management system has been implemented. What special process is used at LVR 15? | The management system program is part of the operation documentation. Within it, activities/processes are defined that can/are affecting nuclear safety, radiation protection, technical safety, etc. Among such processes, fire protection was also determined, and the description of the process specifies, beyond the scope of the company's fire protection documentation, responsibilities for selected parts of the process.
CZ-E-335 | PFP | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | Research reactor LVR 15 | [generic]: o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications. | Management of fire loads LVR The permanent fire load is determined by the nature of the space (office, warehouse, operation, workshop, etc.) and any flammable building structures (e.g. windows, doors, floor) and is based on standards. The temporary fire load is determined by the operation and its needs (repairs, replacements, etc.). As part of the operation, the permanent fire load is reduced (if there is a replacement of non-flammable equipment, non-flammable windows, doors, floors are installed...), the temporary fire load is subject to the approval of the FP department and is monitored and limited. Permanent fire load is documented in the design, temporary in the database of the FP department. The permanent fire load must not be increased, temporary only up to the limit (approved by the FP department) Any information is in the database of the FP department. Limits for permanent load are given by the design and internal procedure (page 46, 50, 57) temporary load is limited to max 1kgm-2 (EDU). Fire load checks are part of the preventive inspections of the building, the frequency is determined by the "Fire Risk Assessment", corrective measures are carried out without delay. Management of ignition sources Hot works are governed by an internal methodology and are subject to approval by the FP department, which checks compliance with measures both during and after the work. Powers and responsibilities are regulated in the permit. Inspections are focused on fire prevention and compliance. Before starting, the FP department evaluates the place of work with an open fire and proposes adequate measures according to the type of work, the place of work and the conditions at the workplace. Subsequently, checks are carried out to ensure compliance with the conditions, and after the work is finished, there is a site security check and checks aimed at preventing the occurrence of fire. Hydrogen is stored in separate building, isolated tubes transport it into generator. For the possibility of hydrogen occurrence in reactor hall there are installed passive autocatalytic recombiners.
CZ-E-336 | PFP | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | Research reactor LVR 15 | How are the fire classes for fire barriers defined? | The fire resistance of a structure is the time for which the structure is able to withstand the effects of fire without breaking its function - limit state of bearing capacity or stability R, integrity E, temperature on the unheated side I, heat flow density W and penetration of combustion products S. Fire sections are defined based on the Fire Safety Solution (FSS) documentation of the building. In FSS, individual fire sections are assigned by fire resistance letter with a number indicating fire resistance in minutes - 15, 30, 45, 60 a 90 minutes.
CZ-E-337 | PFP | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | Research reactor LVR 16 | [generic]: o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers? | In the Fire Safety Resolution of the building, the resistance of individual fire section is indicated, which prevent the spread of fires to other fire compartments. Aiming for a gradual division of the building into fire sections with separation of materials with defined resistance See section 3.3.C2 of the NHZ, p. 122 Extension of the EFD system to more locations in the building/technology; higher division of buildings into fire sections; during renovations, establish qualification requirements and the corresponding qualification documents (fire-retardant materials); regular review of fire protection requirements - fire prevention and fire fighting; regular training of the operator's cooperation with the fire brigade units. The main constraints will be the financial conditions for the implementation of changes (construction modifications and technology replacement), alternatively only the possibility to minimize the fire load and higher frequency of condition inspections. Part of the implementation of changes is the necessary assessment process - this should include assessment against the FP documentation - typically the facility's Fire Safety Resolution when changes are made. Fire load influences the size and degree of fire safety of the fire section - determined by the relevant standards and is part of the Fire Safety Resolution of the building. Material damage caused by flooding can be expected during a (unplanned) start-up. In case of interruption, a minor delay in intervention can be expected due to the need to switch to an alternative source (another hydrant/Fire Brigade vehicle).
CZ-E-338 | PFP | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | Research reactor LVR 15 | Specify the dispositions implemented for iodine filter protection in case of fire? How are the maintenance and integrity check performed on the fire dampers? | The radioactive substances ventilation system is equipped with absolute filters - these are connected as the main ones. Iodine filters are connected to the circuit in the event that increased activity is identified in the ventilation circuits. The basic verification of fire dampers function is their inspection by the supplier at least once a year (identification of the damper, opening of the inspection hole and checking of closing and opening, the movement of the fire damper leaf, the visual check of corrosion presence and the integrity of the fire insulation from the fire separation structure, inspection of cabling, triggering mechanisms and cleaning). Specific actions are given by the manufacturer's documentation.
CZ-E-339 | PFP | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | Research reactor LVR 16 | [generic]: o RR : ventilation management in case of fire Describe the ventilation management in case of a fire ? Explain on what criteria is the ventilation stopped and/or are the fire dampers closed? And is this manually or automatically? o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made? | Due to the installation of fire dampers, automatic decommissioning can be expected. In the event of a fire-related accident, the ventilation system is fitted with fire dampers that are automatically closed when the inlet medium reaches 68°C. In the event of a fire, the building is to be disconnected from electrical power, including the ventilation system. Until the building is disconnected from the power supply, we will use alternative extinguishing agents, designed for extinguishing under voltage. Therefore, the ventilation system will not be functional, the firefighters will follow the rules of intervention with the risk of possible contamination of radioactive release. See section 3.3.C2 of the NHZ, p. 122 The fire dampers are subject to maintenance programs - carried out at least once a year (specified in ČSN 73 0872). No findings were found when inspecting seals or other means used to prevent the spread of a potential fire.
CZ-E-340 | PFP | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | Research reactor LVR 15 | [generic]: o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries). | The occurrence of any fire protection related event is reported to the FRS CR, for the purposes of information keeping it is recorded into a database as an operational event and further investigated and the results discussed at safety committees. Any fire in the guarded area of a nuclear installation is reported to the SÚJB. Any experience is transferred within working groups (typically e.g. RROG - research reactor operation group). FRSU personnel are then members of other working groups. In the CEZ Group, a fire protection expert group has been established, where members meet twice a year and share their experience. In the event of a significant safety event, this information is shared within the group and corrective measures are taken. For workplaces with at least three employees where activities with increased or high fire hazards are carried out, it is obligatory to establish a preventive fire watch. These watches supervise compliance with fire protection regulations and, in the event of a fire, take the necessary measures to rescue persons at risk and take part in the firefighting process. A fire log book is also maintained to record inspections, workplace deficiencies and other information relating to fire safety.
CZ-E-341 | PFP | Fire prevention/Passive Fire Protection | Fire prevention (TS 3.1) | NPP Temelin Dry Spent Fuel Storage | [generic] o Management of fire loads Describe the types of permanent and transient fire loads in the facilities? How is the inventory of fire loads (transitional and permanent) systematically documented (e.g. computer system) and managed (tasks and responsibilities) during operation and decommissioning (if any what is the difference)? How is analysed whether the change on fire loads affects fire risk? How is the existing knowledge of the inventory used during daily activities? What are the limits and practices on permanent and transient loads, which items are excluded? Describe the inspection programme for fire loads, roles and (independent) responsibilities and frequency. What are the lessons learned and corrective actions taken? o Management of ignition sources What types of hot works are managed in the installations? What are the roles and responsibilities and the way they are regulated and listed? Describe the details of the approaches (as documented in procedures) to systemically permit and control hot works, including the types of additional (temporary) measures in fire prevention and firefighting. Is it different during decommissioning? Describe in some detail the programme of (independent) inspections related to hot works including the purpose (before, during, after the work). o Management of the hydrogen risk (not relevant for all facilities) Describe all the elements of the management of hydrogen risk (such as limiting amount, separate storage, pipe routing etc….). Describe events and lessons learned or external experience used to modify the management of hydrogen and the related modifications. | The permanent fire load is determined by the nature of the space (office, warehouse, operation, workshop, etc.) and any flammable building structures (e.g. windows, doors, floor) and is based on standards. The temporary fire load is determined by the working activity and its needs (repairs, replacements, etc.). As part of the operation, the permanent fire load is reduced (if there is a replacement of non-flammable equipment, non-flammable windows, doors, floors are installed...), the temporary fire load is subject to the approval of the FP department and is monitored and limited. Permanent fire load is documented in the design, temporary in the database of the FP department. The permanent fire load must not be increased, temporary only up to the limit (approved by the FP department) Any information is in the database of the FP department. Limits for permanent load are given by the design and internal procedure. Fire load checks are part of the preventive inspections of the building, the frequency is determined by the "Fire Risk Assessment", corrective measures are carried out without delay. Hot works, if any, are managed by an internal methodology and are subject to approval by the FP department, which checks compliance with measures both during and after the work. Roles and responsibilities are regulated in the permit. Inspections are focused on fire prevention and compliance. Before starting, the FP department evaluates the place of work with an open fire and proposes adequate measures according to the type of work, the place of work and the conditions at the workplace. Subsequently, checks are carried out to ensure compliance with the conditions, and after the work is finished, there is a site security check and checks aimed at preventing the occurrence of fire.
CZ-E-342 | PFP | Fire prevention/Passive Fire Protection | Prevention of fire spreading (TS 3.3.1) | NPP Temelin Dry Spent Fuel Storage | [generic] o Compartmentation How is the risk taken into consideration? How is propagation of fire prevented/delayed/mitigated? How are ventilation systems divided among trains/ compartments? What improvements could be achieved to older existing facilities? What limitations are there to do that and what are the alternative measures to cope with that? How is the management concerning fire compartmentation performed as the facility is growing? How are the fire loads linked to fire compartmentation and fire rating of barriers? | The project deals with the division of buildings into fire sections, determines the fire resistance of individual structures, and determines the quantity, scope and location of individual fire safety devices. In the event of a change of use, the project is evaluated and measures are proposed to maintain or increase fire safety. The ventilation system is described in NAR.
CZ-E-343 | PFP | Fire prevention/Passive Fire Protection | Ventilation systems (TS 3.3.2) | NPP Temelin Dry Spent Fuel Storage | [generic] o Maintenance/Access/Inspection of fire dampers (not relevant for all facilities) What are types and frequencies of testing/inspection of fire dampers? How is this applied to (nearly) inaccessible dampers? What insights have been gathered and improvements of the dampers or test/inspection have been made? | The period is 12 month.
CZ-E-344 | PFP | Fire prevention/Passive Fire Protection | Licensee and regulatory experience | NPP Temelin Dry Spent Fuel Storage | [generic] o OPEX on fire events How do you classify and report on fire related events? Are smouldering events reported? How and to what extent is information on these fire events shared and/or discussed national and international level? If applicable: what are the current fire safety related topics that are discussed on national level? Is there an exchange with conventional industry? Can you provide information on events related to fire at your facilities which led to (significant) improvements of fire protection within your country (causes, improvements and relevant lessons learned)? Same question for external experiences (national, international, other industries). | According to the Czech legislation, every fire must be reported, the fire classification is carried out by a fire cause investigator who is a member of the FRS CR. Every fire is reported to the FRS of the Czech Republic, the exchange of experience about fires that have occurred takes place at conferences and at instructional methodical jobs between the commanders of FRSU (energy, automotive industry, chemical industry, airports, etc.) within the Czech Republic. There were no fires in our facilities that resulted in a significant improvement in FP. The Czech legislation is adjusted based on experience from domestic fires as well as world practice.
CZ-E-345 | AFP | Active fire protection | Fire detection and alarm (TS 3.2.1) | Temelin NPP | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems. | Earthquake resistance of fire protection systems in Temelín NPP have the System SSE and High Pressure Pipeline Distribution in the Reactor Building and semi-stable extinguishing of systems diesels. The requirement is that they maintain functionality even during a seismic event. After the replacement of CZ-10 system by SINTESO there are used only addressable detectors. Safety class 3 include system stable sprinklers, selected fire dampers, EFD as defined: EFD are placed in sections according to requirements of the design, technical standards (ČSN), special assessment results, insurance pool recommendation. Rooms with no importance, e.g. toilets, do not have detectors. EFD has certification based on ČSN EN 54, power supply of autonomous operation at least for 24 hours by batteries. In general, it can be stated that in objects with the presence of RA substances and equipment that is classified in safety class 2, the electric fire alarm system is classified in safety class 3.
CZ-E-346 | AFP | Active fire protection | Fire detection and alarm (TS 3.2.1) | Temelin NPP | Page 60-65 Section 3.2.A.1 Topic 2 - No detail on level of system resilience, hazard tolerance or what EMIT is required and how it is controlled. | The electrical detection system is in compliance with the Czech technical standards (see Reference). In the protection of spaces important from the point of view of nuclear safety, the systems are seismic resistant.
CZ-E-347 | AFP | Active fire protection | Fire detection and alarm (TS 3.2.1) | Temelin NPP | Page 61 of pdf, section 3.2.A.1.2, assumption 1. "Multi-criteria (combined) detector AlgoRex and SINTESO - new generation detector, working on the principle of measuring and comparing several different variables characteristic for fire (more than 5000 units installed)". Please, explain the main features, variables compared, design standards and other general information regarding this type of detectors. - Page 61 of pdf, section 3.2.A.1.2, assumption 1. "Video smoke detection system - uses a conventional CCTV camera connected to a central unit, analyses incoming images frame by frame and decides if they contain smoke". "This feature allows the system to detect smoke efficiently and quickly even when traditional detection techniques are ineffective (aspirating, linear and spot smoke detectors)". Please, explain the main features, design standards and other general information regarding this type of detectors. - Page 61 of pdf, section 3.2.A.1.2, assumption 1. In general, are SSC important to safety covered by fire detectors? If not, please explain. | The detail information is available on web page of SIEMENS company. The detectors and video detectors have certified compliance with the Czech technical standard ČSN EN54 (342710). Important SSC are guarded by fire detectors.
CZ-E-348 | AFP | Active fire protection | Fire detection and alarm (TS 3.2.1) | Dukovany | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? • Please provide detail of the safety class of the fire detection systems. | The EFD switchboards at RB have seismic classification 1a. Switchboards of outdoor objects are not seismic resistant. The EFD system is fully addressable, each detector has its own unique address, which, when activated, is displayed on the control panel and in the superstructure (graphic) system. EPS detectors are placed in the premises based on: • Requirements of relevant CSN standards • Outputs from PSR, or requirements of the SÚJB/IAEA instructions • Recommendations of insurance companies • The operator's request • Designer's proposal. Rooms without fire load (with low accidental load) are usually without detectors. In the event of a loss of electrical network power, the EFD switchboard is powered by a backup energy source (batteries). Accumulators are usually part of the EFD switchboards (or auxiliary source) and the battery life is at least 24 hours EFD protecting spaces where the SSC of safety systems are located is classified in safety class 3. Other EPS protecting equipment with an impact on safety is classified as non-selected equipment
CZ-E-349 | AFP | Active fire protection | Fire detection and alarm (TS 3.2.1) | Dukovany | No detail on level of system resilience, hazard tolerance or what EMIT is required and how it is controlled. (As for Temelin.) | The electrical detection system is in compliance with the Czech technical standards (see Reference). In the protection of spaces important from the point of view of nuclear safety, the systems are seismic resistant.
CZ-E-350 | AFP | Active fire protection | Fire detection and alarm (TS 3.2.1) | Dukovany | Page 85 of pdf, section 3.2.B.1.2, assumption 1. In general, are SSC important to safety covered by fire detectors? If not, please explain. - Page 89 of pdf, section 3.2.B.1.3, assumption 4. Explain the procedures established for the examination, inspection, maintenance and testing of fire detection and alarm features. | Important SSC are guarded by fire detectors. Inspections are carried out according to decree no. 246/2001 Coll. i.e. system operability check and, for EFD systems, also activity tests during operation with a frequency of 1M (monthly check) and 6M (semiannual check). Checks are carried out within the scope of the system manufacturer's recommendations, or depending on operational experience, this period will be shortened. Part of the annual inspection of operability also includes the verification of the function of the follow-on equipment that the EFD controls (fire hydrants, ventilation, etc.).
CZ-E-351 | AFP | Active fire protection | Fire suppression (TS 3.2.2) | Temelin NPP | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy. | Earthquake resistance of fire protection systems in Temelín NPP: the Stable Sprinkling System and High Pressure Pipeline Distribution in the reactor building and PHZ of system DGS are seismically resistant. The requirement is that they maintain functionality even during a seismic event. Any failure of EFDS and Dampers must not endanger other seismic resistant equipment. There is no requirement for seismic resistance for the rest of extinguishing systems. Fire equipment is in safety class 3 (stable extinguishers of SSCs, selected fire dampers, EFDS). In the probabilistic risk assessment, fire water systems are included as a possible source that can cause internal flooding. Loss of water as a fire extinguishing agent are taken into account in the design of the system. Active extinguishing systems are connected to electrical power supply category II. (DG) or own batteries with 24 hours of autonomous operation. Stable extinguishing system is designed according to the project in places where there is a high fire load, important equipment, spaces where manual extinguishing is complicated (confined spaces, cable risers, oil management spaces). The FRSU goes out to every fire even in places with a stable extinguisher and, if necessary, extinguishes the fire manually.
CZ-E-352 | AFP | Active fire protection | Fire suppression (TS 3.2.2) | Temelin NPP | Page 65-81 Section 3.2.A.2 Topic 1- large amount of detail regarding the various suppression systems provided on site but it is not clear how it is determined whether the suppression provisions are adequate to extinguish a fire (where this is required) or what the safety classification or design standards against which these systems have been designed. Please could clarification be provided on these points? | Fire extinguishing systems are designed on the basis of a project, which is processed by an authorized person according to valid standards. Design documentation is prepared for individual systems, the part of which are calculations. Fire extinguishing systems are designed to extinguish a fire in a given area. The valid technical standards are listed in Reference in NAR.
CZ-E-353 | AFP | Active fire protection | Fire suppression (TS 3.2.2) | Temelin NPP | Page 65-81 Section 3.2.A.2 Topic 4 - No discussion of hazard effects of suppression systems and retention arrangements for fire fighting water. Please could clarification be provided on these points? | The dangerous effects of fire extinguishing systems are the same as everywhere else. Spaces that are protected by water stable extinguishing systems are connected to the industrial drainage system, and in case of extinguishing, the water flows into the industrial drainage system and then to the cleaning station.
CZ-E-354 | AFP | Active fire protection | Fire suppression (TS 3.2.2) | Temelin NPP | 1. Section 3.2.A.2.3. Requirements for fire resistance of power (6 and 0.4 kV) and control cables of safety systems and compliance of these cables with established requirements - see paras. (3.2.A.) 2. Section 3.2.A.3.1 Information on availability of safe emergency hydrogen discharge from the turbogenerator in the event of a problem with the sealing system. | The fire resistance of cables is documented by certificates from type or selection tests, or their use is individually assessed by designated experts in "group for engineering solutions". In the case of purchases of cables to the internal warehouse, the specified types are subject of verification tests (including fire tests). The entire hydrogen storage and transport system both Units, including the safe release of hydrogen, is described in internal procedure No. 264. Leakage of pressurized hydrogen from the machine around the rotor pins is prevented by radial rotor oil seals and a sealing oil system. CO2 is available for emergency emptying of the machine.
CZ-E-355 | AFP | Active fire protection | Fire suppression (TS 3.2.2) | Temelin NPP | Page 69 of pdf, section 3.2.A.2.2, assumption 1. "Foam Semi-Stable Extinguishers in Diesel Generating Stations: The equipment is designed to extinguish fires arising in the buildings of diesel generating stations. This equipment does not have its own extinguishing agent tank or its own extinguishing agent pump and works in synergy with mobile firefighting equipment". How long does it take to deploy the mobile firefighting equipment and start suppression activities? Is this special arrangement considered in the training program? Which is the water and foam capacity (volume and suppression time) of the mobile firefighting equipment? - Page 72 of pdf, section 3.2.A.2.2, assumption 2. Fire water supply system - seismic resistant: "Water source - the permanent fire water supply consists of a steel tank with a volume of 70 m3". Which is the suppression duration supposed to calculate this capacity? - Page 77 of pdf, section 3.2.A.2.3, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain. | After the arrival of the FRSU on the scene, the intervention starts within one minute and extinguishing takes place immediately. Firefighters of the FRSU regularly practice intervention on extinguishing DGS. Exercises are scheduled according to the training program. The capacity of water and foam is for 10 minutes of extinguishing plus three times the supply of extinguishing agent (water, foam). The water capacity is unlimited, foaming agent at 1% solution, currently FRSU has a stock of approx. 600,000 liters of extinguishing solution. Water is added to the tank from the technical water system, the water source is inexhaustible. The extinguishing time is calculated as 10 minutes. Flooding is not expected, the systems are flooded up to the valve station, and the pipeline is not flooded. Retention is through drainage system.
CZ-E-356 | AFP | Active fire protection | Fire suppression (TS 3.2.2) | Dukovany | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy. | Seismic resistance of individual fire extinguishing systems is described in dedicated chapters. The safety classification is mentioned in NAR – „system“ = safety classified (2 or 3), „non-system“ = without safety class. The fire water flooding in extinguished section is presumed and the water is drained to special sewerage. The emergency electrical supply is based on diesel generators and batteries. The last possibility is fire truck connection to the special inlets. Stable fire extinguishing equipment is designed according to the project in places where there is a high fire load, equipment is important, spaces where manual extinguishing is complicated (confined spaces, cable risers, oil management spaces) in spaces where, thanks to the designed SHZ, the designer can reduce the fire risk and thereby reducing the fire resistance of building structures and others. Main principles of SES use: protection of important equipment - cable management, oil management, complicated manual extinguishing - cable risers. In the area of cable risers, the availability of manual extinguishing was taken into account.
CZ-E-357 | AFP | Active fire protection | Fire suppression (TS 3.2.2) | Dukovany | As for Temelin. | Fire extinguishing systems are designed on the basis of a project, which is processed by an authorized person according to valid standards. Design documentation is prepared for individual systems, the part of which are calculations. Fire extinguishing systems are designed to extinguish a fire in a given area. The valid technical standards are listed in Reference in NAR.
CZ-E-358 | AFP | Active fire protection | Fire suppression (TS 3.2.2) | Dukovany | Page 90 of pdf, section 3.2.B.2.2, assumption 2. In the event of a safe shutdown earthquake, is there an extinguishing system (seismic sub-system) capable of supplying water to equipped fire hoses in fire areas containing equipment necessary for safe shutdown or any similar provision? - Page 96 of pdf, section 3.2.B.2.2, assumption 1. Are there fixed suppression systems based on foam? - Page 99 of pdf, section 3.2.B.2.3, assumption 4. Flooding is not explained when describing management of harmful effects and consequential hazards from actuation or rupture of fire extinguishing systems, please explain. - Page 101 of pdf, section 3.2.B.2.4, assumption 3. Explain the procedures established for the examination, inspection, maintenance and testing of extinguishing systems. | In the protection of spaces important from the point of view of nuclear safety, the systems are seismic resistant. Dukovany NPP do not use foam extinguishers. There is an industrial sewer in the areas protected by the water stable extinguishers, in the event of a start-up, the water flows through this sewer and is collected and cleaned. Inspections are carried out according to decree no. 246/2001 Coll. i.e. system operability check. Checks are carried out within the scope of the system manufacturer's recommendations, operating procedures or depending on operational experience, this period will be shortened.
CZ-E-359 | AFP | Active fire protection | Fire suppression (TS 3.2.2) | Dukovany | 1. Section 3.2.A.2.3 Requirements for fire resistance of power (6 and 0.4 kV) and control cables of safety systems and compliance of these cables with established requirements - see paras (3.2.A.) 2. Section 3.2.A.3.1. Information on availability of safe emergency hydrogen discharge from the turbogenerator in the event of a problem with the sealing system. | The fire resistance of cables is documented by certificates from type or selection tests, or their use is individually assessed by a group for engineering solutions. In the case of purchases of cables to the internal warehouse, the specified types are subject of verification tests (including fire tests). The entire hydrogen storage and transport system both Units, including the safe release of hydrogen, is described in internal procedure No. 264. Leakage of pressurized hydrogen from the machine around the rotor pins is prevented by radial rotor oil seals and a sealing oil system. CO2 is available for emergency emptying of the machine.
CZ-E-360 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Temelin NPP | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. | The FRS CR is located in Týn nad Vltavou, the distance is 7 km from NPP. The duration of an intervention inside the reactor hall in non-working hours is the same as during working hours - 4 minutes from notification to arrival at the scene and 3 minutes for combat deployment inside the building. The nearest FRS has 8 firefighters+1 commander (in 3 shifts totally 25 persons). The FRS has ability to intervene in and off site of NPP. The fire alarm plan defines the FRS to intervene in dedicated area. If the case of fire magnitude exceeds the FRSU sufficient number of forces and resources to extinguish the fire, the hail of the state FRS CR is automatically applied based on permanent connection to the FRS CR operational center. The arrival time of the first Temelín FRSU team from the alarm announcement is a maximum of 4 minutes. The company FRSU has 3 outgoing teams, which means that another team can go out to the fire at the same time or according to the requirements of the intervention commander. The state FRS CR is able to respond to a fire within 15-20 minutes, depending on the driving distance. Arrival times are checked as part of cooperation in joint interventions and exercises. Temelín NPP FRSU is in site. Page 83 Equipment is on Pg. 84. The FRSU is provided with the necessary protective equipment (protective clothing, radiate heating clothing, overpressure clothing for liquidation of chemical incidents). The NPP firefighters are professional staff with no other duties except fire suppression and rescue.
CZ-E-361 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Temelin NPP | Page 81 - 84 Section 3.2.A.3 Topic 5 - no detail provided of fire drills and exercises. Please could clarification be provided on this point? | The FRSU's exercises are based on the annual training program, as a rule, each shift performs two exercises per month. Furthermore, once a month, an exercise is organized in a selected construction object with the aim of evacuating people. Minimum once a year is organized a cooperation exercise with FRS CR.
CZ-E-362 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Temelin NPP | Page 81 - 84 Section 3.2.A.3 Topic 3 - no detail provided on EMIT of fire protection measures. Please could clarification be provided on this point? | Earthquake mitigation was subject to special assessment EU "Stress Tests” in 2012 resulted in Action Plan (published on web page). Many measures after the Fukushima event were implemented also in fire protection measures – upgrading the FRSU station, additional equipment and mobile operating equipment, increasing the number of firefighters, diverse additional and mobile equipment technology for the company fire brigade (Diverse EFW System), hydrogen recombiners. There are actively used external and internal feedback, which assess the influence of external and internal events on the fire protection process.
CZ-E-363 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Temelin NPP | 1. There is no detailed information on the NPP's strategy regarding improvement of the active fire protection, including modernization of the fire protection system. Please provide missing information. 2. Section 3.2.A.3 The information on the organization of safe staff work performance related to fire-hazardous activities is missing. Please provide missing information. | In 2003, the NPP Temelín fire safety improvement study was prepared, which established the requirements for increasing fire safety in individual areas and the conditions under which these improvements can be made and recommended the order of their implementation. The document was a basis for strategic decisions in connection with the gradual increase in fire safety in the power plant. Other suggestions for improving fire safety include the recommendations of insurance companies (nuclear pool, EMANI), the needs of the independent FP administration department, and recommendations from the PSR. As mentioned in the Chapter 1.2.1 (Pg. 16) Act No. 262/2006 Coll., the Labor Code, stipulates the employer's obligation to carry out regular training in the field of occupational health and safety. Details of employee training in fire protection stipulate Section 23 of Decree No. 246/2001 Coll. - the obligation to repeat the fire training every 2 years. All NPP employees are regularly trained once a year in the rules of fire protection, where there is information on the safe behavior of employees.
CZ-E-364 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Temelin NPP | Page 81 - 84 Topic 1 Section 3.2.A.3 - no detail provided on whether the internal fire brigade would need to call on the external fire brigade. If so, what are the criteria and how are the external fire brigade contacted? Please could clarification be provided on these points? | The intervention of an external FRS is based on the extent of the fire, according to the regional fire alarm plan. The regional fire alarm plan determines FP units for individual district of the region. The units are activated through the regional operating center of the FRS region.
CZ-E-365 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Temelin NPP | Page 81 of pdf, section 3.2.A.3, assumption 4. "The firefighters perform repressive activities in four shifts, each with 18 firefighters + 1 driver". Explain the training, organisation, minimum knowledge and physical conditions of the fire brigade. - Page 81 of pdf, section 3.2.A.3, assumption 1. "The maximum time of arrival of the FRSU to the most important buildings of the nuclear power plant (MPU) is 4 minutes from the occurrence of a fire that is detected by EFD". Please, give evidence of the time of arrival from real events and drills. - Page 83 of pdf, section 3.2.A.3.2, assumption 1. Drills and exercises are not described. Please explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade, content and main lessons learnt. - Page 83 of pdf, section 3.2.A.3.2, assumption 2. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 83 of pdf, section 3.2.A.3.2, assumption 2. Explain the coordination between the onsite fire brigade and the offsite response group. - Page 83 of pdf, section 3.2.A.3.2, assumption 2. Explain the written procedures in place defining responsibility and actions of staff in responding to any fire in the installation. | The training of the FRSU is organized according to issued annual training plan of the FRS of the Czech Republic by the Ministry of the Interior. Subsequently, this training plan is applied to the annual training and training plan of the NPP. Physical fitness and the limits for successful completion of physical tests is established in departmental instruction. Physical tests are reviewed once a year. Theoretical and practical knowledge is given by training programs with its examination once a year. On the basis of intervention reports, which is one of the mandatory documents of the FRSU, the individual times of the unit's arrival at the building can be documented. The time of announcement, departure and arrival is controlled by uniform time (NTP). Every year, each of the 4 shifts must perform at least 24 tactical exercises on a selected building object and 3 exercises on the topic of evacuating a building object. An intervention report was drawn up from each exercise. These exercises are given by the Instruction of the head of the fire protection unit. According to the DAM training schedules, all exercises of stress tests management are performed every 3 years. Firefighting documentation for all building objects and intervention cards are prepared, where interventions on important objects and systems in the NPP are described. There is a description of the structure, the system, the determination of the technique for extinguishing the fire, a suitable extinguishing agent, the protection of the responding firefighters, a description of the possible risks during the intervention, recommendations for the intervention commander. Communication is set up and regularly checked through operational centers where the first exchange of information takes place. Subsequently, the FRSU communicate using radio stations on a common communication channel. The units are equipped with the same means of communication. Employees of the power plant and leaders of suppliers are regularly trained in fire protection once a year. Regular exercises in which objects are evacuated are in place. Fire points are located in buildings, on which instructions are described on how to behave in the event of a fire and when evacuating people from the given building.
CZ-E-366 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Dukovany | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. | The nearest professional FRS of the Vysočina region is in the village of Hrotovice (7 km - calculated travel time max. 10 min. - considered at a speed of 45 km/h). In the event of an intervention, the FRSU is not blocked by the administration. The entrance to the buildings, including the reactor building, is through escape routes. Always with the approval of shift engineer and after ascertaining the current radiation situation at central dosimetry control. Each firefighter is then equipped with a dosimeter. After the end of the intervention, a standard output including dosimetry control is performed. The necessary time for combat development in accordance with the combat and training regulations is 2 to 10 minutes depending on the specific location and complexity of the combat development (rescue of a person, stretcher, fire, intervention in pressure suits, danger of explosion, etc.). The minimum number of 4 firefighters in Hrotovice is required. They are able to go out with two vehicles at the same time in the number of 1+1. Average or maximum driving times are not set, according to the applicable legislation, the calculated time is used (7km - calculated driving time max. 10 min. - considered at a speed of 45 km/h), however the modernized technology already has a standard driving speed to hit 60km/h. According to the legislation, the time limit is 7 minutes - only driving time and combat development. The actual time from the start of the intervention since the announcement of the alarm is around 5 minutes. The organization of the FRSU Dukovany NPP unit is set so that both teams leave at the same time. FRSU is described on page 101-103 There are no additional activities that could affect the availability of firefighters; all team is professional.
CZ-E-367 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Dukovany | As for Temelin. | The FRSU's exercises are based on the annual training program, as a rule, each shift performs two exercises per month. Furthermore, once a month, an exercise is organized in a selected construction object with the aim of evacuating people. Minimum once a year is organized a cooperation exercise with FRS CR.
CZ-E-368 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Dukovany | Page 102 of pdf, section 3.2.B.3, assumption 4. "The 70 firefighters perform repressive activities in four shifts, each with 12 firefighters on the day shift and 11 firefighters on the night shift divided into 3 fire teams". Explain the training, organisation, minimum knowledge and physical conditions of the fire brigade. - Page 102 of pdf, section 3.2.B.3, assumption 1. "The maximum time of arrival of the FRSU to the most important buildings of the nuclear power plant (MPU) is 4 minutes from the occurrence of a fire that is detected by EFD". Please, give evidence of the time of arrival from real events and drills. - Page 104 of pdf, section 3.2.B.3.2, assumption 1. Drills and exercises are not described. Please explain their goal, type, frequency, minimum number of drills per year for each member of the fire brigade, content and main lessons learnt. - Page 104 of pdf, section 3.2.B.3.2, assumption 1. Are there pre-fire plans (or document developing firefighting strategies) for each fire area containing SSC important to safety? Please describe their content. - Page 104 of pdf, section 3.2.B.3.2, assumption 2. Explain the coordination between the onsite fire brigade and the offsite response group. - Page 104 of pdf, section 3.2.B.3.2, assumption 2. Explain the written procedures in place defining responsibility and actions of staff in responding to any fire in the installation. | The training plan of the FRSU of Dukovany NPP is in accordance with the professional training (including physical training) and is supplemented by topics that are specific to NPP (special equipment, individual NPP buildings, specific activities, DAM exercises, etc.). The resulting number of hours of professional training more than doubles the set minimum (80 hours) given by national legislation. The training plan for the given calendar year is sent to the Regional FRS of the Vysočina region. Regular verification of the knowledge of FRSU employees takes place once a year (including physical tests), and then there is regular verification of knowledge for individual functions as part of the qualification for the performance of a function in the Training and Education Facility of the FRS CR (period once every 5 years). The reaction time of FRSU intervention is measured an is between 2 to 4 minutes (proven by SÚJB). Practices and exercises are carried out practically every day as part of the established professional training plan. This is mainly training according to combat and exercise regulations, DAM exercises and intervention exercises in individual buildings. There are operative cards in case of intervention for all rooms where EFD/SES is installed. These cards contain information and procedures in case of intervention. Firefighting documentation, including the graphic part, is also processed for selected objects. The coordination of the intervening units is in accordance with the training and Battle Order of the FRS units. The units proceed in the same way for all Integrates Rescue Service interventions. Thus, an intervention commander is determined, who manages the firefighting and rescue work. The coordination and transmission of other units, possibly other components, is carried out by the Vysočina Region FRS Operations Center in cooperation with the NPP FRSU Operations Center (outbound system GINA, DIGITAL RDST, ANALOG RDST, by telephone). At the point of transmission of instructions, the intervention commander ensures, in the case of major incidents, the sector commander/section commander. If necessary, it is possible to use the national emergency cooperation channels of radio traffic. The established written procedures are mainly individual operating regulations in case of fire. Procedures describe how operating personnel should proceed in the event of a fire.
CZ-E-369 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Dukovany | 1. There is no detailed information on the NPP's strategy regarding improvement of the active fire protection, including modernization of the fire protection system. Please provide missing information. 2. Section 3.2.A.3 The information on the organization of safe staff work performance related to fire-hazardous activities is missing. Please provide missing information. | All fire protection systems are subject to an annual operability check, and in case of unsatisfactory condition, they are repaired, modernized or replaced. Detail are in NAR on page 85. NPP have developed a methodology and basic rules of procedure for fire-hazardous work. These works require a permit from the NPP FP department, which sets the conditions for a given type of fire-hazardous work, determines the fire patrol and supervision of these works and the period of supervision after the work is completed.
CZ-E-370 | AFP | Active fire protection | Licensee and regulatory experience | Temelin NPP | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs. | There is no such a experience. Regular checks in accordance with the requirements of the equipment manufacturer and in accordance with legislation are required. After the titanium pipe fire on July 2, 2015 at the Paluel nuclear power plant - France, this event was presented at the training of managers, with the fact that when working with an open flame, an appropriate technological procedure must be chosen and appropriate safety measures must be ensured - rigorous control workplace, workplace fencing, etc. A suitable type of fire extinguisher must be available on site to ensure first intervention.
CZ-E-371 | AFP | Active fire protection | Licensee and regulatory experience | Temelin NPP | Page 125 of pdf, section 3.6, and all the assumptions. Strengths and weaknesses are not clearly mentioned in the NAR, can you confirm that there are no strengths / weaknesses or otherwise mention them if there are any? | Described on page 28
CZ-E-372 | AFP | Active fire protection | Licensee and regulatory experience | Dukovany | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs. | Based on operational experience, the cleaning period of flame detectors on outdoor transformers was adjusted to the 3 month period. For EFD intake units, part of the half-yearly inspection includes filter cleaning as well. The probability of fire in the PSA is calculated according to generic data that is based on international documents.
CZ-E-373 | AFP | Active fire protection | Licensee and regulatory experience | Dukovany | Page 125 of pdf, section 3.6, and all the assumptions. Strengths are not clearly mentioned in the NAR, can you confirm that there are no strengths or otherwise mention them if there are any? - Page 125 of pdf, section 3.6, and all the assumptions. Weaknesses are not clearly mentioned in the NAR, can you confirm that there are no weaknesses or otherwise mention them if there are any? | Described on page 33
CZ-E-374 | AFP | Active fire protection | Fire detection and alarm (TS 3.2.1) | Research reactor LVR 15 | [generic] • Please clarify what is the robustness against earthquake of the fire detection system and alarming system. • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? | The EFD system is not classified with a requirement for seismic resistance. The EFD is designed according to ČSN 73 0875 and ČSN 34 2710 in the scope of the Fire Safety Solution. EFD system has sensors with an address. Solved within the framework of the construction's Fire Safety Solution. Typically, they are not in places where due to the method of EPS detection a relevant response of the system cannot be expected - hall with high ceilings, rooms with significant draught - in these places the placement of EFD on the ceiling does not provide the necessary information and an alternative location (e.g. cable trays) or a surveillance procedure (cameras) is chosen. The control panels have a backup power supply for 24 hours
CZ-E-375 | AFP | Active fire protection | Fire suppression (TS 3.2.2) | Research reactor LVR 15 | [generic] • Please clarify what is the robustness against earthquake of the fire suppression systems. • Please provide detail of the safety class of the fire suppression systems. • Please clarify what can be adverse effects of fire water? Has this been assessed? What could be the adverse consequences of fire water system actuation or break? • Please clarify the emergency power supply arrangements for fire suppression. • Please clarify the balance between fixed fire extinguishing and manual firefighting. What strategy has been applied? What are the main principles? Clarify how accessibility considerations during manual firefighting has been considered in this strategy. | The safety classification is mentioned in NAR on page 15 “fire safety systems are in SC 3. The fire water flooding in extinguished section is presumed and the water is drained to special sewerage. The emergency electrical supply is based on diesel generators and batteries. The last possibility is fire truck connection to the special inlets. Stable extinguishing equipment is designed according to the project in places where there is a high fire load, equipment is important, spaces where manual extinguishing is complicated (confined spaces, cable risers, oil management spaces).
CZ-E-376 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Research reactor LVR 15 | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? •What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). • Please clarify whether the onsite first intervention teams / onsite fire brigades have other day to day duties that could impact their availability for firefighting duties. | FRS of the Czech Republic in Neratovice is in distance 20 km. Required response time is 92 minutes. Calculation from Fire Fighting documentation, approved by the Fire Department of the Central Bohemia Region From the moment of fire detection to the start of actual firefighting is 7 minutes. The minimum staffing of the nearest off-site FRS is 1+5 persons. The FRSU is set at 1+3 persons - in the event of larger incidents, external help is called in parallel. According to the assessment of the management group and the intervention leader on the ability to handle the situation with the current cast/shift. It is done every time a fire is detected. The time needed between the fire alarm declaration and the presence of the first response unit on the scene is 5 minutes. The second response is required in 25 minutes. The actual times measured during recent unannounced exercises and drills are as expected. To be determined in the Fire Fighting document. See 3.2.C.3.p. 108 Firefighters are required to leave within 2 minutes of an alarm being declared for any activity.
CZ-E-377 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Research reactor LVR 15 | Composition of the "shift" dedicated to firefighting. p 125 : "Thanks to the presence of the Fire Rescue Service Unit directly on the site" : it is not clear for the status of this team: public or private ? | This is the Fire and Rescue Service of the company ÚJV Řež, a. s. – private. The minimum shift composition is 4 persons. See Pg. 14 Article 49 of Atomic Act specifies the obligation to ensure the prevention, detection, elimination and suppression of fires and explosions and the limitation of their impact on safety and to provide a unit of the company's Fire Rescue Service in accordance with the Fire Protection Act.
CZ-E-378 | AFP | Active fire protection | Licensee and regulatory experience | Research reactor LVR 15 | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. • Please clarify what key learnings have been taken into account from past fire events in other NPPs or research reactors. | Within the operation of the EFD, sometimes, based on false alarms, the type of sensor is changed, e.g. optical-smoke for thermal, etc. in accordance with the Fire Safety Solution. Based on the experience from the evacuation drills, automatic opening of sliding doors in the administration building depending on the EFD signal has been added. The LVR-15 reactor facility was not affected by a significant fire. Regular exercises at least once every 2 years are a source of experience. Exercises include follow-up analysis and determination of measures: some areas has been equipped with additional portable fire extinguishers During evacuation, an connection to a member of the Fire and Rescue Service unit was tested, where it is possible to ensure the presence of the equipment operator at the workplace for the most necessary actions in a limited period of time. Restricted use identification cards to exit the building during a fire. The FRSU in cooperation with external units is able to provide protection of the reactor from forest fire by remote transport of water from the river based on the experience from the exercise.
CZ-E-379 | AFP | Active fire protection | Fire detection and alarm (TS 3.2.1) | NPP Temelin Dry Spent Fuel Storage | [generic] • How does the fire detection system allow to locate precisely the location of fires? Is the fire detection system addressable or not? • Please describe the strategy and criteria for selecting rooms where to install fire detectors in rooms. In which types of rooms are no fire detectors installed? • What is the ability of the fire detection system to function in case of loss of power? What is their emergency power supply arrangements, criteria and autonomy (how long can they work without power?)? | Described on page 110 - 111 & 124 of NAR.
CZ-E-380 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | NPP Temelin Dry Spent Fuel Storage | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). | The FRS CR is located in Týn nad Vltavou, the distance is 7 km from NPP. The duration of an intervention inside the reactor hall in non-working hours is the same as during working hours - 4 minutes from notification to arrival at the scene and 3 minutes for combat deployment inside the building. The nearest FRS has 8 firefighters+1 commander (in 3 shifts totally 25 persons). The FRS has ability to intervene in and off site of NPP. The fire alarm plan defines the FRS to intervene in dedicated area. If the case of fire magnitude exceeds the FRSU sufficient number of forces and resources to extinguish the fire, the hail of the state FRS CR is automatically applied based on permanent connection to the FRS CR operational center. The arrival time of the first Temelín FRSU team from the alarm announcement is a maximum of 4 minutes. The company FRSU has 3 outgoing teams, which means that another team can go out to the fire at the same time or according to the requirements of the intervention commander. The FRS CR is able to respond to a fire within 15-20 minutes, depending on the driving distance. Arrival times are checked as part of cooperation in joint interventions and exercises. Temelín NPP FRSU is in site. Page 83 Equipment is on Pg. 84. The FRSU is provided with the necessary protective equipment (protective clothing, radiate heating clothing, overpressure clothing for liquidation of chemical incidents). There are no additional activities that could affect the availability of firefighters; all team is professional.
CZ-E-381 | AFP | Active fire protection | Licensee and regulatory experience | NPP Temelin Dry Spent Fuel Storage | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. | Temelín NPP: 68 failures were recorded on the EPS system for the year 2023. In 2023, 10 failures were recorded on the fire water system. In 2023, 19 malfunctions were recorded in the ventilation system. That includes also SFS systems.
CZ-E-382 | AFP | Active fire protection | Administrative and organisational fire protection issues (TS 3.2.3) | Spent Fuel Storage facility | [generic] • How far is the external fire brigade located? What is the intervention time needed in case of a fire inside the reactor hall outside normal working hours? How much time is needed, from the moment of fire detection, until actual firefighting starts in the field (i.e. considering need for presence of RP escort, security/access formalities, personal protection equipment for entering radiological controlled zone, etc.). • What is the minimum staffing of the nearest off-site fire brigade? Can they respond to simultaneous fires inside and outside the NPP? Are there maximum or average times for arrival to the fire location for this brigade? • What criteria are applied for calling or not the off-site fire brigade? Is this done every time a fire is detected? • In case the off-site fire brigade(s) are called, what are the respective responsibilities among all actors? Who takes the lead? How is coordination ensured? • How much time is needed between a fire alarm and presence of the onsite first intervention team at the location? Same question for the onsite second intervention team (if any) or the onsite fire brigade (if any). What are the actual times measured during recent unannounced drills and exercises? Is there any regulatory requirement for this? • If not yet explained in the report, please clarify whether there is a fire brigade on site ? If not yet done, please clarify how it is equipped (protection clothes and equipment, vehicules, ...). | The FRS CR is located in Týn nad Vltavou, the distance is 7 km from NPP. The duration of an intervention inside the reactor hall in non-working hours is the same as during working hours - 4 minutes from notification to arrival at the scene and 3 minutes for combat deployment inside the building. The nearest FRS has 8 firefighters+1 commander (in 3 shifts totally 25 persons). The FRS has ability to intervene in and off site of NPP. The fire alarm plan defines the FRS to intervene in dedicated area. If the case of fire magnitude exceeds the FRSU sufficient number of forces and resources to extinguish the fire, the hail of the state FRS CR is automatically applied based on permanent connection to the FRS CR operational center. The arrival time of the first Temelín FRSU team from the alarm announcement is a maximum of 4 minutes. The company FRSU has 3 outgoing teams, which means that another team can go out to the fire at the same time or according to the requirements of the intervention commander. The FRS CR is able to respond to a fire within 15-20 minutes, depending on the driving distance. Arrival times are checked as part of cooperation in joint interventions and exercises. Temelín NPP FRSU is in site. Page 83 Equipment is on Pg. 84. The FRSU is provided with the necessary protective equipment (protective clothing, radiate heating clothing, overpressure clothing for liquidation of chemical incidents). There are no additional activities that could affect the availability of firefighters; all team is professional.
CZ-E-383 | AFP | Active fire protection | Licensee and regulatory experience | Spent Fuel Storage facility | [generic] • Please clarify whether you have any interesting operating experience feedback from testing fire detection and suppression systems. | Same as NPP.
CZ-C-85 | Austria | 01-General information | 19 |  | As stated in 1.2.3. FRS performs inspections of nuclear power plants on an annual basis, always on one selected building. FRS has performed a comprehensive inspection of all nuclear power plant buildings in 2013 at Temelín NPP. However, one of the conclusions was that due to the scope and documentation requirements of such an action and the resulting inadmissible duration of the entire inspection process, the feedback effect of the inspection process completely disappears. Thus, the FRS followed the path of annual inspections of one selected building from the list of risk buildings determined by deterministic analysis. How many buildings are declared significant? How are those inspected? Are there any other inspections (e.g. conditions of fire detection of fire extinguishing systems and components)? How often are they inspected? | At the Temelín NPP, 22 buildings are declared as important. Inspections of these buildings are carried out in accordance with the requirements of state legislation, namely according to the determination of fire risk, usually 4 times a year by FRSU. The FRS of CR inspect one of those separately. Fire safety equipment is checked by FRSU according to the requirements of the equipment manufacturer and legislation, an operability test must be carried out at least once every 12 months. The manufacturer of the device can also specify a shorter inspection period.
CZ-C-86 | Austria | 02- Fire safety analyses | 20 |  | Regarding "Audit No. 5", which examined the design of significant nuclear power plant buildings in relation to the terms between fire hazards and safe shutdown of the nuclear reactor according to the criteria defined in US 10CFR50, Appendix R and NUREG-8000, Part 9.5.1 (1995). How do you define significant buildings? | Important buildings are defined according to the fire risk, the content of security systems and the content of safety important equipment and radiation protection areas. Algorithm for fire safety assessment of NPP buildings is on page 22 of NAR.
CZ-C-87 | Austria | 02- Fire safety analyses | 21 |  | Regarding the study prepared by Nuclear Research Institute Řež, Energoprojekt Praha for the purposes of the Topical Peer-Review "Fire Protection" division many areas were covered but some of the most important areas for Nuclear Safety are not mentioned (e.g. MCR, cable spreading rooms, etc.). Please elaborate on the reasons for not mentioning these areas. | In this study, evaluated were areas where there was need for increased fire safety. Areas that met the required safety parameters and where no room for further improvement was found were not evaluated in this study.
CZ-C-88 | Austria | 02- Fire safety analyses | 24 |  | In 2011, a "Technical Assistance" document was prepared to examine the suitability and addition of Electrical Fire Detectors (EFD) in selected areas of the reactor and auxiliary buildings. A fire risk analysis was made for each room and, where values were exceeded for rooms without fire risk, the actual values were verified on site. Could you explain which rooms were covered here and what does “where values were exceeded for rooms without fire risk” mean? On which basis was the status “without fire risk” determined and what was e.g. the probability of fire ignition for those rooms? | Fire sections and spaces without fire risk are defined in the Czech technical standard (ČSN) and those are spaces in which the maximum fire load is less than 7.5 kg/m2 and are bounded by non-combustible structures. There is very little or no fire load in these spaces and there are no sources of initiation.
CZ-C-89 | Austria | 02- Fire safety analyses |  |  | It is stated that power cables and most low-current cables have enhanced resistance to the spread of fire, complying with IEC 332.3 category A, or IEC 331 tests, in all nuclear safety-important buildings. Were all original cables replaced in a course of pre-start up modernization at Temelin? | The decision to use only cables with increased resistance to the spread of flame according to IEC 332.3A and, in the case of safety cables, additionally according to IEC 331 in the buildings of the main production unit was made even before the start of cables implementation during construction stage.
CZ-C-90 | Austria | 02- Fire safety analyses | 25 |  | It is stated that documentation is actualized as required by the Fire Protection Act. This document approves the South Bohemian Regional Fire Rescue Service. The latest version of the fire risk assessment of the 1st reactor turbine hall has approval issued on 18 April 2016. What is the frequency of the updates as per applicable regulations? How of the is the fire risk assessment for all buildings updated? | The fire risk assessment is checked once a year, and if there have been changes in the building that affect the updating of the document, the documentation is revised.
CZ-C-91 | Austria | 02- Fire safety analyses | 30 |  | The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 20.3% level. This is a rather high contribution from internal fires, possibly indicating a safety challenge in this area. On which total CDF is 20.3% fire related? | CDF/year of all internal initiating events = 3,42E-06. CDF/year of fire internal events = 7,05E-07. IE groups are: Internal fires leading to the LOCA; Internal fires leading to the loss of secondary circuit; Internal fires leading to the LOCA; Internal fires leading to the loss of electrical power supply.
CZ-C-92 | Austria | 02- Fire safety analyses | 31 |  | The contributions of internal fires to the overall risk of unit operation are generally of little importance. The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 20.3% level. What about MCR and cable spreading areas? | Internal fire hazard analyzes include all fire section that contain equipment important to nuclear safety or related equipment, including MCR and cable areas. The fire in MCR is one if initiating events calculated in PSA.
CZ-C-93 | Austria | 02- Fire safety analyses | 33 |  | In this section, it is mentioned that the water SE, which protects the cable compartments, is obsolete. At present, the Dukovany NPP has developed a requirement for the selection of the most suitable method of securing the cable compartments by the SE. A working group has been set up to evaluate the different options. Since fire in the cable spreading areas is likely the dominant risk factor, when will this be completed and why was it not done before? | The water system is functional, but its innovation was not approved. The internal procedure is not finished as management of such a big modification is subject to legal conditions.
CZ-C-94 | Austria | 02- Fire safety analyses | 33 |  | Conference on fire protection and nuclear safety. Fire protection specialists obtain information on the latest trends in the field of fire safety. The information can be used to comment on new actions, or specialists recommend the implementation of these innovations a NPP. GOOD PRACTICE | Employees of the FP department participate in several conferences, seminars, and fire protection workshops every year. The last one was held in České Budějovice on 9-10 April 2024. In June 2024 is planned specialized conference on FP of NPP.
CZ-C-95 | Austria | 02- Fire safety analyses | 35 |  | “The introduction of the elements of cooperation and real distress cannot be replaced by any training for the members of the Fire Rescue Service.” Please clarify what is meant by this statement. | The level of stress and collective and personal responsibility and perception of danger in a real intervention is completely different from any training. This is a fact that affects the behavior of each individual, albeit to varying degrees. For the commander, the behavior of the subordinates during the actual intervention is an important indicator of the abilities of the team members.
CZ-C-96 | Austria | 02- Fire safety analyses | 35 |  | In regards to the inspection activities performed by the SÚJB and the Fire Rescue Service results. What is the frequency and scope of the inspections? | Fire inspections at the NPP are usually carried out once every 3 years by the Regional FRS. From the results of these inspections it can be stated that within the scope of the inspection points the obligations set out in Act No. 133/10985 Coll., on Fire Protection, as amended, were fulfilled. The NPP FRSU performs “day-by-day” inspections of all NPP buildings. SÚJB has Standard Annual Inspection Plan, which includes 4+2 inspection of reactor unit ventilation systems and every other year the fulfilment of implementation of fire protection system assurance of dedicated NPP.
CZ-C-97 | Austria | 02- Fire safety analyses | 36 |  | On this page it is mentioned that temperatures of several 1 000 °C are reached during the combustion of chemical gases and vapors. Several thousand degrees sounds rather high. | In the reactor building there are present combustible gases with high ignition temperature or combustible liquids e.g. diesel fuel. The structural systems are made of non-combustible material type DP1 (they do not increase the fire intensity during the required fire resistance period). For cable penetrations from fire sections, they are at least EW 30 DP1 and the fire resistance of structures is at least EI 60 DP1. Combustion takes place in a controlled manner within safety limits and the possible temperature is taken into account in approval of such a work.
CZ-C-98 | Austria | 02- Fire safety analyses | 39 |  | It is mentioned that the next fire exercise is planned for 2023. Did the mentioned fire exercise already take place and what are the outcomes? Are any exersices planned that would focus on safety significant sequences (for systems of the RR itself) rather than on the sources? | Fire exercise organized in cooperation with the company FRS and a group of volunteer firefighters was performed by the end of 2023. The theme was „simulated operation of the LVR-15 reactor at power; during operation, a warning signal of a reduced flow through the cooling trains was issued“. Subsequently, due to the drop in cooling flow, the reactor was shut down in an emergency. The operator performs a status check, shift personnel announce potential fire in pump station and FRSU is activated. After the end of the HZS intervention, handing over the operator's workplace and carrying out the decontamination of the interveners; after ensuring monitoring, further necessary decontamination of premises.
CZ-C-99 | Austria | 02- Fire safety analyses | 40 |  | In this section, it is mentioned that the LVR-15 reactor has not been affected by a significant fire since the 1989 reconstruction and the last documented fire was in the reactor hall in the cable line, which was extinguished. How many fires have there been in the LVR-15 reactor facility in total? | The event was the burning in cable duct. As mentioned only that one during 35 years of operation.
CZ-C-100 | Austria | 03.1 - Fire prevention | 43 |  | It is mentioned that in the USSR, the basic requirements for fire safety were based on production categories only. Could you please explain what “Production Category” means? What is the relation of “Production Category” to “Safety Class”? | This is a division of objects into production and non-production, and conditions are set based on the evaluation. At present the FHA is made according to the Czech legislation. There is no relationship between the production category and the safety class.
CZ-C-101 | Austria | 03.1 - Fire prevention | 47 |  | Here it is noted that non-conformities detected are at a very low level (2022: 73/942). This does not sound low; it is 8% of the inspection. Could you please comment on the findings? | All mentioned findings are category 4 - findings of low relevance. A root cause analysis is not required and it is not necessary to involve multiple departments to resolve it. These are deficiencies, potential noncompliance, near misses. The examples are on page 47 „usually caused by human factors (e.g. improper storage of combustible materials, closing of fire doors) and are promptly corrected“.
CZ-C-102 | Austria | 03.1 - Fire prevention | 72 |  | The permanent fire water supply consists of a steel tank with a volume of 70 m3. On which basis was it determined that a 70 m3 tank volume would be sufficient for e.g. seismically induced fire extinguishing, in case the resupply is damaged by the same seismic event? | The volume of the tank was determined by a project prepared by an authorized person in the FP field and is classified as selected equipment safety class 3 and is designed in seismic resistance category 1b.
CZ-C-103 | Austria | 03.2 - Active fire protection | 78 |  | It is stated that protected piping is not required for the supply system tubes, which filters outdoor air containing radioactive aerosols for the control room when necessary, and does not need to be used for fire sectioning for the following reasons. The system is only operational when the outdoor air is contaminated with radioactive substances. This seems to imply that an event with a release of radioactivity (e.g. radioactivity in ambient) and a simultaneous fire are deterministically excluded. On which basis was such an exclusion justified? | In the FHA, a fire is not considered to occur simultaneously with non-fire related failures in safety systems, plant accidents, or the most severe natural phenomena, except the loss of off-site power (IAEA TECDOC-1977, VIENNA, 2021).
CZ-C-104 | Austria | 03.2 - Active fire protection | 79 |  | The report mentions that the parallel installation of different divisions of cable routes of the secured power supply systems in compartments without separation by construction with fire resistance of at least 90 minutes is assessed and evaluated in detail in special documentation "engineering solutions". In how many cases does such a situation of multiple redundancies in one fire compartment occur? What are typical “engineering solutions” to assure power supply to redundant trains in a case of fire in such rooms? | In total there are registered 245 cases where there is more than one divisional cable route in one section (room), requiring assessment. In these cases (concurrence of cable routes/cables belonging to several divisions), the following is assessed: • Functions of the cables participating in the concurrency • Design of cables • Transmitted power of the cables participating in the concurrency • Disposition (distances, geometry) of individual routes/cables participating in the concurrency • Installed technology in places of concurrency
CZ-C-105 | Austria | 03.2 - Active fire protection | 81 |  | Temporary measures to ensure the required fire safety are applied e.g. during shutdowns of fire safety equipment, repairs, modifications and maintenance. How often are such temporary measures activated on average (per unit and per years)? | Abnormal/temporary safety measures are set by the FRSU for approx. 20 times per year
CZ-C-106 | Austria | 03.2 - Active fire protection | 103 |  | In the report it is stated that the fire resistance of the pipe penetrations through the fire separating structures prove a certificate according to the approved test methodology from 1995. Has the test methodology for penetration been upgraded since 1995? As for the plant life extension, how does the life extension affect the penetrations and their testing in the sense of the fire resistance? How are those penetrations inspected in the course of life extension? | Currently, the operability check of fire partitions is assessed according to Act No. 133/1985 Coll. (a major amendment to the fire law took place in 2000) and Decree No. 246/2001 Coll. and according to the manufacturer's instructions. The ageing inspection is subject to AMP. BTW documents created in 1995 are subject to amendments in the view of legislation changes.
CZ-C-107 | Austria | 03.3 - Passive fire protection | 106 |  | It is stated that the Vltava River is used as the main source of firewater in the reactor hall with a total water supply of 14.000 liters. Is there any firewater tank available at the site? What does the 14000-liter volume for the reactor hall refer to? | The page 106 refers to LVR 15. The use of water in firefighting is limited as much as possible, inert substances are preferred - carbon dioxide, powder, CAFS - dry foam. Water only in extremely necessary cases and in small quantities (mist, splinter stream). The Vltava River is used as the main source of firewater in the area. According to the methodology for extinguishing fires, an extinguishing time of 10 minutes is considered, 14,000 liters is the amount supplied by all streams for a period of 10 minutes. The supply of fire water is inexhaustible thanks to the water source.
CZ-C-108 | Austria | 03.3 - Passive fire protection | 116 |  | The fire resistance of the penetration seals installed in critical areas is 90 minutes. Does this apply to both the piping and electrical (cables) penetration? How do you define “critical areas”, and how many critical areas are defined in each NPP unit? | Penetrations of pipeline routes through fire-dividing structures are fire-sealed with fire resistance complying with the requirements of ČSN. The fire resistance of the sealing of pipe penetrations in important spaces is 90 minutes and the sealing construction is designed to allow pipes dilatation. The fire resistance of hermetic grommets installed at the boundary of the containment is 90 minutes. It applies to all distributions and applies to all "important" objects calculated in FHA methodology. Dukovany NPP has 24, Temelín NPP 22 important objects
CZ-C-109 | Austria | 03.3 - Passive fire protection | 120 |  | In the report, it is mentioned that flammable air filters are designed in such a way that they cannot leak radioactive substances above the specified limits in the event of a fire. The filter is automatically separated from the rest of the channel by closing the air dampers. Are those dampers gas-tight ones? If so, to which over-pressure are those designed? E.g. for the main charcoal filter in the MCR clean-up system? | The filters are airtight and are rated for an overpressure of 6 kPa, based on national legislation.
CZ-C-110 | Austria | 03.3 - Passive fire protection | 120 |  | It is noted that part of the dampers are designed so that when a temperature of 130°C is reached, the damper blade is "baked" - sealed in the pipe. Which dampers are designed to have such a feature? | The dampers at the partitions which separate safety systems.
CZ-C-111 | Austria | 03.3 - Passive fire protection | 121 |  | The originally undivided reactor building is being divided into fire sections subsequently during use; the division is not complete and finished. What exactly is unfinished and when will it be finished? | The information was valid to the required date June 2022. The division of fire sections is finished as of 2024. Planned actions include revising the Fire Solution document and equipping some areas with Electrical Fire Detectors (EFD) to increase safety in fire protection (plan for 2024). Subsequently, the new EFD will be added to the existing documentation of the object.
CZ-C-112 | Germany | 02- Fire safety analyses |  | Regarding Temelin NPP, p. 21 | The NAR states on p. 21: "In 2011, a "Technical Assistance" document was prepared to examine the suitability and addition of Electrical Fire Detectors (EFD) in selected areas of the reactor and auxiliary buildings. A fire risk analysis was made for each room and, where values were exceeded for rooms without fire risk, the actual values were verified on site." Could you provide information on the criteria used for the analysis? Is there a minimum risk for fire detectors to be installed in the areas of the reactor and the auxiliary buildings? | The criteria for the analysis were the fire load values in the individual assessed rooms. The EFD system must be designed in fire sections in buildings listed in the technical standards or ČSN 730875.
CZ-C-113 | Germany | 02- Fire safety analyses |  | Regarding Temelin NPP, p. 22 | On p. 22, Algorithm for fire safety assessment Could you explain the meaning of the "coefficient of fire safety, k8"? How is the "equivalent fire duration" calculated? | The equivalent duration of the fire is calculated according to the ČSN, the equation includes parameters: fire load, ventilation, effect of fire safety devices, area of the fire section and head of the room of the fire section. k8 = the fire resistance safety factor of the building structure depending on the number of floors and the construction system of the building
CZ-C-114 | Germany | 02- Fire safety analyses |  | Regarding Temelin NPP, p. 28 | On p. 28, Sect. "2.1.A.6.2. Lessons learned from events, reviews, fire safety related missions", the sources for lessons learned are explained; however, examples for lessons learned are missing. Could you please provide examples? | Retrofitting of engine rooms - addition of fire extinguishing, increase of fire resistance of the perimeter wall, replacement of fire pumps. Minimization of oil leaks – over-sealing of fittings, slope/downgrade of draining pans.
CZ-C-115 | Germany | 02- Fire safety analyses |  | Regarding all installations, different pages, staring on p. 20 | The phrase "fire section" is used many times all over the NAR for different facilities. A definition could not be found. It is correctly understood that "fire section" could either mean "fire compartment" or "fire cell"? A clarification and distinction between "fire compartment" and "fire cell" would be appreciated. | The mixture of words "section" and "compartment" is basically caused by incorrect SW translation form Czech to English. The term "fire section" could either mean "fire compartment" in the internationally adopted vocabulary. Compartment itself is mostly a "part of a building" which need not be only "fire section". Fire cell is only used in sections with redundant equipment which can´t be effectively separated by structure.
CZ-C-116 | Germany | 02- Fire safety analyses |  | Regarding Dukovany NPP, p. 30 | On p. 30 of the NAR, regarding special cables like optic cables, coaxial cables "which could not be manufactured to meet the test according to IEC 332.3 category A in order to ensure their functionality, their resistance to the spread of fire is ensured by covering their entire length in steel tubes". How and against what type of scenario is this solution qualified? | The functionality of the affected cables is ensured by placing them in a non-flame-spreading plastic pipe, ensuring that the fire does not spread.
CZ-C-117 | Germany | 02- Fire safety analyses |  | Regarding Dukovany NPP, p. 33 | On p. 33, Sect. "2.1.B.6.2. Lessons learned from events, reviews, fire safety related missions", the sources for lessons learned are explained; however, examples for lessons learned are missing. Could you please provide examples? | Expansion of the EFD system, substitution of SES (e.g. Halon for NOVEC), spraying fire protection coating on steel structures.
CZ-C-118 | Germany | 02- Fire safety analyses |  | Regarding LVR 15, pp. 36-40 | The scope of the analyses covering also shutdown states during outages should be more clearly (and not only implicitly) addressed. | The shutdown state means that the rods are in the low end position and possible fire will not affect the change in its position even if the cabling to the drives and power supply is damaged - extraction of the rods is impossible. In case of cooling failure caused by fire during shutdown the followed water reheating and evaporation loss of water do not uncover core at least 3 days. In the event of a fire during the shutdown state, the scenario of a barrel with radioactive waste burning is being considered. This is assessed as not endangering the population.
CZ-C-119 | Germany | 02- Fire safety analyses |  | Regarding LVR 15, pp. 36-40 | Information on how the presence of permanent and temporary fire loads is considered and addressed in the fire safety analyses is missing. | The „permanent“ fire load affects the size and degree of fire safety of the fire section as given by the relevant technical standards and it is part of the Fire Solution of the building. The temporary fire load is subject to specific assessment case by case.
CZ-C-120 | Germany | 02- Fire safety analyses |  | Regarding LVR 15, pp. 36-40 | What is the reason for not considering the radiation hazard of a release from burning radioactive waste in the fire safety analysis? | Analysis of a burning barrel with RAW is part of the safety analysis and estimates unknown content. The radiation in the air is supposed to be same as during operation. Taking into account these the dose is under limits.
CZ-C-121 | Germany | 02- Fire safety analyses |  | Regarding LVR 15, pp. 36-40 | Detailed information on how the direct and indirect fire effects are assessed and which methods and data are used is missing. | In deterministic evaluation, fire is converted into events symptomatically as power loss - for these scenarios, a number of parameters are evaluated by computer programs - the most important of which is the temperature on the fuel surface and its comparison with the acceptance criteria.
CZ-C-122 | Germany | 02- Fire safety analyses |  | Regarding all installations, pp. 36-43 | Information on consideration of plant modifications in updates of the safety reviews and how they are addressed is missing. | Procedures for the evaluation of experiments and modifications are introduced to monitor these actions, where the description of the change is part of the documents for the evaluation of the safety commission, which member is also fire protection person. Following the assessment a procedure is subsequently determined for fire protection - supervision of work, change of documentation, fire prevention measures; conditions for carrying out activities etc.
CZ-C-123 | Germany | 02- Fire safety analyses |  | Regarding all installations, pp. 36-43 | Information in how far and how information from the operating experience regarding deterioration of fire protection features at the Czech installations reported in the NAR and from fire events at other nuclear installations applicable to the installations reported is applied in the fire safety analyses should be provided. | Considering the fact that research nuclear facilities are often unique in design - even in the case of facilities that were originally typical (such as reactors of the VVR-S type), direct transferability is often not possible due to changes during operation - experience is transferred in within working groups (typically e.g. RROG – Research Reactor Operation Group). Fire fighters are subsequently members of other groups for sharing experience within FRSs. LVR 15 operator take experience according to the ČEZ group (occurrence of events at nuclear-energy facilities) + fire protection conferences - according to set topics
CZ-C-124 | Germany | 02- Fire safety analyses |  | Regarding LVR 15, pp. 36-40 | The INSARR mission in 2020 revealed the need for fire hazard reduction (disposal of older technologies) and for comprehensive instructions for personnel response (emergency procedures and emergency instructions) also in case of fire. This statement needs some basic information for justification. | INSARR-type missions always include a tour of the workplace - in the case of the LVR-15 reactor, as part of the tour, it was recommended to remove older (unused) equipment from the technology, not to store material in the technology (e.g. air conditioning filters, etc.) and thereby reduce both the amount of material and, possibly, risk of fire. . The INSARR mission pointed out and recommended a more comprehensive procedure for the operator should be prepared so that the response to the event is easier - that is, the document for the response of personnel was modified, which contains according to event type links to other subdocuments.
CZ-C-125 | Germany | 02- Fire safety analyses | 36 |  | A PSA study is mentioned for LVR-15. Did you perform a full scope Probabilistic Safety Analysis (including Fire Analysis) for this research reactor? Could Czech Republic please provide information on the probabilistic analysis and the major findings? | Internal fire scenarios were incorporated into LVR-15 PSA study in 2023. The quantification will be processed in the PSA update in 2024.
CZ-C-126 | Germany | 02- Fire safety analyses | 40 |  | The inclusion of the internal FRSU in the region's alarm plans and the possibility of the unit's departure to the nearby surroundings to cooperate with the Regional FRS is identified as a good practice. Could Czech Republic please provide more information on the means and procedures at LVR-15 to guarantee the smooth cooperation between the FRSU and FRS? | The inclusion of the internal FRSU of the Research Instute Řež in the region's alarm plans is impossible due to limited number of personnel in site (4). There are organized common exercises with state FRS and also voluntary FRS of the village.
CZ-C-127 | Germany | 03.1 - Fire prevention | 42 | Regarding Temelin NPP, p. 42 | In the NAR on p. 42, under Chapter 3, 3A - Temelin it is mentioned that weak points were found in a 2003 study. However, the weaknesses were not mentioned. It was only reported that "None of these "weak points" relate to the potential impact of fire on nuclear safety." The weak points should be mentioned in some detail in order to allow the community to learn from each other. | Extinguishing in the bitumen area; Addition of a warning device for the presence of CO2 in the area equipped with Stable extinguishes; System of extinguishing turbogenerator and turbine powered feed water, pipe channels; Oil capture and collection system; Cooling system of load-bearing roof structures and equipment for heat removal, Increasing the fire resistance of the perimeter shell, including doors on in turbine hall and in the transformer area; Internal fire water supply in containment; Replacement of CO2 extinguisher agent with another type; Replacement of foam semi-stable fire extinguisher; stable fire extinguish in the simulator area; Extinguishing in warehouses; Semi stable and stable fire extinguish in electro control room; Suctioning the Pyrocool fire extinguisher into the stable sprinkler device in the oil storage areas in reactor building.
CZ-C-128 | Germany | 03.1 - Fire prevention | 44 |  | It is stated that the company's FRSU has a contract with Nuclear Research Institute Řež PLC. Is FRSU an internal fire department of LVR-15? Could Czech Republic please provide more information on the structure of fire fighting and involved parties? | FRSU has the status of a professional firefighting unit, the founder of which is ÚJV Řež, a. s. Firefighters work in FRSU as their profession. It is included in the Administration and Operation section, in the Security and Protection department.
CZ-C-129 | Germany | 03.1 - Fire prevention | 51 | Regarding Dukovany NPP, p. 51 | On p. 51, section "3.1.B.3.2. Lessons learned from events, fire safety related mission evaluations" the way findings are generated and treated is explained, but the findings itself are not reported. Could you please give some examples for findings? | Missing EFD detectors, low period for removal of oiled cleaning textiles.
CZ-C-130 | Germany | 03.1 - Fire prevention | 80 | Regarding Temelin and Dukovany NPPs, p. 80 | Could you add the fire specific characteristics of the turbine oil used? | Turbine oil MOL Turbine 32 K, Flash point (COC) (EN ISO 2592): temp. 220°C, not explosive, practically insoluble in water.
CZ-C-131 | Germany | 03.1 - Fire prevention |  | Regarding LVR 15 | What is the regulatory basis for conducting firefighting drills at least one per two years? | Legislation in the field of radiation emergency management requires regular (min. 1 x 2 years) exercises for relevant events referred to as radiation incidents - in the case of LVR-15 documentation, fires are also identified as sources of radiation incidents.
CZ-C-132 | Germany | 03.2 - Active fire protection |  | Regarding Temelin NPP | The frequently used "semi-stable" extinguishing equipment should be defined. It is understood so far as a piping system for fire extinguishing agents which need manual support. Could you comment and define? | A semi-stable extinguishing device (SSE) is a fire safety device that is firmly built into a protected building and has its own distributor of mobile equipment, to which firefighters with mobile fire equipment can be easily connected. There is air in the entire distribution of a semi-stable fire extinguisher.
CZ-C-133 | Germany | 03.2 - Active fire protection |  | Regarding both NPPs | The flow capacity of the fire water systems should be explained and for what scenario it is designed (e.g. the largest fire extinguishing system plus x water hoses). | The water system is designed to supply firewater to the stable extinguishing, sprinkling and cooling extinguishers to protect selected compartments of the reactor building that house safety system equipment and components. The system also supplies the internal high-pressure firewater distribution system for manual firefighting in the reactor building.
CZ-C-134 | Germany | 03.2 - Active fire protection |  | Regarding LVR 15 | There are no fixed fire extinguishing systems at LVR 15. What is the basis for justification? | The technical standard ČSN 73 0804 defines conditions for stable extinguishers based on fire load in section and its position in the building. The LVR 15 building does not fit to any of definition and is though excluded.
CZ-C-135 | Germany | 03.3 - Passive fire protection |  | Regarding Temelin and Dukovany NPPs, pp. 112 - 117 | On p. 112 (p. 117) of the NAR the actual fire resistance is reported to range from 15 to 240 min for walls and ceilings and from 15 to 90 min for doors and hatches. For fire dampers and fire seals (for pipework, cables) no actual fire resistance is given. How was the given fire resistance rating determined? Please provide information on the required fire resistance rating of fire barriers and their elements and the justification for that. Is the required fire resistance given by calculations or by prescriptive requirements? | Fire resistance is determined by the project, in which calculations are mainly used, but normative requirements are also used based on the value in the table, which is related to the degree of fire safety. The degree of fire safety depends on the structural system of the building, the fire load and the height of the building. The actual fire resistance must not be lower than that specified in the project.
CZ-C-136 | Germany | 03.3 - Passive fire protection |  | Regarding Temelin NPP, p. 115 | From p. 115 it can be read that fire dampers were only installed in the place of "penetrations of ventilation equipment smaller than 0.04 m2" depending on certain criteria. How is the max 0.04 m2 opening area is justified? The criteria mentioned for closing penetrations smaller than 0.04 m2 with dampers do not include structural protection of redundant trains. How is this considered? | This requirement is set in ČSN 730872 (air ventilation equipment with natural and forced air flow).
CZ-C-137 | Germany | 03.3 - Passive fire protection |  | Regarding LVR 15, pp. 123 | In the NAR it is written on p. 123 regarding fires close to the pump house: "A fire in any of these spaces can disable the cooling function for the prescribed 30 minutes." Could you explain why in case of such event the cooling function is restored after 30 min? | The limit of 30 minutes is taken as the minimum cooling time that must be ensured after shutdown. Thus, the events are assessed as to whether they are capable of causing a situation where cooling for 30 minutes will not be possible.
CZ-C-138 | Germany | 03.4 - Licensee's experience |  | Regarding all installations, pp. 124-125 | The two licensee's experience chapters are very unspecific and may be extended by examples. | Experience of the permit holder with the implementation of the fire protection concept is not based on examples as the concept is described in dedicated chapters. Specific examples are given in other chapters, in particular the expansion of fire safety devices and the increase of the level of fire protection.
CZ-C-139 | Finland | 03.2 - Active fire protection | 94 |  | Has another extinguishing agent been considered instead of CO2? | In the case of Temelín NPP when replacing CO2, the preparation for the replacement is for inert gas. In Dukovany NPP it is required by the design.
CZ-C-140 | Finland | 03.2 - Active fire protection | 79, 101 |  | How is the flooding induced by actuation of fire extinguishing systems considered? | Spaces that are protected by water-stable fire extinguishing systems are connected to the industrial drainage system, and in case of extinguishing, the water flows into the industrial drainage system and then to the cleaning water station. In the PSA, after a fire breaks out in the fire section, the inoperability of the equipment is caused by the fire. In in the PSA model, the inoperability of the equipment is not "duplicated" by flooding caused by the activation of the extinguishing equipment.
CZ-C-141 | Finland | 03.3 - Passive fire protection | 119-120 |  | Do fire dampers have the same fire resistance requirement as the penetrated fire-separating structure? | All fire dampers have a fire resistance of 90 minutes
CZ-C-142 | Finland | 03.3 - Passive fire protection | 120 |  | What is the structural separation between turbine hall and reactor buildings? Are there any systems important to safety located inside the turbine hall? | The reactor building is structurally separated from the turbine hall where also systems important for safety are incorporated in Temelín NPP. The reactor building is separated from the turbine hall by another object - horizontal shelf in Dukovany NPP.
CZ-C-143 | Poland | 02- Fire safety analyses | 40 |  | Was the potential aspects of gas generation from waste or spent fuel considered in the safety analyses? | From the point of view of fire protection, they were not evaluated. SFS has natural ventilation in storage part and forced ventilation in the rest of the building.
CZ-C-144 | Poland | 02- Fire safety analyses | 56 |  | Was the cliff-edge effect taken into consideration in the fire safety analyses? | As part of the deterministic analyses, the fire scenarios are converted to events associated with the power failure of individual devices up to the level of the scenario for DEC - complete loss of power. All scenarios will be included in PSA study in 2024.
CZ-C-145 | Slovakia | 01-General information | page 17; chapter 1.2.2 and throughout the report |  | 50 - SG - D2 rev.1 was valid from 1992 to 2004 and is now invalid. In 2004 it was superseded by NS-G.1.7. Since 2021 NS-G-1.7 has been superseded by SSG-64. SSG - 64 and SSG - 77 are safety standards currently in force for fire safety.The report needs to be assessed in the context of currently applicable safety standards and corrected as necessary. | The binding legal Czech documents are the Acts, the Decrees and the Government´s Orders published in Collection of Laws, together with the Czech Technical Standards (ČSN), if listed in the law. The NAR is prepared on that base. IAEA SSG are adopted in the Czech regulatory framework as recommendations, typically as SÚJB Nuclear Safety Guides (listed in chapter 1). The NAR mention the IAEA safety guide 50-SG-D2 as used for the fire protection of Dukovany and Temelín original assessment.
CZ-C-146 | Slovakia | 03.2 - Active fire protection | page 25; chapter 2.1.A.4 |  | In the case of an oil leakage between the 1st and 2nd section of the low-pressure of a steam turbine, one of the worst outcomes is an oil leakage into the insulation, which is not listed in the report. Only an oil leakage from a +15m to a -8.20m floor is indicated. | The FHA describes the most complex variant of the fire, in which the fire spreads in the building from the +15 m floor to the -8.2 m floor, and FRSU must use special extinguishing agents and procedures to extinguish it. Oil leakage into the insulation was not evaluated as the most complex variant of a fire in the building.
CZ-C-147 | Slovakia | 03.2 - Active fire protection | page 39; chapter 2.2.6.1 |  | Is Halotron allowed to be used as a fire extinguishing medium in the Czech Republic? If it is banned, is there a replacement and a recycling process ready, or underway? | In general, technological and highly demanding ecological requirements are currently met by such extinguishing agents that are made by mixing several chemical individuals and their resulting quality are usually better than these of the individual components. This group also includes new extinguishing agents of American origin, HALOTRON I and HALOTRON II, products of AMERICANPACIFICCORP. The recycling process is regulated by Ministry for Environment
CZ-S-42 | Joint Project - Nuclear Risk & Public Control (AT) | 2 | 20 |  | “The assessment presented in the Operational Safety Analysis Report includes a set of postulated initiating events, which take into account the nature of the event, the type of occurrence and the frequency of the event occurrence. Initiating events include internal and external fire events.” -Is an aircraft crash included in the external events considered for all nuclear facilities in the Czech Republic? | The aircraft crash is included in the external events considered for all nuclear facilities in the Czech Republic
CZ-S-43 | Joint Project - Nuclear Risk & Public Control (AT) | 4 | 126 |  | Is the safety culture evaluated with regard to fire protection in nuclear facilities? If so, how is this assessed in the respective facilities? | Fire or its effect on operation and consequences are a typical operational event according to Decree No. 21/2017 Coll. that defines the events that must be reported to the SÚJB and a fire in the installation is included. The Decree requires an analysis of the event causes based on investigation and, in general, for operational events, the impact on nuclear safety culture. Such an assessment performs the operating company and subsequently any event is assessed by special SÚJB inspection.
CZ-S-44 | HAEA (Hungarian Atomic Energy Authority) | 01- General information | Page 8. |  | How are the commonly shared resources (e.g., onsite fire brigade, common drills, etc.) shared between the installations? | There is regular communication between the Temelín and Dukovany sites, and both inform each other about unusual events with impacts on fire protection. Fire fighters are members of specialized groups for sharing experience within Czech FRS and participate in fire protection conferences - according to set topics. Operators take experience according to the ČEZ group; LVR 15 also consider occurrence of events at nuclear-energy facilities.
CZ-S-45 | Joint Project - Nuclear Risk & Public Control (AT) | 01- General information | 1 |  | The "Joint Project - Nuclear Risk & Public Control" submitted today a long list of questions for CZ, HU, BG and PL via the survey support form. Sorry but it was not possible to put our questions in your form. I kindly ask you to verify that you received our list and will consider it in the consultation. Thank you! | ANSWERS FOLLOW
CZ-S-46 | HAEA (Hungarian Atomic Energy Authority) | 02- Fire safety analyses | Page: 36 |  | 2.2.3. Fire phenomena analyses: overview of models, data and consequences Question: How are the on-site or off-site fire departments/brigades taken into account in the fire safety analysis. | Fire risk is taken into account: permanent and accidental fire load, structural system – flammable, non-flammable and mixed, height of the building, area of fire section, ventilation parameter, size of fire-opened areas, presence of fire safety devices EFD, stable extinguishers, devices for smoke and heat outlet, by the presence of the FRSU.
CZ-S-47 | HAEA (Hungarian Atomic Energy Authority) | 02- Fire safety analyses | Page: 32 |  | 2.1.B.5. Periodic review and management of changes Question: What regulation/regulations set the requirements for Fire PSA and Deterministic Fire Hazard Analysis? | General requirements are defined by Atomic act and Decree No. 162/2017 Coll. on safety assessment. The requirements for fire PSA are further set in the evaluation of external hazards (external hazards), which are listed in the SÚJB Safety Guide BN-JB 2.5 - probabilistic safety assessment and in use is also IAEA SSG-3 - Development and Application of Level 1 Probabilistic Safety Assessment for Nuclear Power Plants.
CZ-S-48 | HAEA (Hungarian Atomic Energy Authority) | 02- Fire safety analyses | Page: 31 |  | 2.1.B.4 Main results / dominant events (licensee´s experience) Question: Were there major fire events at the Dukovany NPP that was taken into consideration in modifications (engineering or administrative) and/or had an effect on the fire safety assessment? | During the operation of the Dukovany NPP, there was only one significant fire, which happened in 1994 – the transformer station fire. On the basis of this fire, EFD and SSE were built on all transformers, individual transformers were fire separated from the surrounding area.
CZ-S-49 | HAEA (Hungarian Atomic Energy Authority) | 02- Fire safety analyses | Page: 30 |  | 2.1.B.3. Fire phenomena analyses: overview of models, data and consequences Acc. WENRA SV 6.2: “The extent of reliance on on-site or off-site fire brigades shall be shown to be adequate in the fire hazard analysis.” Question: How are the on-site or off-site fire departments/brigades taken into account in the fire safety analysis? | Fire risk is taken into account: permanent and accidental fire load, structural system – flammable, non-flammable and mixed, height of the building, area of fire section, ventilation parameter, size of fire-opened areas, presence of fire safety devices EFD, stable extinguishers, devices for smoke and heat outlet, by the presence of the FRSU. The fire risk assessment evaluates possible events and compares the forces and resources of the FRSU. In case of insufficiency of forces and resources, measures are proposed to fulfill them. Fire brigades outside the power plant area are only taken into account in case of effective deployment.
CZ-S-50 | HAEA (Hungarian Atomic Energy Authority) | 02- Fire safety analyses | Page: 26 |  | 2.1.A.5. Periodic review and management of changes Question: What regulation/regulations set the requirements for Fire PSA and Deterministic Fire Hazard Analysis? | General requirements are defined by Atomic act and Decree No. 162/2017 Coll. on safety assessment. The requirements for fire PSA are further set in the evaluation of external hazards (external hazards), which are listed in the SÚJB Safety Guide BN-JB 2.5 - probabilistic safety assessment and in use is also IAEA SSG-3 - Development and Application of Level 1 Probabilistic Safety Assessment for Nuclear Power Plants.
CZ-S-51 | HAEA (Hungarian Atomic Energy Authority) | 02- Fire safety analyses | Page: 25 |  | 2.1.A.4 Main results / dominant events (licensee´s experience) Question: Were there fire events at the Temelin NPP that was taken into consideration in modifications (engineering or administrative) and/or had an effect on the fire safety assessment? | Yes – retrofitting of engine rooms: TG and TBN extinguishing, increasing the fire resistance of the engine room walls, modernization of the CO2 extinguishing system of the oil management.
CZ-S-52 | HAEA (Hungarian Atomic Energy Authority) | 02- Fire safety analyses | Page: 25 |  | Acc. WENRA SV 6.2: “The extent of reliance on on-site or off-site fire brigades shall be shown to be adequate in the fire hazard analysis.” Question: How are the on-site or off-site fire departments/brigades taken into account in the fire safety analysis? | Fire risk is taken into account: permanent and accidental fire load, structural system – flammable, non-flammable and mixed, height of the building, area of fire section, ventilation parameter, size of fire-opened areas, presence of fire safety devices EFD, stable extinguishers, devices for smoke and heat outlet, by the presence of the FRSU.
CZ-S-53 | Hungarian Atomic Energy Authority | 03.1 - Fire prevention | 57 |  | Are there internal regulations at the LVR-15 facility to limit and control the transport of combustible and flammable materials and substances into the facility? Are these activities and the amount logged, checked, etc.? | Directive OSM 18 is used for the registration of dangerous substances, including flammables. A shared table is created for keeping information on the current amount of hazardous substances. Every year the lists are checked and the purchase of new substances is part of the approval procedure for the purchase of chemical substances. The FRSU is involved in the approval process. Transportation of dangerous substances is part of process management and is subject to registration/approval.
CZ-S-54 | Hungarian Atomic Energy Authority | 03.2 - Active fire protection | 106 |  | Are there regulations in force for the LVR-15 facility that require specific temporary measures to be taken for example during occasional flammable activities or work involving dust/smoke generation? If so, how are these requirements met? | Plans and analyzes are prepared for buildings - Fire Safety Solutions for buildings. It describes in detail preventive fire measures such as escape exits, resistance of building structures, determination and scope of fire technology and other safety and technical information including fire load analyses. According to the assessment of temporary fire load, a procedure is subsequently determined - supervision of work/change; change of documentation; fire prevention measures; conditions for carrying out activities etc. Procedures for evaluating experiments and modifications are in place to monitor these actions.
CZ-S-55 | Hungarian Atomic Energy Authority | 03.3 - Passive fire protection | 124 |  | Could you provide details on the fire sectioning and applied passive fire protection solutions (e.g.: fire retardant coating on cables)? | Buildings are divided into fire sections and fire cells by the design. Fire section – area of a building, separated from other parts of this building, or from neighboring buildings, fire separation structures or fire safety equipment - is the basic assessed unit from the point of view of fire safety of buildings. Passive fire protection - the aim of this protection is to stop or slow down the spread of fire in the building by closing and sealing openings and passages through which this spread can occur (non-combustible fire walls, fire penetrations, fire coatings, etc.) Cables with reduced reaction to fire and limitation of flame spread are used in SFS, therefore coatings are not used here
CZ-S-56 | Joint Project - Nuclear Risk & Public Control (AT) | 1.1.2 | 9 |  | “From the candidate nuclear installations, the SÚJB selected those with the potential for significant radiological risks to the environment and the population caused or affected by fire, to enable a meaningful comparison of the level of fire protection provision and the feasibility and quality of the assessment.” -Why was the newer SFS Temelin selected for the assessment and not the older SFS Dukovany? | The legal requirements and design/construction essential features are the same, regardless the time of construction of dry SFS. The same permit holder ČEZ, a. s., equal requirements, measures and procedures. The SFS has been described in NAR however it is not individual nuclear installation as it is localized in the site of NPP.
CZ-S-57 | Joint Project - Nuclear Risk & Public Control (AT) | 1.1.3 | 12 |  | “The LVR-15 is a tank-type light water research reactor housed in a non-pressurized stainless steel vessel under a shielding lid with forced cooling. The reactor uses IRT-4M type fuel with 19.7% 235U enrichment and an operating thermal power of up to 10 MW.” -What beyond-design-basis accidents are possible for this reactor? It should be taken into account that it uses fuel with relatively high enrichment and therefore the radiological consequences could be comparatively high. | For the DEC events, the complete loss of working sources of electric power supply, the step input of reactivity of 0.7 β, the loss of the coolant of the primary circuit due to leakage through the hole with cross-sections of 4 cm2 and 8 cm2 and the loss of the final heat sink without pumps of the primary circuit are selected as initialization events. Furthermore, there is the loss of coolant of the primary circuit due to the detachment of the horizontal channel and the complete blocking of one fuel assembly. The use of uranium enrichment of approx. 20 percent does not represent an increased risk - the radiological consequences are determined by the inventory of radioactive substances in the fuel and this is rather proportional to both the total amount of fuel and the level of burnout. Due to operation under atmospheric pressure (open vessel) there is no risk of phase transformation of the coolant during a LOCA type event etc.
CZ-S-58 | Joint Project - Nuclear Risk & Public Control (AT) | 1.2.2 | 16 |  | Are the current valid WENRA Safety Reference Levels for a) Existing Reactors, for b) Existing Research Reactors, for c) Waste and Spent Fuel Storage and for d) Decommissioning Safety included in the national regulations? And are they already applied in the safety assessment of all nuclear facilities, if not, when will they be applied? | Any WENRA valid SRL is included in the Czech legislation. WENRA SRLs for NPPs and RRs (if relevant) are appropriately implemented in the Czech „nuclear legislation“ since 2017.
CZ-S-59 | Joint Project - Nuclear Risk & Public Control (AT) | 1.2.2 | 17 |  | “Internal feedback system provides inspectors involved in inspections by information of operational events and the results of their investigations in their area of expertise. In addition to the inspection of the actual feedback process, inspectors review the progress and analysis of the checked events. “ -What are the main results of these inspections? | Inspections focused on internal feed-back system are performed quarterly at both NPP (8 inspections per year). The investigation and analyses of selected operational events are reviewed. It can be summarized that in several cases the SÚJB requires further investigation of the event and root causes or the addition of corrective measures. In rare cases, a new analysis of the operational event is required.
CZ-S-60 | Joint Project - Nuclear Risk & Public Control (AT) | 1.2.3 | 19 |  | “The scope of the state fire supervision enforcement: ….Identifying the causes of fires.” -What are the main causes of fire events? | In the Czech Republic, according to the statistics of the FRS CR, the most common causes of fires are carelessness and technical failure. The main cause of the fire in Dukovany NPP (5 during the entire period of operation of almost 40 years) was a technical fault.
CZ-S-61 | Joint Project - Nuclear Risk & Public Control (AT) | 2.1 | 20 |  | Are beyond-design-basis fires for the NPPs possible? What would be the radiological consequences, if any? | PSA does not differentiate between project and beyond-design-basis fires. The PSA output is the frequency of individual scenarios leading to a leak. In FHA the most complicated fire is assessed.
CZ-S-62 | Joint Project - Nuclear Risk & Public Control (AT) | 2.1.7.1 | 34 |  | “In accordance with the requirements of the SÚJB, a basic set of operational safety indicators is defined, including: -Unit availability factor - Fuel reliability - Number of INES events - Number and severity of failure events - Unplanned loss of power factor - Containment tightness - Number of fires in the NPP area ….” -Since when are these indicators determined? What are the results and trends of the indicators for the 6 reactors in the Czech Republic? | The first set of Safety Performance Indicators was created and the first evaluated year was 1991. The following knowledge and experience gained from regular evaluations resulted in a revision of the file. The annual evaluation is published on SÚJB web page in the Czech language.
CZ-S-63 | Joint Project - Nuclear Risk & Public Control (AT) | 2.1.A.3 | 25 |  | “The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 13.6% level.” -What are the CDF results for Temelin 1 and 2 according to the latest PSA? What is the date of the most recent calculation? What contribution is made by fire events to the frequency of beyond design-basis accidents or accidents involving the release of radioactive substances? | The contribution of internal threats, and thus also the contribution of internal fires, to the overall risk is evaluated annually and reported in the Operational Safety Analysis Report (PrBZ). For 2022, the contribution from internal fires to FDF (Fuel Damage Frequency) was 12.95%.
CZ-S-64 | Joint Project - Nuclear Risk & Public Control (AT) | 2.1.A.4 | 25 |  | How many and which kind of events/failures per year of the fire protection equipment have been occurred? | Temelín NPP: 68 failures were recorded on the EPS system, 10 failures were recorded on the fire water system and 19 malfunctions were recorded in the air-conditioning system in 2023. Due to the scale of these systems and the number of components, there are one per thousand failures.
CZ-S-65 | Joint Project - Nuclear Risk & Public Control (AT) | 2.1.A.4 | 26 |  | “A. The measures to eliminate the most dangerous fire scenario in the area of sufficient forces and resources compared to the guaranteed 1st level of fire alarm for the given area confirms the necessity to establish the Fire Rescue Service Unit in the Temelín NPP (FRSU). B. The minimum member of this unit shall not be less than 12 personnel per shift continuously ready to respond to an emergency.” -This requirement applies to Temelin, is there a comparable requirement for Dukovany? | The number of members of the FRSU is given by the "Assessment of fire risk" and, as stated in other chapters, the minimum number is 12 on the day shift and 11 on the night shift in Dukovany NPP.
CZ-S-66 | Joint Project - Nuclear Risk & Public Control (AT) | 2.1.B.3 | 30 |  | Dukovany NPP: “The contributions of internal fires to the overall risk of unit operation are generally of little importance. The overall contribution to the unit operating risk (CDF risk measurement) to internal initiation events from internal fires is at 20.3% level.” -What are the current CDF results for the 4 units of the Dukovany NPP? -When was the last PSA carried out? -What contribution is made by fire events to the frequency of beyond design-basis accidents or accidents involving the release of radioactive substances? | The PSA model is updated regularly as part of the Living PSA, the risk assessment is carried out continuously, and once a year the summary results are presented in Chapter 19 of the Safety Analysis Report. The mentioned value is the share of internal events caused by fires in the total value of Core Damage Frequency = 3,42E-06. Contribution to LERF value is 5,8% (2,4E-08).
CZ-S-67 | Joint Project - Nuclear Risk & Public Control (AT) | 2.1.B.4 | 31 |  | How many and which kind of events/failures per year of the fire protection equipment have occurred? | The SÚJB record in database approximately 3 fire protection related event per year per NPP - fire protection equipment malfunctions majority of which is false activation.
CZ-S-68 | Joint Project - Nuclear Risk & Public Control (AT) | 2.2 | 36 |  | Are beyond-design-basis fires possible? What would be the radiological consequences, if any? | The FHA describes the most complex variant of the fire
CZ-S-69 | Joint Project - Nuclear Risk & Public Control (AT) | 2.2.6.2 | 40 |  | LVR-15: “The last documented fire was in the reactor hall in the cable line, which was extinguished without limiting the operability of safety-significant equipment and the affected portion of the cable line was repaired.”. -What was the reason for the last fire mentioned and when did it happen? How many fires have occurred since the start of operations? | The fire in the cable bridge was in a location outside of safety-relevant components - the event occurred on an older part of the cable line in the hall (not made in a non-fire-spreading design). There are no further records of fires in reactor technology.
CZ-S-70 | Joint Project - Nuclear Risk & Public Control (AT) | 2.4 | 40/41 |  | “The analysis of a deliberate attack by a large transport aircraft on a SFS falls into the category of extended design conditions and meets the requirements of a realistic approach. Application of a conservative approach in the form of "largest existing aircraft" is not required. The analyses performed indicate that the mechanical effects of the accident are not of such magnitude as to cause the spent fuel package leakage.” -What assumptions are made for this aircraft crash with regard to the type of aircraft, the fire temperature and the duration of the fire? What are the radiological results of this analysis? -Can radiological effects due to the thermal effects of the fire be completely ruled out? -Are the results for both SFS facilities in Dukovany the same? | The NPP´s PSA does not consider a deliberate attack by an airliner, only an accidental crash. The construction of SF transport and storage package is subject to special type approval and tests which are in accordance with Decree No. 379/2016 Col. The Decree implements all requirements of EU Directives valid in this area, international transportation rules (UN, RID) or IAEA Safety Standards Series No. SSR-6.
CZ-S-71 | Joint Project - Nuclear Risk & Public Control (AT) | 3.1 | 44 |  | -What experiences have been made since the start of operation, when and where have fires occurred and what was the cause in each case? | Since start of operation (in 2001) 9 fires occurred in Temelín NPP, majority was technical failure or personnel carelessness.
CZ-S-72 | Joint Project - Nuclear Risk & Public Control (AT) | 3.1.A | 44 | ETE | A typical cause of internal fires in NPPs is a short circuit in an electrical component or due to ageing cable insulation. Have fires already occurred due to this cause? How are fires from this cause prevented? | Only self-extinguishing cables with increased resistance to flame propagation (ČSN EN 60332-1, ČSN EN IEC 60332-3-22) are allowed to be used in the objects of the main production unit (in listed objects). Safety cables shall comply with ČSN IEC 60331. Cable penetrations through fire separation structures are fireproof sealed.
CZ-S-73 | Joint Project - Nuclear Risk & Public Control (AT) | 3.1.A.3.2. | 47 | ETE | -Have all recommendations and suggestions from the last OSART mission been fully implemented for Temelin? How many recommendations have been given? | 8 recommendation were issued by OSART mission and all are implemented.
CZ-S-74 | Joint Project - Nuclear Risk & Public Control (AT) | 3.1.B | 48 | EDU | A typical cause of internal fires in NPPs is a short circuit in an electrical component or due to ageing cable insulation. Have fires already occurred due to this cause? How are fires from this cause prevented? | Only self-extinguishing cables with increased resistance to flame propagation (ČSN EN 60332-1, ČSN EN IEC 60332-3-22) are allowed to be used in the objects of the main production unit (in listed objects). Safety cables shall comply with ČSN IEC 60331. Cable penetrations through fire separation structures are fireproof sealed.
CZ-S-75 | Joint Project - Nuclear Risk & Public Control (AT) | 3.1.B | 49 | EDU | Dukovany “When it is not possible to locate redundant equipment and components of safety systems or safety-related systems in separate fire sections (containment, control room, emergency control room, cable space under control room, etc.), fire protection systems shall be designed to limit the spread of fire in these fire sections and to eliminate unacceptable effects of fire or the fire protection systems themselves on the redundant safety systems.” -Which redundant safety system equipment and components are not located in separate fire sections? | From the point of view of safety systems, it is mainly the outlet of pipeline routes. Within the hermetic space, the fire separation of the individual divisions is carried out using fire cells. The cable ducts in the hermetic space are separated from it by fire separation structures. A stable fire extinguisher is located in the areas with the greatest fire risk
CZ-S-76 | Joint Project - Nuclear Risk & Public Control (AT) | 3.1.B.2 | 50 | EDU | Dukovany: “In all nuclear safety-relevant buildings, power cables and most low-current cables are of a design with increased resistance to the spread of fire, complying with IEC 332.3 category A, or IEC 331. c) In the case of special cables (optic cables, coaxial cables) which could not be manufactured to meet the test according to IEC 332.3 category A in order to ensure their functionality, their resistance to the spread of fire is ensured by covering their entire length in steel tubes.” -Which low-current cables are not of a design with increased resistance to the spread of fire, complying with IEC 332.3 category A, or IEC 331? | Mainly cables from construction phase (thermometers, pressure gauges, cabling from I&C stands), telephone, radio, company radio, accurate time, data network cabling. Optical, coaxial cables of computer network.
CZ-S-77 | Joint Project - Nuclear Risk & Public Control (AT) | 3.1.B.3.2 | 51 | EDU | Have all recommendations and suggestions from the last OSART mission been fully implemented for Dukovany? How many recommendations have been given? | The last OSART mission was held in Dukovany NPP in 2013 and issued no recommendation related to fire protection.
CZ-S-78 | Joint Project - Nuclear Risk & Public Control (AT) | 3.2.A.2 | 65 | ETE | Are the fire extinguishing systems of Temelin designed to withstand earthquakes? | In main operational units are seismic resistant extinguishers. Seismic-resistant is stable sprinklers systems and distribution of high-pressure pipelines in the reactor building and PHZ of system diesels. The requirement is that they maintain functionality even during a seismic event.
CZ-S-79 | Joint Project - Nuclear Risk & Public Control (AT) | 3.2.B.2 | 89 | EDU | Are the fire extinguishing systems of Dukovany designed to withstand earthquakes? | Safety important equipment is protected by stable extinguishing equipment with seismic resistance.
CZ-S-80 | Joint Project - Nuclear Risk & Public Control (AT) | 3.2.C.2 | 106 | LVR15 | Are the fire extinguishing systems designed to withstand earthquakes? | Firefighting equipment and EFD are not seismically qualified.
CZ-S-81 | Joint Project - Nuclear Risk & Public Control (AT) | 3.2.D.2 | 111 | SVJP | Are the fire extinguishing systems designed to withstand earthquakes? | Based on FHA there are no stable extinguishing systems in the SFS. The building has a hydrant distribution of fire water, which is not seismic resistant.
CZ-S-82 | Joint Project - Nuclear Risk & Public Control (AT) | 3.4 | 124 |  | Are the components of fire extinguishing systems, fire alarm systems and fire dampers in the aging management program included? If yes, since when? What are the results, how many ageing effects have occurred in these components? Are there any trends to be observed? | The requirements of Aging Management Program (AMP) for research reactors were introduced by legislation in 2016. The program includes the EFD in buildings, fire dampers and fire water distribution of the building. For these devices, the AMP defines condition monitoring methods, acceptance criteria (activity/functionality test form and required result) + selected preventive measures to minimize aging. In 2019, the central switchboard, located in the FRSU building, was replaced; in 2020, the main hydrant water supply (service) was reconstructed and part of the horizontal distribution lines up to the supply to the reactor hall were reconstructed; in process is gradual replacement of selected parts based on regular tests and condition inspections results.
CZ-S-83 | Joint Project - Nuclear Risk & Public Control (AT) | 3.4 | 124 |  | How many incidents/failures of fire detection and alarm components, fire extinguishing systems, fire barriers and ventilation systems have occurred in the different nuclear facilities to date? Can trends be observed over the last two decades? | The vast majority of EFD malfunctions are diagnosed by the system online (defects of detectors, input modules, etc.) System failure (affecting downstream equipment) did not occur. Non compliances in mechanical parts of extinguishing systems are detected in walk downs or functional testing (related with system ageing) were detected: e.g. in 2022 recorded 70, in 2023 recorded 35 in Dukovany NPP.
CZ-T-9 | EC | 01-General information | N/A |  | What fire safety improvements/measures have you done/taken based on internal/external operating experience, if any? | Many measures after the Fukushima event were implemented also in fire protection measures – upgrading the FRSU station, additional equipment and mobile operating equipment, increasing the number of firefighters, diverse additional and mobile equipment technology for the company fire brigade (Diverse EFW System) or hydrogen recombiners. There are actively used external and internal feedback, in which is assessed the influence of external and internal events on the fire protection process.
CZ-T-10 | TPR Team | 01-General information | §1.2 |  | The NAR in §1.2 presents the regulatory framework. If not yet clearly mentioned in the NAR, could you indicate whether the WENRA SRLs for NPPs, and RRs (if relevant for your country), which are used as reference for this topical peer review on 'fire protection' (as per the Technical specification) are binding or not in your country? If they are not binding, what is the status of the SRLs (non-binding, guidance, advisory..)? | WENRA SRLs for NPPs and RRs (if relevant) are appropriately implemented in the Czech „nuclear legislation“ since 2017. Note: It is stated in approved TS, 21 June 2022: „While the SRLs are considered as a framework for the TPR, the TPR is not meant to be a compliance check to SRLs.“
CZ-T-11 | EC | 03.1 - Fire prevention | 45 |  | What specific cable design to prevent spreading fire over power and control cables has been used? | Only self-extinguishing cables with increased resistance to flame propagation (ČSN EN 60332-1, ČSN EN IEC 60332-3-22) are allowed to be used in the objects of the main production unit (in listed objects). Safety cables shall comply with ČSN IEC 60331. Cable penetrations through fire separation structures are fireproof sealed.